## Sheet0
COVID-19 and Buildings: Re-Occupation after Lockdown Q&A Report:
Question Asked | Answer Given
what is the required intensity for UV lamp to kill the covid19 | in a recent study, the research team applied a dose of 5mJ/cm2, resulting in a reduction of the SARS-CoV-2 virus of 99% in 6 seconds. Based on the data, it was determined that a dose of 22mJ/cm2 will result in a reduction of 99.9999% in 25 seconds.
prefer location of uv ,is it after hepa filter or berfore | Ideally after the HEPA because that ensures better lamp cleanliness. But for duct mounted UVC the location is more likely to be chosen to suit access and the ability to supply an electrical service to the unit. Maintenance is also very important because the UV unit will require regular lamp changes - possibly every 2 years (13000 hours are quoted) - and an operative must be able to get to the unit, remove its access panels in order to carry out the work. In many installations it might be better to have several smalller UVC units located in branch ducts - for ease of installation, resilience (in case one fails and needs fixing), supplies to each zone rather than just one 'big' UV unit at the AHU. Each case will require an engineer's advice to discuss options.
in the AHU, VAV System using the UVC in AHU ot after each VAV which one the more efficent | The actual efficiency of the UV as an air cleaner depends on the intensity of the UV and the dwell time - which means how long the virus spends as it travels along the length of the lamp. Bearing in mind that any airborne particles are probably swirling around in the airstream. It should be more cost effective and efficient to install at the AHU , or in the main ductwork rather than after the VAV boxes. Installation after the VAV boxes would mean multiple units. In many North American hospitals they install at the main AHU and also downstream after VAV boxes in order to have a final clean of the air before it is supplied into the rooms. But these would be special case ultra clean rooms.
Bi-polar ionization could be beneficial, but has not been researched in enough detail at this point, most publically available data is coming from the manufacturers. There is also the fact that bi-polar ionization functions by converting oxygen molecules into charged atoms that then deactivate bacteria and viruses. These charged particles could remain in the air so we need to be careful that by solving one problem, we are not creating another (thus more research is still required). On the other hand, UVGI disrupts the DNA of viruses that are in its path and will not negatively impact anyone unless directly exposed to it. | Yes agreed. As engineers we must always be open to new ideas and technologies but we must also take a practical and pragmatic approach which would generally direct us to the more established solutions. But we can always trial new technologies provided we advise our client accordingly. We should only do this if we think the new technology has a major advantage which is worth the trial. At the moment UVGI is a proven technology and is known to work well.
Do we have enough evidence that the UVGI technology can be effective not only in sick rooms but also in places where the human circulation is high like shops or public places? | Yes, it has been proven to be effective for tuberculosis and other viruses but no studies yet for SARS-COV-2 yet to the best of my knowledge. However it has been tested for other viruses such as influenza and SARS 1 and has been found to have a high 'kill' rate - over 99 %. It is reasonable to assume it also kills SARS 2 at the same rate - but we must await the scientists trials to find out. Such testing is very complex and can only be carried out in labs using Covid samples - or a substitute.
At an offices building with splits and multisplits cimatization system and separate ventilation system, would you recommend the operation of the splits knowing that it will recirculate the inside air in spaces with more than one person? | The advise at present is to turn off the recirculation units. However this may be impossible if they are being used to condition the room space. But if they are to be used the systems must include UV air sterilisers to clean the recirc air. The fresh air supply must be increased as much as possible. Refer to ASHRAE website for latest information. | It is important to make sure the ventilation system is working properly. UV can be used, portable air filters are recommended as well. Refer to ASHRAE website for latest information.
Several studies show a potential increase of similar viral threads being more frequent in the future. Wouldn't it make sense to fit BACS/BMS with a scenarios that can be activated and change the settings to the behaviour of the HVAC system for as long as the scenario is triggered? Shouldn't things like that be consifdered even during conception of new buildings? | Covid has come as a shock to us all. It has shown that we should choose systems which provide healthy environments rather than those that do not. Air systems are better than in room units such as splits because they can deliver more fresh air and dilute any pathogens in the air. But we already have many buildings with fan coils, splits, heat pump units etc etc. So I agree that going forward we must consider systems which can switched to overcome sudden viral threats. We must all work to ensure that the ASHRAE handbooks provide advice on this topic.
Please talk about whether school buildings should not open until most if not all virus mitigation measures are installed? Funding for doing these measures can impact how quickly they can be done. | ASHRAE's ETF - Emergency task force - has published guidance on the website. For schools a UVGI unit can be installed into each classroom to reduce the viral load if a Covid person enters. The aim must be to ensure that an outbreak is contained to a single room. Funding is an issue and in many cases it will fall to the government to pay for these measures. It does seem that such measures must be carried out in order to achieve confidence amongst teachers, pupils and their parents. The UK tried to re-open schools without doing any such measures and teachers and pupils refused to go back.
A UV light after the filter would help keep mold and mildew off of cooling coil | Yes UV lamps are often used to keep cooling coils clear of mold.
We are not discussing about energy impact, but in a case if we have to balance the energy consumption and better IAQ (increased venti, filtration etc.) what would be the measures can be suggested? | The current advice to supply MORE fresh air will certainly increase energy usage and costs. Measures such as UVGI which kill viruses can be used to achieve recirculation and will help conserve energy.
what if our office building HVAC do not have the MERV 13 filters what are the alternative solutions for filtration? | It may be possible to upgrade filters. It would be necessary to check fan duty and space for new filters. A bigger fan may be needed to overcome resistance of filters. UVGI is an alternative that does not impact on the fan duty.
Yuguo Li did a presentation at last week's ASHRAE 2020 Virtual Conference. He suggested that the outdoor air rates in ASHRAE 62.1 were insufficient. Is ASHRAE revisiting the rates? | I am not aware of ASHRAE 62.1 being changed for this reason but it is being reviewed. The ASHRAE website does give advice for Covid which does suggest increasing fresh air supplies to dilute any Covid loads. It also suggest early starts for purging the rooms before occupancy and overruns after occupancy.
what about alternatives to UVGI? Such as needlepoint bipolar ionization(NPBI) on Covid-19? Are they as effective or perhaps even more effective than UVGI? | As noted in number 7 above, Ioniazartio is a possible measure but has yet to achieve full testing and application.
For temporary housing areas for Covid-19 patients in healthcare facilities, where the rooms are unfortunately being supplied by recirculating air, do we have to disinfect the AC units (e.g CFCU, FCU) before the area is reconverted back for normal non Covid use? | Yes a deep clean and sterilisation must be carried out.
What duties (if any) would a BMS have in overseeing the UV light instrumentation in the HVAC? | A BMS unit would report on lamp life is use - hours run - and operational status. It would advise on the time for lamp replacement.
What is the relationship between increasing filtration levels and increasing outside air ventilation? ASHRAE Standard 62.1, Ventilation for Acceptable Indoor Air Quality, defines ventilation as “the process of supplying air to or removing air from a space for the purpose of controlling air contaminant levels, humidity, or temperature within the space.” There is no mention of outdoor air or percentage of outdoor air. Any air that has a lower concentration, even if non-zero, of the contaminant that is being diluted can provide “ventilation”. | The Ventilation Rate Procedure which is the most used procedure of the standard is a prescriptive design procedure in which outdoor air intake rates are determined based on space type/application, occupancy level, and floor area. the Indoor Air Quality (IAQ) Procedure is the performance-based design procedure in which the building outdoor air intake rates and other system design parameters are based on an analysis of contaminant sources, contaminant concentration limits, and level of perceived indoor air acceptability. Filtration and outdoor air ventilation help in imporving indoor air quality, where filtration would target some contaminants and remove part of them from the airstream while the outdoor air ventilation would reduce contaminants level by dilution depending on the poluttants concentration difference between the indoor air and the outdoor air
What's the role of aerosol and PM monitors in optimizing filtration and ventilation controls? | Having PM monitors would help in informing the building management if the ventilation/filtration systems are working properly and would give feedback so corrective action can be given
What precautions is recommended in the ablution facilities in offices, hospitals, old age homes ? | similar to what have been discussed in the course, visit the ASHRAE website where guidance on many typologies are given
CAn you discuss Bipolar Ionization vs. UVC?
With an Energy Recovery wheel, is there a possiblity that a droplet will be transferred between airstreams even if pressures are controlled? Water goes from high pressure to low pressure, as does air, so if the exhaust air has higher water pressure than the supply, won't it transfer through the wheel? | Evidence suggest that rotors with adequate purge secctor practically do not transfer particles, but the transfer is limited to gaseous pollutants (e.g. smells, tobacco smoke). The source is RHEVA
Does anyone have actual test data on UV dosage required to kill coronavirus? | refer to question 1. However more studies need to be done to confrim the required "dosage"