## Sheet0
Q&A Report:
Study Requests |  | Team Answers:
| Is there a link to the hospital ductwork study the first speaker referred to? | Here is a link to the study. Keep in mind that it has not yet been peer reviewed, but it at least gave us some more intel into the ductwork. https://www.news-medical.net/news/20200630/Identification-of-SARS-CoV-2-RNA-in-healthcare-HVAC-units.aspx Within this link you will find the pre-print that has all of the materials and bibliography. https://www.medrxiv.org/content/10.1101/2020.06.26.20141085v1
What is the reference for the study you are saying indicates virus on the exhaust vents?
Can you provide more information about the study referenced in the beginning of the presentation about SARS-CoV-2 testing in various HVAC locations? In relation: is there any evidence of SARS-CoV-2 in recirculated air, or is filtration a conservative approach at the moment?
Please share the reference to publication studying spread of COVID19 through ventilation system in a hospital.
Would you be able to share a link to the study showing virus in HVAC system ductwork (return to supply stream)
Can Wade provide a link to the study referenced that looked at HVAC system in a hospital that found virus in the filters?
Can we get a link to that study showing the travel of COVID-19 into the air handling system?
Can you post a link to the latest HVAC study you mentioned?
Can we get a cite for the new study just referenced?
Can you please link to the study about SAR-CoV-2 in healthcare facilities, where traced the air pathway?
Question Asked
Filters
| Good day, if I don't have the ability to use MERV 13 or more , I just use MERV 10 , is it effective to reduce filter change intervals | Use whatever the highest efficiency filter you can, but a clean filter is less effective at capturing particles than a loaded one. We recommend leaving a filter in until it is near its rated holding capacity.
| Can you provide guidance on HEPA modifications to existing AHU. | The best route is to contact the unit's manufacturer to see what they recommend. Most ASHRAE guidance does not indicate the need to install HEPA filters.
| is it less than 2.5 nm particle will filered by H 14 HEPA filters and how it effect the pressure drop and cost overall and efficiency? | MERV 14 filters aren't HEPA filters. Using the building readiness guide, you can field measure the difference in fan HP required. Leaving the filter in until it is near its rating holding capacity, may increase the amount of time between filter changes, which could partially offset the increased cost of the filters.
| please comment on the thinner MERV 13 filters that are available for existing low static terminal equipment; I assume these will have to be changed out much more quickly than a lower MERV filter? | Assuming you are talking about 1" filter depths for the MERV 8 verus MERV 13 filter. A check on a supply chain website for a MERV-8 general purpose versus their MERV-13 filter indicates that the initial resistance at 500 FPM is 0.33" versus 0.36" of pressure drop. Both have a Final Recommended Resistance of 1". So, there is a difference, but that is extremely neglible for filter life and pressure drop. Based on these, it does not seemt that the change out date would change any more often.
| What is your opinion on using electrostatic filtration when MERV 13 can’t be used? | Please review the Filtration and Air Cleaning Position Document (https://www.ashrae.org//File%20Library/About/Position%20Documents/Filtration-and-Air-Cleaning-PD.PDF )
| Would it be a good idea to put MERV 15/16 if the ventilator total pressure is good enough? | We would recommend a cost/ benefit analysis for the slight benefit of using the MERV 15/16 filters instead of the MERV 13 in your systems.
| How did you conclude MERV 14 + UV-C approaches a HEPA filtration effectiveness? | This calculation for an in-duct system in which UV is in series with a filter. For a MERV 13 filter, the minimum efficiency for 1 – 3 micrometer particles must be at least 85% and it must be at least 50% for 0.3 – 1 micrometer particles. Single pass efficiency of two filters in series is: Eff_total = 100[ 1- (1-eff_1)(1-eff_2)] = 100 [1 – (1-eff_f)S_UV] Let’s assume (not unreasonable) that most of the viruses are in the larger particle size range. In that case, for 99.97% combined performance, 99.97 = 100[1 – (1-0.85)S] S = (100 - 99.97)/15 = 0.002 = 2%, so you’d have to design the UV system for 98% single pass inactivation to get to exactly the HEPA minimum performance level.
Sarah mentioned using UV lights along w/ Merv13 can give you HEPA reults. Where can i find documentation on that?
| Can you speak to the relative advantages and disadvantages of in-duct vs. in-room filtration, UV systems etc. | Relative advantages/ disadvantages depend on the system and air delivery method. This reinforces the need to perform an analysis and determine which engineering controls/ mitigation strategies are most appropriate for your building systems.
| Can MERV 13 remove viruses? | The COVID virus particles tend to clump, so the more efficient filters would help to capture these particles.
| The primary question I have is related to the ASHRAE recommendation to increase filtration from MERV6 or MERV8 (standard for packaged rooftop HVAC equipment) to MERV13 or MERV 14. Specifically, if the coronavirus size is 0.12 to 0.16 um, what will a filter that has (virtually) no ability to capture this particle size do to help? and (related) with the loose fitting of typical rooftop filters, would these gaps between filters not be a significant problem in capturing virus sized particulate? | If you are going to upgrade your filters, sealing the gaps between the filters would be recommended. The Building Readiness Guide describes the process to minimize the gaps/ leakage between filters. See this link: https://www.ashrae.org/file%20library/technical%20resources/covid-19/ashrae-building-readiness.pdf The MERV 13/14 filters perform better at 0.1 um than 0.3 um. Also the SARS-COVID 2 virons tend to clump together, creating a particle that has been observed to be between 1-4 microns. Refer to the chart detailing fractional efficency of filters per mean particle size. (https://www.ashrae.org/image%20library/main%20nav/technical%20resources/hepafilters.png)
| Why MERV 13 (not 14, 15, etc.) | We recommend the highest efficiency filter that your systems can handle. We would recommend a cost/ benefit analysis for the slight benefit of using the MERV 15/16 filters instead of the MERV 13 in your systems.
| Is HEPA recommended for COVID-19? | Most ASHRAE guidance does not indicate the need to install HEPA filters. We recommend the highest efficiency filter that your systems can handle. We would recommend a cost/ benefit analysis for the slight benefit of using the HEPA filters instead of the MERV 13 in your systems.
| Is it neccesary to implement additional air filtration and technologies like UVC to occupy back an office building? | Relative advantages/ disadvantages depend on the system and air delivery method. This reinforces the need to perform an analysis and determine which engineering controls/ mitigation strategies are most appropriate for your building systems. Some type or combination of mitigation strategies that were discussed here would be recommended, but not mandated.
| it would be best to address the issue of changing the filters the static pressure increase would create a problem in fan RPM and if we change the fan diameter it wont be fitting into existing unit | Using the building readiness guide, you can field measure the difference in fan HP required. Leaving the filter in until it is near its rating holding capacity, may increase the amount of time between filter changes, which could partially offset the increased cost of the filters.
Changing Filters
| Hi everyone... I want to ask, which is the ASHRAE's position for the filter replacement during O&M during Epidemic? | Please refer to the following sections in the ASHRAE website, https://www.ashrae.org/technical-resources/resources. under the Filtration/ Disinfection tab Facilities/Maintenance – PPE Basics HVAC System Maintenance and Filter Replacement during the COVID-19 Pandemic And for Healthcare, refer to this section of the Healthcare Guide, under Buildings tab- Filter Changing in units serving COVID-19 patients from the HC Guidance.
When it comes to PPE requirements for changing HVAC filters, how can a person tell if there has been a potential contamination to the system? Or should full PPE be worn any time a filter is changed on a HVAC system during this time?
For maintenance crews, do they have to disinfect air filters during periodic maintenance? Will it affect the occupants, is it safe?
If the air filter is capturing COVID is this filter considered hazardous and what should be the done to safely remove and not allow COVID to spread throughout the entire AHU?
If the filters are catching the virus, how often should they be changed? If they're loaded up with viruses, will they stay live or gradually die?
What protection is recommended when replacing filters?
Virus particle size is 50-120nm. Merv 13 cannot filter the virus. Can you address how the facility operators going to handle changing filters if MERV 13 can filter the virus? Wouldnt it put them into risk?
If COVID 19 is considered as airborne, then there shall be a special procedure for filter change, such as bag in bag out, does ASHRAE take that into consideration?
UV
| UV lights can generate Ozone that is harmful, I think it worths to alert people to take precautions before using this technology | Correct- some UV lights can generate ozone, and those wavelengths should be avoided.
| How effective is UVC when virus is flying by at 500 fpm? | The UVC in-duct air disinfection section on the ASHRAE website states they are typically designed for 500 FPM. For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
| What about velocity restrictions with the efficacy of UV. Most AHUs are 400-500 FPM. How can UV be effective at these velocities? I hear it needs to be 250-300 FPM. | The UVC in-duct air disinfection section on the ASHRAE website states they are typically designed for 500 FPM. For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
| Hi, the contaminant "hang time" with UV works good for UV in rooms such as hospitals. How effective are UV tubes really in AHU's when velocities are 500 - 100 FPS? | The UVC in-duct air disinfection section on the ASHRAE website states they are typically designed for 500 FPM. For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
| Does UV-C systems actually have an impact against COVID-19? If so, what kind of dwell time in the light pool would be required to kill the virus? | The UVC in-duct air disinfection section on the ASHRAE website states they are typically designed for 500 FPM. For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
| Hi, Does it make sense to use UV on 100% OA units with heat wheel recovery in case of cross contamination thru the wheel? | If designed properly, it could help. Final filters in the supply air duct could also be an engineered solution.
| How effective is UV and where it will work best? | UV is effective if applied correctly. For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
| What is the best way to implement UV protection in an HVAC system? | Please utlilize your Building Readiness Team for mitigation strategies appropriate to your systems. See the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
| It was stated that UV can kill off the virus. We have been told there is no proof that UV can complete eradicate COVID. Is this the case? | See the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab. If the system is properly designed, it can kill virus particles.
| Is Air Velocity over the coil a concern using UV? | The UVC in-duct air disinfection section on the ASHRAE website states they are typically designed for 500 FPM. For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
| Will UV derate wiring or any gaskets or seals in the AHU | Potentially. Best to use UV resistant materials and consult the HVAC equipment manufacturer before retrofitting an existing unit with UVC.
| UVGI Lamps. Can you use them to sanitize the air? Do UVGI lights inside the AHU's sanitize the air as well as the surface of the coils? | The UVC in-duct air disinfection section on the ASHRAE website states they are typically designed for 500 FPM. For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
UV effectiveness? Any resources?
How many seconds will the UVGI need to shine on SARS-CoV-2 to kill it? Is the air moving too fast through the duct system for it to shine long enough?
How would you specifically suggest UV-C be applied in an HVAC system?
How will UV light help when air flows by at 500 fpm and is only exposed to the light for a few seconds? The UV light systems for an empty room may help but involve logistics issues and can damage components in the room.
Sir how to evaluate the uv light performance
what dwell time is needed for UV to be affective on COVID19?
| With UV lights in the AHUs, should you be operating the building systems 24/7? | No- follow your normal occupancy schedule
| Is UV lighting a suggested component that is installed inside an AHU? | We recommend that you increase your filter efficiency to MERV 13 or better if possible first. If filters cannot be upgraded without causing increased static pressure losses or decreased airflow through the air handling equipment, then consider combining UVC air cleaning in the unit with as good a filter as possible. We suggest you work with a local licensed professional engineer and consult with the air handling equipment manufacturers before making major upgrades or retrofits to existing equipment.
| Do you have specifics on UV intensity and/or time of exposure for the airstream in the UV light? Are other technologies, such as bipolar ionization, being regarded by ASHRAE as a solution to support better IAQ? | The UVC in-duct air disinfection section on the ASHRAE website states they are typically designed for 500 FPM. For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
| Where would the UV light solutions be most effective for COVID? In the room or at the HVAC unit? | This depends on the HVAC systems in the building and the space layouts. If there is displacement ventilation, upper room UVC could be used. If you have a ducted system, in-duct UVC could be used.
| Is it possible to put UV light in HVAC system against COVID virus? | The UVC in-duct air disinfection section on the ASHRAE website states they are typically designed for 500 FPM. For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
| Regarding UV lights, is there some controversy to their effectiveness, especially as far as contaminant control (point of use) is concerned? | For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
| I read an article that suggested UV lighting insatlled within the HVAC system can be used to kill the virus. Any information on these types of systems? | The UVC in-duct air disinfection section on the ASHRAE website states they are typically designed for 500 FPM. For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/resources, under the Filtration/ Disinfection tab.
Bi-Polar Ionization & other Technology
| Do you recommend using bipolar ionization as a tool to control the virus? | An industry standard Method of Test (MOT) for most of these air cleaning technologies that would allow different manufacturers product's efficiency and effectiveness to be compared does not exist. For example, ASHRAE Standard 110 is a MOT used to verify Fume Hood Performance to a common standard. A standard MOT would allow an easy comparison - like a consumer reports study. Some of these technologies can create unwanted byproducts from their process such as ozone. So without a method of test, how do you know how they each perform against each other? There is a UL standard (2998) that allows an electronic air cleaning device to be tested to determine it does not emit harmful levels of ozone. You should check that any device being considered has been tested to this standard. Lacking a MOT we recommend an owner or a facilitiy operator work with a local licensed engineer to evaluate any air cleaning systems being considered so that an informed decision about their application may be made. A beneficial characteristic of BPI and DHP that is also a feature of UVC systems is that they do not add much to increased static pressure losses and increased fan horsepower requirements.
Can you discuss effectiveness of ionization devices?
Has Ashrae evaluated bipolar ionization and photohydroionization equipment to oxidize contaminants bacteria and viruses?
Do you have any feedback on ionizing systems vs UV?
did you mention bi-polar ionization. what is the effectiveness?
UVGI vs Ionization? Are ionization devices effective at all?
What are your thoughts on Needlepoint BiPolar Ionization systems in lieu of UV Systems?
Any analysis of the needlepoint bipolar ionization technology...especially as compared to UVC?
Has anyone reviewed bipolar ionization and what are the thoughts on this technology
Will ASHRAE be recommending the incorporation of bipolar ionization technology which has been shown in studies to deactivate viruses?
What is your opinion of Ionization systems?
How about bipolar ionization?
Is bipolar ionization a viable alternative to UV disinfection?
In regards to air purification technologies, what is the view on bi-polar ionization technologies and their use / regulation moving forward?
Will ASHRAE be providing testing & guidance on other mitigation options such as Needlepoint Bipolar Ionization and Photocatalytic Oxidation?
We have a lot of building operators look at Photo-Catalyric Oxidation (PCO) versus Bipolar ionization, and every vendor will certainly say their technology is best, but looking for some information from ASHRAE on recommendations as far as technology
What have you heard about air disinfection by bi-polar ionization?
Would increased inline electrostatic charging increase filtration of covid-19 sized viruses
Has bi-polar ionization air cleaning technology or other electronic air cleaning technology been a topic discussed on the task force?
What is the team's experience with ion generators, and are they recommended for reducing viral quantities in the building air? A number of manufacturers claim studies show these devices kill viruses.
Can you comment on the use of bipolar ionization systems that are currently being promoted as having the ability to neutralize viruses? What is ASHRAE's position on this technology.
Is there any definitive information on the ability of Bipolar Ionization to render the current the virus inactive?
Any guidance on bi-polar ionization?
Is bi-polar ionization a good alternative to UV?
Bipolar ionization vs. UVC?
Has there been any studies on ionization units and the benefits.
What are your thoughts on ionization technology and it's efficacy at purifying building air?
For control strategies (other than UV): what does ASHRAE think of bi-polar ionization technology (sometimes also called "Needlepoint Bi-polar Ionization, NBPI) ?
Any thoughts about using Ozone gas to sanitize the HVAC system?
What is position of ASHARE of the use of Bipolar Ionization systems, as am alternative to UV-C?
Technology systems to consider, does the team have any thoughts/ comments on systems such as: - airPHX: non-thermal plasma technology, airPHX units disinfect air drawn through the device. The oxidizing molecules that exit the device then disinfect air and surfaces in the treatment area. OR - synexis : Dry Hydrogen Peroxide (DHP) : delivers a gas composed of dry hydrogen molecules combined with ambient room oxygen and humidity
Good day, what's ASHRAE position on PCO and cold plasma solutions against COVID19? on the released document does not seem as a good choice.
Ventilation/ Return Air
| how much in terms of percentage fresh air intake is required for ventilation ? | ASHRAE Standard 62.1 should be consulted for minimum acceptabe ventilation rates for commercial buildings, ASHRAE Standard 62.2 for residential buildings and ASHRAE 170 for healthcare buildings or local code and statutory requirements, if more stringent.
| Can you comment on displacement ventilation? | Properly engineered HVAC systems, including displacement ventilation systems, using well mixed air can be beneficial at mitigating the spread of infectious aerosols.
| Has there been a study to show how much air flow is needed to reduce potential spread of the virus in an open office format? | None at this time. There has been at least one study in a healthcare facility that sampled the air distribution system and found the virus in multiple places within the system. According to Bill Bahnfleth, Ph.D., the preprint of this paper suggests the possibility of a number of things: 1. Opportunistic airborne transmission if poor filtration and ventilation exist in a recirculating system, and 2. Better filters in an AHU are not pointless as some have suggested. A copy of the preprint may be found at the following link: https://www.medrxiv.org/content/10.1101/2020.06.26.20141085v1.
| Have RTUs with re-circulation been studied for possible spread of viruses, etc.? | Not as far as we know.
| in the 70's we started using return air in hospitals. Should we consider 100% asa systems for hospitals to protect some of our most valuable citizens? | Healthcare facility HVAC systems should comply with the requirements of ASHRAE Standard 170. Properly engineered systems using the correct ventilation rates, air change rates and filtration efficiencies can be just as effective as systems that utilize 100% outside air at maintaining indoor air quality in healthcare facilities, and depending on the location and outdoor air quality, may be better.
| Is it reasonable to consider a partially occupied building as being provided with 'increased ventilation' because the present population is half or less than design? | Yes
| Is the recommended 3 air change flush period before or after occupancy? | The 3- hours flush can occur either pre or post occupancy.
| What is your take on Clean Rooms that are changing the air over 60+ times per hour (recycling with minimum OA intake)? Is there more of a perceived risk having less make-up air. | Clean rooms have a high-level of filtration already. No, there is no added concern at this time.
| I’m particularly concerned about increased OA in winter, and its effect on RH. In New England it’s difficult to maintain 30% RH is a building without active humidification. So which takes precedence? Keep OA where it is and maintain RH, or increase OA and let RH drop? | This is a safety/ benefit analysis when reviewing mitigation strategies. You may want to investigate increasing your filter efficiency or installing an air cleaner before increasing your OA percentage.
| the flush of the builiding is with only outside air? | The goal is 3 air changes of outside air to flush the building. That could be 3 hours with your standard OA setting.
| The 4 hour or 3 air changes should it be done in morning before the office time starts? Or is it 3 air changes through out the day? | The building flush (3 air changes of outside air) can occur either pre or post occupancy.
| how do you recommend to induce ventilation in the buildings | For further information, please see the ASHRAE website at https://www.ashrae.org/technical-resources/building-readiness#increasedvent
| is that 3 air changes per hour or 3 air changes prior to occupancy (say at night) | The building flush (3 air changes of outside air) can occur either pre or post occupancy.
| Flushing building should be done when the building goes into unoccupied while virus is potentially airborne once people have left the building. or should you do it prior to occupancy? | The building flush (3 air changes of outside air) can occur either pre or post occupancy.
| Steve Taylor mentions that additional OA isn't the answer but increased circulation (getting VAV boxes and VFD's to open up such as lower space setpoints and slightly higher supply air discharges will do this). Do you agree with this? | For the system and climate zone that he is speaking about, this is an acceptable approach. The ASHRAE guidance may be applicable to all climate zones and system types.
| Increased ventilation is not possible for buildings with DOAS sized for max occupancy how am I to address why in a building that can do increased OA I am not doing it since a DOAS facility can't do this but it is still consider safe? | It is worthwhile to investigate the spare capacity of the DOAS units, since design engineers usually carry a safety factor in their designs. Other mitigation strategies could include reduced building occupancy, or increased filter efficiency.
| Can you talk to outside air versus ACH, is their any guidance on this? | For further information, please see https://www.ashrae.org/file%20library/technical%20resources/covid-19/ashrae-building-readiness.pdf
| If you are looking at reduced occupancy of the building due to social distancing does this not help the cooling load and hence the opportunity to increase outside airflow without too much energy penalty? | Yes, this is a reasonable assumption.
Building Operation
| Operating HVAC 24/7 carries a significant cost impact. If building is lightly occupied with temp checks, masks, sanitization, social distancing, good ventilation/outside air maximized, and merv 13 filters is it OK to just modify the start and stop times rather than 24/7? How much of a risk is really mitigated | Our current guidance indicates that 24/7 operation is not necessary.
| If owners don't have the funds to implement most of the necessary measures right away, should they not reopen buildings until the measures are implemented? | This decision should be made after a safety/ benefit analysis has been done with your building readiness team.
| should the bldg be operated 24/7 during ECIP | Our current guidance indicates that 24/7 operation is not necessary.
| Operation during Pandemic: Extended hours ventilation-24/7 and disable DCV? | Our current guidance indicates that 24/7 operation is not necessary, and we do recommend temporarily disabling the DCV control strategy.
| Lot of Class B office buildings have millions of dollars in deferred maintenance. How are they going to find budget for these additional recommendations? This may not be practical. | This decision should be made after a safety/ benefit analysis has been done with your building readiness team.
| We've been talking in the past few years about energy efficiency on the hvac systems, we should have control systems in place to efficiently run our systems. Now you're telling us to run systems 24/7, isn't that "overkill"? | Our current guidance indicates that 24/7 operation is not necessary.
| Is there any guidance on air change rates for occupied times - and if the current system can not handle it, should small space re-circulation filters be used? | There is not a stated air change rate requirement for non-healthcare buildings.
| To add. so whats better, less ventilation/ air movement with UV or more ventilation without UV. Same things applies to MERV 13/14 filters. More ventilation wiht MERV 8 or less air with MERV14. Whats better | This is a safety/ benefit analysis when reviewing mitigation strategies.
| What are some key components to look at when analysing systems? | For further information, please see https://www.ashrae.org/file%20library/technical%20resources/covid-19/ashrae-building-readiness.pdf
| do you have any guidance on how to control the pressure hierarchies of a building | Based on our understanding, this issue is not covered by the ETF guidance for non-healthcare buildings.
| Do you think occupant-count sensing at the zone level can be a better way to ensure that fresh air is distributed where occupants really are? This may help with the coil & fan capacity related issues - without really increasing the total outdoor air significantly. | This is a reasonable approach if you have these controls in place.
| What is the evidence behind 24 hour operation? It appears SARS-CoV-2 does not linger in air for longer than approximately 8 hours with a significant drop in viable particles over time. So with this in mind, how does overnight operation provide any added benefit? | Our current guidance indicates that 24/7 operation is not necessary.
| Thanks for the clarification on the 24 hour operation question. That wasn't necessarily clear in the ASHRAE guidance - would be great to make that more apparent in the official guidance! | We will take a look at adding this to the ASHRAE guidance documents.
| How about occupancy sensing/ counting as in input to operating strategy | This is a reasonable approach if you have these controls in place, but we still recommend bringing in the minimun outside air requirment as stated in ASHRAE Standard 62.1.
| is it possible to prioritize mitigation needs and efforts by importance or impact (i.e., ventilation, filtration, humidification, UVGI, etc.)? | This is a safety/ benefit analysis when reviewing mitigation strategies. Each system/ building is different.
| how much supply air and exhaust air we will keep in a core labs ...in terms of percentage. and also air change in order to decrease covd19 transmission shall we consider negative pressure inside buildings bcz of covd19..... | Labs are inherently designed to take into account the safety of the occupant. This needs to take into account the types of buildings systems and climate zone. We are not recommending that the building should be operated at a negative pressure relative to the outdoors.
| I would like to know which could be the best mitigation strategies for the Climate Zone 1A. | Climate is one consideration, but also need to consider building type and existing systems to evaluate mitigation strategies.
| Should we look in to air distribution patterns? E.g. location of supply and return air outlets | Yes, it needs to be evaluated, but there are too many variables at play here to discuss it. Consider consulting a professional who does CFD modeling.
| Is there any recommendation for diffusers and return grills location? | Yes, it needs to be evaluated, but there are too many variables at play here to discuss it. Consider consulting a professional who does CFD modeling.
| Do we need to worry about exhaust systems in restrooms? | Confirm that restrooms are negative pressure relative to the adjacent spaces.
| If a building does not have central air but operable windows, can we still occupy it but with windows open? | There are too many variables here to discuss. Consider having the building evaluated by a local professional.
Virus
| If the migration is by droplet, how the hvac retrofit can help? | Distribution paths- droplet, aerosol, and airborne, are still being evaluated. Current research indicates that airborne transmission is likely.
| What do you say about the fact that there has not been one reported case of airborne transmitted COVID by either the CDC or WHO? | Distribution paths- droplet, aerosol, and airborne, are still being evaluated. Current research indicates that airborne transmission is likely.
| How to quantify (measure) the viruses? | Virus quantification involves counting the number of viruses in a specific volume to determine the virus concentration.
| Also, can you share the reference for the 1-4um virus particle size. | Although the virus is around .125 microns in diameter, it tends to clump in particles that are 1-4 microns in size. For more information, see https://www.nature.com/articles/s41467-020-16670-2
| To be clear, there are studies underway but we don't actually know the viability of the virus to be "ingested" into a system via a return and exit the supply. Is that correct? In other words we don't yet know if it will be viable in system that has had no modifications.? | For more information, see https://www.medrxiv.org/content/10.1101/2020.06.26.20141085v1
| I understand the difference between contact/ fomite spread and airborne spread via aerosols. For commercial buildings do you have a view on what proportion is by which route? | We do not have information on this subject matter.
| TB is airborne so are you saying COVID 19 acts the same as TB since you keep saying it is airborne? | For more information, see https://www.medrxiv.org/content/10.1101/2020.06.26.20141085v1
| If Covid 19 is being found in fecal matter, can we conclude that it can survive a trip through the human digestion system? | Yes.
Other Cleaning
| Is it safe to use products such as SaniSolve or Puritex on filters or coils to help kill virus that lands on those surfaces inside the AHUs? The thought is to prevent live virus from being spread by the AHU. | Review the N-list provided by the EPA. https://www.epa.gov/pesticide-registration/list-n-disinfectants-use-against-sars-cov-2-covid-19
| Is duct cleaning necessary? | This is not necessary.
Humidity
| I have a question that how relative humidity between 40 to 60 effects growth of covid and is it 3 ach is enough for safety quality air condition in the building?? | Research indicates maintaining space relative humidity between 40-60% decreases virus infectivity. The calculations for the determination of 3 ACH is in the Building Readiness Guide, see https://www.ashrae.org/technical-resources/building-readiness#ventcontrol
| in sudan (north africa), we use evaporative cooler as low-cost and low-energy consuming hvac solution, but it comes with the high humidity problems. is there any way to over come the high humidity aspect, and keep using the evaporative cooler, espically in COVID-19 isolation/treatment centers ? | Humidification up to about 60% RH is considered to be protective in comparison to low relative humidity. Evaporative coolers increase humidity. To the extent that they move air in occupied spaces, they may have some role in disease transmission, but studies to date have not indicated high probability of space to space COVID-19 transmission. That said, we know of no studies to date specifically on this type of system.
| Can you give us your view on air conditioning systems with 100% return air. Does temperature and humidity play a role on your body's defense system (mucous), what's ashrae view on that? | Research indicates maintaining space relative humidity between 40-60% decreases virus infectivity.
| Do you have a reference or study that supports the RH effect on COVID19? I'm interested on looking more into this topic. | Please see this link, https://www.theglobeandmail.com/canada/article-researchers-look-at-how-humidity-can-impact-virus-transmission/
| You mentioned 40-60% humidity as being the ideal zone for the virus. Can you comment or link the research this came from? | Research indicates maintaining space relative humidity between 40-60% decreases virus infectivity.
HVAC Equipment
| Have there been any documented cases where infection was attributed to the HVAC system duct supplied air? Not air currents created in the space | The mode of transmission for infectious cases is not being tracked. For more information, see https://www.medrxiv.org/content/10.1101/2020.06.26.20141085v1
| AHU Fixed plante energy recover heat exchanger are safer than the ones with Energy Recover Wheel? | For more information, please see https://www.ashrae.org/technical-resources/resources#energy
| What is your opinion on the continued operation of heat recovery wheels and the potential to have some leakage from the exhaust to outdoor air? | If the unit is well-maintained, ASHRAE is advising that the unit continue to run. Check the seals and adjust pressure differential, such that any air "leakage" is from the supply to the exhaust side.
| Also, why is the HVAC being considered because it has also been proven that there has not been any transmission of COVID or even influenza via HVAC ducts? | The mode of transmission for infectious cases is not being tracked. For more information, see https://www.medrxiv.org/content/10.1101/2020.06.26.20141085v1
| If you have an existing VRF system with multiple indoor units,what would be the best filter upgrades consideration a maximum air velocity of 1200ls max at about 28mmAq of ESP? | Consult with the manufacturer to see what the unit is capable of handling.
| When we examine the increases in pressure differential across the filter and thus fan horsepower for replacing MERV 8 with MERV 13, and then also ask for increased the air flow, it may be beyond the capabilities of many existing air handling units. | These are all issues that need to be accounted for in the building readiness team review of the building systems.
| Any recommendations for a chilled beam building? I'm limited by zone humidity in the summer. In the winter I will see RH below 35%. | The building needs to be evaluated for dew point control. All HVAC system components will need to be included in the evaluation.
| Have there been studies to determine if COVID or similar sized particles will transmit from the exhaust stream into the supply stream via a heat recovery wheel? | If the unit is well-maintained, ASHRAE is advising that the unit continue to run. Check the seals and adjust pressure differential, such that any air "leakage" is from the supply to the exhaust side.
| Do condensate drain pans present additional problems? | No more than usual.
| In other webinars I've heard talk of disabling energy recovery to avoid crossover between supply and exhaust. It seems like this is counterproductive as this reduces OA capacity. To me, the focus should be adjust balancing so the pressures at the ERV ensure crossover is only from supply to exhaust. This increases ERV OA capacity significantly. | Correct. If the ERV is well-maintained, ASHRAE is advising that the unit continue to run. Check the seals and adjust pressure differential, such that any air "leakage" is from the supply to the exhaust side.
| i want to remind to the speaker that if we r flushing the OA are we precooling it because if we do not precool it the cooling coils inside the building cannot dehumidify that temp | Understood. It sounds like you understand the systems that you are referring to. We don't take exception to your evaluation. ERV systems need to be well-designed and well-maintained.
i beg to differ with the speaker, even if we do not have a chiller we can use dx- DOAS SYSTEM with heat recovery wheel and heat pipe in hot and humid climate and with enthalpy wheel we can remove much of latent from ambient air the mixed air temp will be around 30 deg c and the cooling coil of air handler cannot handle
i believe that the best would be to increase the OA. using DOAS system with a configuration of HRW with HEAT pipe. i did a energy analysis on how much can we save on energy side if we use DOAS systems kindly provide your email i can send my analysis
| For non medical buildings, with old (30 plus year old AHUs), is 4 air change overs an hour, (ACH) still acceptable for P-ECiP? | There is not enough detail in this question to provide a concise answer.
| Purging function of the recovery wheel, will the air stream return to the same stream or cross over to the opposite air stream? | The purge cycle on an energy wheel typically flows from the intake into the exhaust air stream.
| Would adding a gas fired heater to heat return air or outside air to 150 degF and then cooling it down to 80 degF before it gets in the AHU be effective? Can we kill the virus with high heat? | Theoretically yes, however, they may be a high energy penalty for doing this.
| Possibly use reheat for dehumidification in spite of energy code requirements in emergency mode? | This seems like a reasonable approach during epidemic conditions.
Plumbing/ Water Systems
| Domestic Hot Water (DHW) Systems: flushing may not/will not rid your piping system if water has been stagnant for a while. Legionella bacteria may already be resident in the biofilm within the piping interior and therefore, other solutions/measures are required. | We agree that systems should be tested.
| Why do you need to look at water systems when talking about the spread of an infectious aerosol? | It is not so much the spread of an infectious aerosol, but if the building sits unoccupied for a considerable length of time, there may be issues other than HVAC that may need to be attended to.
| Off-topic, but regarding P-ECiP, are you aware of procedures for the drainage systems (stagnant lines, controlled flushing of surface drainage, etc.)? | There are resources available, and we will be trying to incorporate these into the next revision of the Building Readiness Guide.
Controls/ Energy
| How much energy consumption will increase if there is any study. Owners would like to know the price tag. Everyone is under differed maintenance and no rent for 3 months they do not have toomuch money to spare. | This is a system by sytem analysis. There is no rule of thumb.
| Any thoughts on clustering recommendations or mitigating Engineering Control recommendations? IE, including some partitions or localized air cleaners (Air Purifiers) between people seated or clustered closely. | Yes, the analysis should consider engineering controls.
| There should be some mention of cybersecurity for ICS (industrial control systems) cybersecurity measures/controls to prevent unauthorized access or DDoS, which could be catastrophic for building owner and tenants. | Yes, we agree.
| There will be increased operating expenses (increased kWh) from many of these engineering controls actions . What can we do to offset those increased costs? This has a significant impact for small business in particular. | Consider operating your building for occupant safety. A safety/ benefit should be completed for the specifics of your building, occupants, and activities.
Codes/ Standards/ Government
| Is ASHRAE planning a mandate to retrofit building especially public areas, like restaurants, etc. to improve air filtration, adding air cleaners, change ventilation requirements, etc.? | Not at this time. ASHRAE does not mandate, but can make recommendations for best practices. Standards can be referenced in codes.
| Excellent information! Has there been any states that have considered putting some of these extra Mitigation recommendations into code? | Not that we are aware of.
| NY Governor is asking malls and offices to install hepa filters. Is this required? | That is based on the authority having jurisdiction in that area.
| When does CA require Marv 13 anyway? | Title 24 2019 Part 6, requires MERV 13. This was rolled out in January of 2020.
| Do you think there should be a certification for IAQ in order to open buildings safely for post epidemic scenario, both for existing and new buildings? | This is an interesting proposition. Due to the variety of building types, hvac systems, and many other factors this would take a long time to develop and implement.
| What are your thoughts regarding some of the non-mechanical system related mandates such as scanning and tracking, and how they relate to the integration into the control systems. What comes to mind is how and when to sanitize certain spaces to mitigate spread. | This is something being considered for public restrooms to sanitize via UVC between uses.
Miscellaneous
| If the current owner doesn't bring their building into a healthy condition, the next owner will. | We hope they do.
| Can the inspection process be combined with recommissioning, especially if design and/or system parameters may change? | Absolutely
| one of the obvious assertions that comes from the Guanjho restaurant is that drafts can be an issue, does ASHRAE recommend rebalance of HVAC systems or running room AC units on low speed? Desk fans? | There are other analysis of that incident that showed the units had poor filtraiton and the space did not meet code minimum (per US standards) ventilation rates.
| How to improve elevator car ventilation? | There are examples of using portable HEPA fitlers with UV in the car. We do not know of any study showing its effectiveness since people are touching many surfaces and in close proximity.
How to improve elevator car ventilation for existing building?
| Sarah - you did not mention modeling airflow patterns in rooms. Do you consider this important? | This is a great tool to evaluate airflow patterns in the space.
| What guarantees the quality of OA? How will the quality of the OA be checked and if contaminated how will it be treated? | The quality of OA should have been checked during its design or normal mainenance. That issue should already be known to the Owner, and the guidanace talks about not increaseing OA if your air quality is poor.
Clarifications
| What is "TAB"? | Testing, Adjusting & Balancing
| What does epidemic condition in place mean? Is that based on a certain R-0 rate in our region? | This is based on the public authority declaration at this time. This could be expanded in the next phase of work for the Epidemic Task Force.
| Re: 1$ / 10$ / 100$ / 1000$ ---- I missed what the $10 and $100 represented. | $10 was construction cost, and $100 was operating cost
| After installing air filter or UV setup, how do you test and validate to make sure it is better than before? Is there any recently tested data? | You could perform an integrity test for your filters after the ugrade. You could also test the air quality before and after the installation.
| How do you think the new social distancing and new acrylic or material barriers in the built space affect the HVAC flows and energy use? | CFD would be a great tool to evaluate the acrylic barriers. As for the impact on energy, that would be based on the HVAC systems for that building.
| What should take priority- higher OA or maintaining temp/humidity? | Standard 55 provides a range for what is considered good indoor comfort conditions. This is part of the safety benefit analysis for that system.
Administrative
Can the other presenters mute their mic when not presenting? There is feedback from one of their mics
There is a very bad echo!
Hey. Thanks for your time today bringing us this presentation. I tried to download the documents from pg 13 of PPT Pres. the "Position Document" worked, but the link to "Emerging Issue Brief" does NOT work, and the third link doesn't work either
I got the link from a friend, so I'm not sure if I am signed up. Can you let me know about getting the slide deck. Martin.Nolan@gmail.com