## Slide 1
Cold-Climate Design 101
For Decarbonization
Center of Excellence for
Building Decarbonization (CEBD)

## Slide 2: Agenda
Introduction
Cold-Climate Challenges
Cold-Climate Solutions
Design to Reduce Emissions
ASHRAE Update

## Slide 3
Introduction

## Slide 4: Global building sector energy-related CO2 emissions, 2021
Source: IEA 2022. All rights reserved. Adapted from "Tracking Clean Energy Progress" (IEA 2022f). https://www.unep.org/resources/publication/2022-global-status-report-buildings-and-construction

## Slide 5: Net GHG Emissions Reductions Needed to Minimize Catastrophic Climate Change
Source: IPCC AR6 Synthesis Report on Climate Change 2023. All rights reserved. https://www.ipcc.ch/report/ar6/syr/figures/figure-spm-5

## Slide 6: Directly Impacting The Work Of ASHRAE Members
Source: United States Centers for Disease Control and Prevention. All rights reserved. https://www.cdc.gov/climateandhealth/effects/default.htm

## Slide 7: Directly Impacting Health Safety Comfort
Source: United States Centers for Disease Control and Prevention. All rights reserved. https://www.cdc.gov/climateandhealth/effects/default.htm

## Slide 8: Building Performance Standards Driving Local Emissions Reduction Requirements
Source: DOE Office of Energy Efficiency and Renewable Energy. https://www.energycodes.gov/sites/default/files/2023-12/Building_Performance_Standards.png

## Slide 9
Source: US Environmental Protection Agency
Source: US DOE
SEC Emissions Reporting Requirements
Publicly Traded Companies FY2023

## Slide 10
Eliminating GHG emissions from the built environment is essential to address climate change
ASHRAE’s position…
Notes: ASHRAE’s position is simple. Eliminating GHG emissions from the built environment is essential to address climate change.

## Slide 11
2050
All new and existing assets must be net zero GHG emissions across the whole life cycle
2030
The global built environment must halve its 2015 GHG emissions
All new buildings must be NZE
Widespread EE retrofits of existing assets
New construction embodied carbon must be reduced by at least 40%
ASHRAE goals…
Notes: By 2030, the global built environment must halve its 2015 GHG emissions, whereby
all new buildings must be net zero GHG emissions in operation,
widespread energy-efficiency retrofits of existing assets must be well underway, and
embodied carbon of new construction must be reduced by at least 40%.
By 2050, at the latest, all new and existing assets must be net zero GHG emissions across the whole life cycle.

## Slide 12
Cold-Climate Challenges

## Slide 13
Challenge 1:
Buildings in Colder Climates Use more Energy (Especially heating) = More Energy End use to decarbonize
Source: U.S. Energy Information Administration, 2020 Residential Energy Consumption Survey (RECS)
Note: Average temperature derived from National Oceanic and Atmospheric Administration (NOAA) weather data for RECS sampled households.
Three Big Challenges: And All Three relate to Temperature

## Slide 14
Challenge 1:
Buildings in Colder Climates Use more Energy (Especially heating) = More Energy End use to decarbonize
Source: U.S. Energy Information Administration, 2020 Residential Energy Consumption Survey (RECS)
Note: Average temperature derived from National Oceanic and Atmospheric Administration (NOAA) weather data for RECS sampled households.
Three Big Challenges: And All Three relate to Temperature

## Slide 15
Challenge 2:
Air-Source Heat Pump Capacity Drops with Outside Air Temperature
Source: U.S. Energy Information Administration, 2020 Residential Energy Consumption Survey (RECS)
Note: Average temperature derived from National Oceanic and Atmospheric Administration (NOAA) weather data for RECS sampled households.
Three Big Challenges: And All Three relate to Temperature

## Slide 16: Three Big Challenges: And All Three relate to Temperature
Source: U.S. Energy Information Administration, 2020 Residential Energy Consumption Survey (RECS)
Note: Average temperature derived from National Oceanic and Atmospheric Administration (NOAA) weather data for RECS sampled households.
Challenge 2:
Air-Source Heat Pump Capacity Drops with Outside Air Temperature

## Slide 17
Challenge 3:
Air-Source Heat Pump Efficiency Drops with Outside Air Temperature
Source: U.S. Energy Information Administration, 2020 Residential Energy Consumption Survey (RECS)
Note: Average temperature derived from National Oceanic and Atmospheric Administration (NOAA) weather data for RECS sampled households.
Three Big Challenges: And All Three relate to Temperature

## Slide 18: Three Big Challenges: And All Three relate to Temperature
Source: U.S. Energy Information Administration, 2020 Residential Energy Consumption Survey (RECS)
Note: Average temperature derived from National Oceanic and Atmospheric Administration (NOAA) weather data for RECS sampled households.
Challenge 3:
Air-Source Heat Pump Efficiency Drops with Outside Air Temperature

## Slide 19: The Grid Challenge: Emissions Factors
Source:
https://www.epa.gov/egrid/data-explorer
Notes: Many of the colder regions also have higher grid emissions factors, compounding the challenge of decarbonization

## Slide 20: The Existing Building Challenge: The need for efficiency
Source: https://www.architecture2030.org/intervention-points/

## Slide 21
Cold-Climate Solutions

## Slide 22
Building Decarbonization
  whole life = operational
  + embodied

## Slide 23: Solution 1: Enhanced Enclosure Efficiency
Source: ASHRAE 2022 Advanced Energy Design Guide for Zero-Energy Multifamily Buildings

## Slide 24: Solution 2: Heat/Energy Recovery (AirSide)
Source: ASHRAE 2020 Advanced Learning Institute Air-To-Air Energy Recovery Applications: Best Practices

## Slide 25: Solution 2: Heat/Energy Recovery (Waterside)
Source: Image Courtesy SmithGroup

## Slide 26: Solution 2: Heat/Energy Recovery (Sanitary-Side)
Source: DC Water Headquarters Image Courtesy SmithGroup

## Slide 27: Solution 2: Heat/Energy Recovery (Sanitary-Side)
Source: DC Water Headquarters Image Courtesy SmithGroup

## Slide 28: Solution 3: Right-Sourcing (GSHP)
Source: Image Courtesy SmithGroup

## Slide 29: Solution 3: Right-Sourcing (Networked District)
Source: Image Courtesy SmithGroup

## Slide 30: Solution 4: Advanced Cold-Climate Heat Pump Technologies
Source: Image Courtesy SmithGroup

## Slide 31: Solution 4: Advanced Cold-Climate Heat Pump Technologies (Enhanced Vapor Injection)
Source: Pacific Northwest National Laboratory
1
2
EVI Main Components
Compressor with two suction ports, one in the middle of the scroll to suck saturated vapor, and a traditional suction port for low temp low pressure vapor.
Subcooler (heat exchanger) to extract residual heat from the high-pressure liquid line to warm up some low-pressure liquid refrigerant into a saturated vapor.
EVI is an important technology for enhancing low temperature performance of heat pumps
Notes: Not all cold climate heat pumps have or utilize EVI. But EVI is an important technology for enhancing low temperature performance of heat pumps.
Example subcooler, part.
https://sdecoice.en.made-in-china.com/product/UyaxXzVogMcm/China-Slhe-Series-Refrigerant-Suction-Line-Copper-Tube-Heat-Exchanger.html

## Slide 32: Solution 4: Advanced Cold-Climate Heat Pump Technologies (Inverter-Driven Compressors)
Source: Pacific Northwest National Laboratory
Previously
Heat pumps and furnaces relied on 1 or 2 stages of heating to meet the desired setpoint. Full power, half power, and off.
Now
Inverter-driven heat pumps rely on variable-speed operation, allowing them to modulate themselves to maintain a constant setpoint while using less energy. 100% power can modulate down to 0% power, or anywhere in between.
Photo: inverter-driven heat pump installed in PNNL field site in Cordova, AK

## Slide 33: Solution 4: Advanced Cold-Climate Heat Pump Technologies (Optimized Controls to Significantly Improve Performance)
Source: Northwest Energy Efficiency Alliance
Controls Impact - "Old" and "New"
"Old" product: dramatic cycling at virtually all load conditions
"New" product: modulates as expected
Under identical testing conditions, the same equipment with new control strategies resulted in a dramatic improvement in efficiency.

## Slide 34: Solution 5: Advanced Cold-Climate Heat Pump Technologies (Next Generation Cold Climate Heat Pumps)
Source: Pacific Northwest National Laboratory
CCHP Challenge: https://www.energy.gov/eere/buildings/residential-cold-climate-heat-pump-challenge
Field testing of a new heat pump product provides reliable high-efficiency heating performance in cold climates.
Notes: Driven by:
Use of EVI, Larger evaporators and condensers for the rated capacity, and Smarter control logics

## Slide 35: Solution 6: Advanced Cold-Climate Heat Pump Strategies (Pairing with Storage)
Source: Images Courtesy of SmithGroup
Notes: Saving energy during the peak Maintaining heating/cooling capacity during the extreme/critical hours

## Slide 36
Design to Reduce Emissions

## Slide 37
Source: Images Courtesy of SmithGroup
Cold-Climate Design Criteria: Target Emissions Parity

## Slide 38: Cold-Climate Design Criteria: Target Emissions Parity
Source: Images Courtesy of SmithGroup
MIN. HEAT PUMP COP FOR CARBON EQUIVALENCY

## Slide 39: Cold-Climate Design Criteria: Target Emissions Parity
Source: Images Courtesy of SmithGroup

## Slide 40: Cold-Climate Design Criteria: Target Utility Cost Parity
Source: Images Courtesy of SmithGroup
https://electrification.ornl.gov/

## Slide 41: Cold-Climate Design Criteria: Target Utility Cost Parity
Source: Images Courtesy of SmithGroup

## Slide 42: Cold-Climate Design Criteria: Target Utility Cost Parity
Source: Images Courtesy of SmithGroup

## Slide 43: Cold-Climate Design Criteria: Pick the Right Refrigerant
Source: Images Courtesy of SmithGroup

## Slide 44: Cold-Climate Design Criteria: Pick the Right Refrigerant
Source: Images Courtesy of SmithGroup
  100x 1-Bedroom
  100x 2-Bedroom
  ASPE
    Peak: 1,433 gph for 3 hours
    Off-peak: 158 gph for 8 hours

## Slide 45: Cold-Climate Design Criteria: Pick the Right Refrigerant
Source: Images Courtesy of SmithGroup
  100x 1-Bedroom
  100x 2-Bedroom
2,750 Gallons of Storage
(@ 140F)
4 Air-Source R-134a Heat Pumps
4 x 70 A CB @ 480v
176 KVA
COP ~<2 @ 5F OAT
COP: 4.1 @ 40F OAT

## Slide 46: Cold-Climate Design Criteria: Pick the Right Refrigerant
Source: Images Courtesy of SmithGroup
  100x 1-Bedroom
  100x 2-Bedroom
1,500 Gallons of Storage
(@ 180F)
2 x C02 Heat (R744)
2x 125A CB at 480v
138KVA
COP 2.2 at 5F OAT
COP 3 at 40 F OAT

## Slide 47: Cold-Climate Design Criteria: Pick the Right Refrigerant
Source: Images Courtesy of SmithGroup
  100x 1-Bedroom
  100x 2-Bedroom
2,750 Gallons of Storage
(@ 140F) + ~2,250 Gal Waste Storage Below Grade
2 x Waste Heat Recovery Heat Pump (R-513a)
2x 110A CB @ 480v
88 kVA
COP 4.1

## Slide 48: Cold-Climate Design Criteria: Right Size For the Load Profile
Source: Images Courtesy of SmithGroup

## Slide 49
Four Key Areas
Focused on strategy, thought leadership, industry collaboration, and public advocacy related to building decarbonization
Works with the ASHRAE councils to deliver projects
  Technology
  Education
  Research
  Standards
Center of Excellence for Building Decarbonization (CEBD)

## Slide 50: ASHRAE Published Decarbonization Guides

## Slide 51: ASHRAE Decarbonization Guides COMING IN 2025!
Expanded Version 2

## Slide 52
Thank You