## Slide 1
Decarbonization:
Retrofitting Buildings,
Reducing Emissions
Center of Excellence for
Building Decarbonization (CEBD)

## Slide 2: Agenda
Introduction
Moving Towards a Low Carbon Future
Exploring Technologies
Alternatives
Challenges
ASHRAE Update

## Slide 3
Notes: Nature is beautiful.
This forest embodies an efficient, self-sustaining system where nothing goes to waste.
Fallen leaves decompose and enrich the soil, supporting new plant growth and maintaining a balanced ecosystem.
This cycle is sustainable; it supports biodiversity and regulates ecological balance without external inputs.
Nature also uses renewable energy.

## Slide 4
Notes: We are all mostly intelligent lifeforms. We create order out of chaos.
The order we create is not reversible and not 100% efficient.
Talking Points:
Landfills are a standard method for managing human-generated waste, highlighting the scale and permanence of waste accumulation.
The negative impacts of landfills include soil and water contamination, methane emissions (a potent greenhouse gas), and the loss of usable land.
Many materials in landfills could be recycled or reused, pointing out missed opportunities for more sustainable resource management.

## Slide 5
Notes: We have done a great job of figuring out how to use our natural resources to improve our lives.
The challenge has been the growing population and whether our past ways will serve a population of 10 billion people
Without harming the environment we must live in.

## Slide 6
Notes: We're engineers... we want the calculations; we're not interested in hype or hysteria. But we do want to make sound decisions that protect the well-being of our communities and clients.

## Slide 7: Global building sector energy-related CO2 emissions, 2021
Source: IEA 2022. All rights reserved. Adapted from "Tracking Clean Energy Progress" (IEA 2022f). https://www.unep.org/resources/publication/2022-global-status-report-buildings-and-construction
Notes: The fact of the matter is that global greenhouse gas emissions are the largest contributor to climate change. This matters to us, because the building sector makes up more than a third of the global annual emissions.

## Slide 8
Eliminating GHG emissions from the built environment is essential to address climate change
ASHRAE’s position…
Notes: ASHRAE’s position is simple. Eliminating GHG emissions from the built environment is essential to address climate change.

## Slide 9
2050
All new and existing assets must be net zero GHG emissions across the whole life cycle
2030
The global built environment must halve its 2015 GHG emissions
All new buildings must be NZE
Widespread EE retrofits of existing assets
New construction embodied carbon must be reduced by at least 40%
ASHRAE goals…
Notes: By 2030, the global built environment must halve its 2015 GHG emissions, whereby
all new buildings must be net zero GHG emissions in operation,
widespread energy-efficiency retrofits of existing assets must be well underway, and
embodied carbon of new construction must be reduced by at least 40%.
By 2050, at the latest, all new and existing assets must be net zero GHG emissions across the whole life cycle.

## Slide 10
Understanding
Beneficial
Electrification
Notes: We hear a lot that all we need to do is electrify everything and the grid will take care of the rest, right? In reality, there's way more nuance in how we should approach decarbonization. One single strategy doesn't necessarily result in emissions reductions everywhere. Where is your project located? Is the grid "clean"? Does the technology you're looking at perform well in your climate zone? As engineers, we want to do the math to make sure our designs are actually reducing emissions, saving clients money, and reducing our whole-life carbon footprint. A key place to start this journey is making sure your existing building is actually working in an efficient manner.

## Slide 11: Electricity generation from low-carbon sources, 2000 to 2022
Source: Ember - Ember - Yearly Electricity Data (2023); Ember - European Electricity Review (2022); Energy Institute - Statistical Review of World Energy (2023), OurWorldInData.org/energy
Low-carbon electricity is the sum of electricity generation from nuclear and renewable sources
Notes: Low-carbon electricity sources will be essential to reduce indirect GHG emissions from the building sector.
Low-carbon electricity can come from nuclear or renewable sources such as hydropower, solar, wind, and geothermal.
The contribution of each varies from country to country.
Globally, 39% of our electricity came from low-carbon sources in 2020.
But there is a lot of variation in low-carbon electricity production worldwide.
World electricity generation has added roughly 5700 TW of low-carbon electricity generation since 2000,
increasing it by 106% in the past 22 years.
China accounted for roughly half of the global low-carbon electricity generation growth during that period.
China is set to quintuple its renewable energy installations by 2050,
shift its power mix from 30% renewables today to 88% by mid-century,
in less than a decade has increased its solar power generation from 1 to 5%, but this will increase to 38% of electricity production by 2050.
They will reduce annual emissions by 8Gt between now and 2050, which is three times as much as Europe’s emissions reductions.

## Slide 12: Electricity generation from coal, 2000 to 2022
Source: Ember - Ember - Yearly Electricity Data (2023); Ember - European Electricity Review (2022); Energy Institute - Statistical Review of World Energy (2023), OurWorldInData.org/energy
Measured in terawatt-hours
Notes: We will need to figure out how to substantially reduce emissions from the world’s reliance on electricity generation from coal.
As we look for solutions, it is important to understand why we have relied on coal in the past.
Coal has been a reliable and affordable energy source. It is abundant and easy to extract and relatively inexpensive to transport.
Additionally, it is a very efficient fuel source, meaning that a large amount of energy can be produced from a small amount of coal.
As we look to reduce GHG emissions, coal generation produces more than double the GHG
emissions when compared to combined cycle natural gas generation.
World electricity generation added roughly 4450 TW of coal electricity since 2000.
Many countries have decreased their coal generation during this period.
China’s growing economy added roughly 5600 TW of coal generation since 2000,
slightly more than the amount of low-carbon generation they added during the same timeframe.

## Slide 13: Carbon intensity of electricity, 2000 to 2022 Carbon intensity is measured in grams of carbon dioxide-equivalents emitted per kilowatt-hour of electricity
Source: Ember - Yearly Electricity Data (2023); Ember - European Electricity Review (2022); Energy Institute - Statistical Review of World Energy (2023)
OurWorldInData.org/energy
226 gCO2e
NG boiler
80% eff
Source: EPA Emission Factors for Greenhouse Gas Inventories
Notes: Carbon intensity on this chart is shown in grams of carbon dioxide-equivalents emitted per kilowatt-hour of electricity generated.
The electric grid carbon intensity has been trending downward since 2010 in many parts of the world.
Much of the reduction is due to the rapid increase of low-carbon generation and natural gas generation replacing coal generation.
Economics will continue to play a critical role in the overall solution sets as we transition towards low-carbon generation.
The energy around the globe must be accessible and affordable.
<click> The GHG carbon intensity from an 80% efficient natural gas boiler is shown. This is gCO2/kWh of output.
<click> The boiler’s actual annual operating efficiency is closer to 70% when accounting for off-standard stack losses.
The electric grid carbon intensity values typically increase by 5% to account for the electrical distribution system losses to the building.
This is why efficient electrification of heat loads will be required using heat pump technology.
A heat pump with an operational COP of 2.0 or 200% efficiency would cut the electricity carbon intensity in half per kWh of heating
Electric resistance technology would generate more emissions than natural gas boilers in many areas of the world.

## Slide 14: Electricity production by source, United States Measured in terawatt-hours
Source: Ember - Yearly Electricity Data (2023); Ember - European Electricity Review (2022); Energy Institute - Statistical Review of World Energy (2023)
OurWorldInData.org/energy
Fossil fuel
Low carbon
Notes: As we look at the US breakdown, we can see that natural gas has largely displaced coal, and there is a rapid growth in the last 10 years of renewables on the grid.

## Slide 15: California Power Mix, 2009 to 2022
Source: https://www.energy.ca.gov/sites/default/files/2023-10/California_Electrical_Energy_Generation_2001-Current_ADA%20%28for%20web%29.xlsx
2022 California Power Mix
Notes: This is a breakdown of California’s 2022 electricity mix from generation sources. More than 50% of our electricity is generated from low carbon sources.
You can see the trend for the last 14 years. Our nuclear energy dropped in 2012 while solar and wind energy more than made up for that reduction in the past 10 years. Natural gas still has the largest percentage of source generation.

## Slide 16: Local Utility Power Content Labels, 2022
Sources: https://sce.com and https://www.ladwp.com/powercontent
Southern California Edison
552 lbs CO2e/MWh
250 gCO2e/kWh
LADWP
567 lbs CO2e/MWh
257 gCO2e/kWh
Notes: Let’s break this down to your local utility level. This data is taken from the yearly power content labels. It is essential to understand the carbon content of electricity as we convert from natural gas to electricity.

## Slide 17: Average retail price of energy U.S. Energy Information Agency
Chart: $ per kWh
| U.S. Commercial | CA Commercial | U.S. Residential | CA Residential
Electricity | 0.1251 | 0.2181 | 0.1504 | 0.2584
Natural Gas | 0.037283 | 0.053125 | 0.04858 | 0.066662
Notes: In our effort to reduce emissions, we also want to keep our eye on the cost of utilities. The "spark gap" is the cost difference between delivering a btu of heat with heat pump vs a gas boiler. If you don't beat the spark gap, your client will see increased utility costs, which is not our goal. The spark gap is another driver in why retro-commissioning is a key step to improve building performance before doing any electrification projects.

## Slide 18: Pillars of Beneficial Electrification
Help the Environment
Energy
Efficiency
Renewable Energy Integration
Improve the Quality of Life
Grid Responsiveness
Save
Money
Reduce overall greenhouse gas emissions
Upgrading buildings to use energy more efficiently
Use of energy generated from renewable sources
Improves IAQ without onsite combustion emissions
Enhancing buildings' ability to respond to grid demands
Potential to reduce building utility costs
Audience
Participation
Notes: ASK the audience to provide reasons for electrifying buildings before showing the text.

## Slide 19
Understanding
Whole Life
Carbon
(WLC)

## Slide 20
Building Decarbonization
  whole life = operational
  + embodied
Notes: One really important aspect of decarbonization is that operational emissions aren't the whole story; when aiming for true decarbonization, we need to take into account the emissions associated for the full life of our buildings and equipment.

## Slide 21
Source: BS EN 15978:2011
Building lifecycle stages
PRODUCT
CONSTRUCTION
MAINTAIN AND USE
END OF LIFE
BEYOND THE LIFECYCLE
STAGES
GHG
EMISSIONS
TIME
MODULE
EMBODIED
CARBON
EMBODIED
CARBON
EMBODIED
CARBON
EMBODIED
CARBON
EMBODIED
CARBON
OPERATIONAL
A1
A2
A3
A4
A5
B1
B2
B3
B4
B5
B6
B7
C1
C2
C3
C4
D
RAW MATERIAL SUPPLY
RAW MATERIAL TRANSPORT
MANUFACTURING
TRANSPORT TO SITE
CONSTRUCTION
USE
MAINTENANCE
REPAIR
REPLACEMENT
REFURBISHMENT
ENERGY USE
WATER USE
DECONSTRUCTION
END OF LIFE
TRANSPORTATION
WASTE PROCESSING
DISPOSAL
REUSE - RECOVERY
Notes: Lately, there has been a lot of discussion around whole-life carbon emissions based on the life cycle of a building.
As we can see from the left side of this figure, building GHG emissions are locked in place as soon as a building is built, even before its operation
[click] This starts with extract, transport to the factory, and manufacture during the product stage
[click] to the construction stage transporting to the site and constructing the building.
[click] We have both embodied and operational emissions during the maintain and use stage.
The operational carbon is energy and water-related emissions during the use of the building.
Equipment replacements and building renewals add additional embodied carbon during this stage.
[click] It doesn't stop there, we also have embodied emissions at the end-of-life stage due to demolishing the building, hauling away the waste materials, and whether we send it to a landfill or recycle.
[click] The last stage is beyond the lifecycle that covers the emissions for reuse and recovery.
[spend some time on this slide – especially at the end – the idea of a circular economy – remember Edward McDonough – Architecture 2030. He gave our keynote at COP27 this year. Edward wrote a book called Cradle-to-Cradle. The circular economy is the same idea. He used the example of nature and specifically a tree as being one of the most sustainable – self sufficient organisms on the planet. It grows, sheds leaves to feed the microorganisms under it to create its own fertilizer and continues to perpetuate itself year after year. There is no waste in nature – the idea behind the circular economy – no waste – everything is recyclable in some way]
Reducing both embodied and operational carbon in buildings is critical to achieving a more sustainable and low-carbon future.
Governments and other organizations are beginning to understand the importance of evaluating means to reduce embodied and operational emissions.

## Slide 22: Refrigeration Equipment Greenhouse Gas Emissions EN 15978
B6: Energy
Operation Carbon
B1: Refrigerant
Embodied Carbon
A1-A5:
Embodied Carbon
CO2e
CO2e
CO2e
Notes: In this graphic, you can begin to see which portions of energy use related to which whole life carbon category. The energy that was needed to manufacture and deliver the heat pump to site fits into the A1-A5 Embodied carbon category. The refrigerant leaks over the lifespan of the equipment falls into the B1 category, while the emissions from the purchased electricity to run the heat pump fits into B6, Operating emissions.

## Slide 23: Refrigerant Greenhouse Gas Emissions
GHG Emissions =
Refrigerant Charge x Annual Leakage Rate x GWP
  Can calculate it per year in lbs or kg
  Can also calculate it over the life of the building
ASHRAE Fundamentals Handbook Chapter 29, Refrigerants
  Specifies GWP100 for various refrigerants using IPCC (2013)
Standard 228 – Standard Method of Evaluating Zero Net Energy and Zero Net Carbon Building Performance
  Specifies annual leakage rates for various system types
Notes: ASHRAE has great reference resources to help you calculate the refrigerant emssions as you can see on this slide. In addition, there is a research project now running to update these values and get better longitudinal understanding of whole life leakage characteristics.

## Slide 24: Refrigerant Greenhouse Gas Emissions
GWP of Select Refrigerants, IPCC AR5 (2013)
Propane
CO2
*Breaks down into trifluoroacetic acid (TFA)
*
Notes: One key strategy to reduce the impact of refrigerant leaks is through the selection of lower GWP refrigerants. As you can see, R410 is nearly 2,000x more potent of a greenhouse gas than some of the A2L synthetics, CO2 (R-744) or even Propane (R-290)

## Slide 25: Refrigerant Greenhouse Gas Emissions
Equipment Type | Annual Leakage Rate
Water chillers | 5%
Hermetic units | 1%
Rooftop air conditioner | 6%
Residential HP or AC | 2%
VRF | 10%
Commercial condensing units | 15%
ASHRAE Standard 228-2023
Typical Annual Refrigerant Leakage Rates by Equipment Type
Notes: Research is ongoing to update the leakage rates in the Standard 228 leakage rate tables, but these can be used to help you with your calcs. One key consideration during a Retro-commissioning project is not only check the operational performance of the equipment, but also check historical service records for refirgerant leakage. Not only does refrigerant leakage cause GHG emissions to increase, but leakage can also be an indicator of a soon-to-fail piece of equipment.

## Slide 26: Refrigerant Greenhouse Gas Emissions
Use of low-GWP refrigerants
Enhanced energy efficiency
Innovative non-refrigerant technologies
Lower refrigerant volume
Regular maintenance and leak prevention
Refrigerant management and recycling
Reducing Refrigerant Emissions
For ways to reduce refrigerant leakage, refer to REAL Zero booklets at www.realzero.org.uk
Notes: There are a lot of ways to reduce refrigerant emissions, and many of those are also efforts that can be implemented during a retro-Cx project.

## Slide 27
Considering
Decarb Retrofit
Alternatives

## Slide 28
Considering
Decarb Retrofit
Alternatives

## Slide 29: Typical Decarb Retrofit Barriers
Equipment costs
Equipment footprints
Design team expertise
Age of existing buildings
  Electrical capacity
  Service upgrades
Ownership/lease structures
Utility interaction & upgrades
  Wait times, distribution congestion
Power reliability/resilience
Refrigerant embodied carbon
Notes: You will hear a lot of barriers to electrification on projects. Nearly all of them can be improved by first going through a retro-commissioning process. Getting your building to be in top-notch working condition will provide the imformation needed to delivery a cost effective design. Many buildings have drifted out of their originally designed parameters.... which wastes energy and will continue to waste energy even after a decarb retrofit.

## Slide 30: The lens we look through determines what we see…
Simple payback
1:1 equipment replacement
My engineer says, ”It can’t be done.”
Electrify all
at once
Wait for better technology
I have “THE” solution!
Electricity produces emissions
Too
disruptive
Decarb is
not possible
Long term capital planning
Partial electrification and right size equipment
Phase in measures over time
Start with partial electrification
Start now
with enabling steps
There is no “ONE” solution!
Electricity grid is rapidly decarbonizing
Decision tree, phased approach
Decarb is viable

## Slide 31: Why not a 1-for-1 replacement?
There is nothing so useless as doing efficiently that which should not be done at all.
Peter Drucker
Notes: When approaching a project, whatever you do, don't just do a 1-for-1 replacement of the existing equipment with an equally sized heat pump. You'll waste money, and leave a lot of performance improvement opportunities on the table.

## Slide 32
01
Data
Collection
On-site Inspections
Analysis and Reporting
Selection and Implementation
02
03
04
Understand how the building operates and set targets & RCx
Existing equipment assessment
Emission reduction measures
Choose the right set of strategies
GHG Emissions Reduction

## Slide 33
01
Data
Collection
02
Existing equipment assessment
GHG Emissions Reduction
Compile building documentation and energy data
Calculate GHG emissions
Set building-level GHG emissions reduction targets
RCx Systems First!
UNDERSTAND
Notes: Compile building data
As-built drawings
Equipment inventories and cut sheets
Property condition assessments and capital plans
Refrigerant leakage and repair documentation
Prior energy or GHG emission reduction audits (completed within the past five years)
Access to data from a building automation system
Calculate Scope 1 and 2 Emissions
The historical energy consumption data can be used to calculate the building’s Scope 1 and 2 emissions.
The owner and auditor should agree on applicable GHG emissions factors for all energy sources prior to the detailed analysis portion of the audit.
Industry standard emission factors are published by the U.S. Environmental Protection Agency (EPA) and Intergovernmental Panel on Climate Change (IPCC).

## Slide 34
01
Data
Collection
02
Existing equipment assessment
RCx and Verify Operation
Notes: Gather trend data and verify installed systems are even operating as intended. Adding expensive heat pumps to cover fantom loads will not reduce emissions or save money.

## Slide 35
01
Data
Collection
02
Existing equipment assessment
RCx and Verify Operation
Installed Capacity
Notes: In this case, local distribution equipment was over sized... this gives us options to either resize during the retrofit, or more likely gives us more room to optimize supply water temperatures without needed expensive upgrades on the distribution side.

## Slide 36
01
Data
Collection
02
Existing equipment assessment
RCx and Verify Operation
Notes: Comparing measured zone level 5-minute increment loads can show zones that are not operating as intended. In this case, a deadband had been narrowed too far, and the zone widly oscillated between cooling and reheat, resulting in a phantom load at the plant. Controls fixes are the cheapest first step in reducing cost.

## Slide 37
Source: Energy & Buildings, Insights from space heating hot water systems in 259 commercial buildings
Existing heating hot water system operation
Buildings in
each climate
Heating load normalized to max
Cumulative fraction of operating hours
Notes: What has been found in extensive testing of commercial buildings is that 90% of operating heating hours are running at less than 50% capacity. One of those lessons in those studies is that a lot of existing buildings aren't running well. And we want to make sure we go through extensive retro-commissioning to get the building running really well and loads are optimized.

## Slide 38
Chart: Sample Building Annual Heat Load Profile
| 0.05 | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.55000000000000004 | 0.6 | 0.65 | 0.7 | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1
Annual Therms | 77.5795 | 226.4864 | 1662.0681 | 4156.7696 | 4097.7746 | 2710.1016 | 600.245 | 257.0653 | 294.8446 | 113.9515 | 89.004 | 30.8539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative Annual Percent Consumption | 0.0054188 | 0.021238 | 0.13733 | 0.42767 | 0.7139 | 0.90319 | 0.94512 | 0.96307 | 0.98367 | 0.99163 | 0.99784 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
60-year-old building
125,000 ft2 (11,600 m2)
Mild climate
Design 22 Btu/ft2 (250 W/m2) peak
Actual 13 Btu/ft2 (148 W/m2) peak
80% of annual heating energy
consumption occurs when the load
is 25% or less
1 kWh/ft2-yr
Notes: We should strive to understand existing building annual heating load profiles before replacing boilers with electrical alternatives.
This example shows a 60-year-old building in a mild climate. Two years of trend data show the existing heating system was oversized. This is common with boiler systems.
80% of annual heating therms occur when the load is 25% or less of the installed capacity.
If the system were sized for the peak load experienced, 80% of annual heating therms would occur when the load is 42% or less.
If we are concerned about whole-life carbon, there will not be enough operational carbon savings in the lifetime of the equipment to electrify more than that 50%.
The incremental investment for the additional electrification doesn’t make sense.

## Slide 39
Chart: Sample Building Annual Heat Load Profile
| 0.05 | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.55000000000000004 | 0.6 | 0.65 | 0.7 | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1
Annual Therms | 77.5795 | 226.4864 | 1662.0681 | 4156.7696 | 4097.7746 | 2710.1016 | 600.245 | 257.0653 | 294.8446 | 113.9515 | 89.004 | 30.8539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative Annual Percent Consumption | 0.0054188 | 0.021238 | 0.13733 | 0.42767 | 0.7139 | 0.90319 | 0.94512 | 0.96307 | 0.98367 | 0.99163 | 0.99784 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Notes: If we are concerned about whole-life carbon, there will need to be more operational carbon savings in the lifetime of the equipment to electrify more than 30% of the design load if there is still life left in the existing boilers.
The incremental embodied carbon investment for the additional electrification doesn’t make sense.
We must understand existing building heating load annual profiles to decide how to optimally decarbonize existing hot water systems.

## Slide 40: 1-row VAV Percent Reheat Capacity vs. EWT
130°F could possibly meet the HHW loads in the previous example without changing piping or reheat coils
Notes: During a reto-commissing process, we can also perform a heating supply water winter time stress test to see how low we can go on supply water temperatures and still meet zone level setpoints.

## Slide 41
Existing equipment assessment
Electrical service capacity
Combustion equipment inventory
On-site renewable energy assessment
UNDERSTAND
On-site Inspections
02
GHG Emissions Reduction
Notes: The next phase of our work after getting the building working is to look at options for retorfits.

## Slide 42: 1-row vs. 2-row Reheat Coil Percent Capacity
Assumptions:
55°F EAT, water flow constant
Percent of 180°F EWT
1-row coil capacity
Notes: If you've measured loads and gotten good data, you can check whether you can get your needed capacity from existing single row reheat terminals. Doing a winter time stress test can help identify specific zones that may need coil upgrades without going through an upgrade across the whole building.

## Slide 43
Analysis and Reporting
03
GHG Emissions Reduction
Emission reduction measures (ERMs)
  Energy efficiency
  Electrification options
  On-site renewable energy
  Fugitive emissions
  Monitoring-based Cx
Future pathway to zero
ANALYZE
Notes: Now we move into Step 3: Analysis and Reporting, which is really the core of turning data into action.
At this stage, we take the emissions data we’ve gathered and begin identifying and evaluating specific emission reduction measures, or ERMs.
First, we look at energy efficiency opportunities—these are typically the most cost-effective and immediate actions, such as optimizing HVAC systems, improving controls, and reducing overall energy demand.
Next is electrification—shifting fossil fuel-based systems, like gas heating or hot water, to electric alternatives. This becomes especially impactful as the grid continues to decarbonize.
We also assess on-site renewable energy, such as solar PV, which can directly offset building energy use and reduce emissions.
Another important category is fugitive emissions—for example, refrigerant leaks—which are often overlooked but can have a high global warming impact.
We then incorporate monitoring-based commissioning, or continuous optimization, to ensure systems are operating as intended over time and savings persist.
Finally, we use all of this analysis to define a future pathway to zero—a long-term, strategic roadmap that sequences these measures in a practical and cost-effective way to achieve deep decarbonization.
So this step is really about moving from understanding emissions to building a clear, actionable plan forward

## Slide 44
Energy Efficiency 1st!
Notes: Before we swap out equipment.... and after we've made sure our building is truly opeating as intended through a thoughful Cx process, we can now focus in upgrading efficiency measures!

## Slide 45: Heat Recovery to Reduce Heating Loads
Source: 2020 ASHRAE Learning Institute Air-To-Air Energy Recovery Applications: Best Practices
55-75%
efficiencies
Ventilation loads are
a substantial portion
of heating loads
Notes: Air-to-air energy recovery is a very cost-effective and efficient way to recycle waste energy and create superior indoor environments.

## Slide 46: Heat Recovery MA/EA Heat Pumps
Image Source: Transom
Notes: Some HRV's also include supplemental heat pumps to further boost the heat recovery by recovering additional energy from the exhaust air stream. For some applications, this may reduce the need for additional terminal heating and cooling units.

## Slide 47
Selecting Retrofit Heat Pump Systems
Notes: You can see some additional considerations through the process of working through these options.

## Slide 48: Heat Pump Alternatives
Image Source: Copeland
Notes: Heat pumps can use multiple sources for their energy. Air source heat pumps are not the only option. Ground source/water source heat pumps can be great options in cold climates. There are even heat pumps that use waste heat recovery from the sewer system.

## Slide 49: Heat Pump System Sizing, Chicago
Load
Capacity
BIN hours
Capacity (MBH)
Ambient Temp (°F)
Hours
Compressor Speed Adjusted
Note that overcapacity in the blue area can be as much as 2.5 times the design load
Short cycling compressor runs
Nuisance trip on high-pressure alarms
Image Source: Transom
Notes: The typical winter design point is -5°F ambient
To match the load (3,000 MBH)
Multiple units would be needed
The capacity curve slopes down as ambient temp goes down.
The unit can still operate and produce heat below, but it will add up to the full load.
For this gap back up electric resistance heat is used. See YELLOW area

## Slide 50: Long Beach Ambient Temperature TMY3
Heating system turndown ratios have always been important for stable control.
Heat pumps don’t change that requirement!
Notes: Continuing your focus on performance and turndown is important... and heatpumps don't fix that.

## Slide 51: Understand the Operating Limits for ASHPs
Image Source: Transom
Notes: The key takeaway is that not all heat pump applications are feasible across all conditions. As the temperature lift increases—meaning colder outdoor air and higher required supply temperatures—the system approaches these limits quickly.
So when we’re designing or evaluating heat pump retrofits, especially in existing buildings with high-temperature heating systems, it’s essential to check that the required operating conditions stay within this envelope.
Otherwise, you either need system modifications—like reducing supply temperatures—or alternative strategies.
In short, understanding this envelope is fundamental to designing systems that are both efficient and reliable

## Slide 52: Heat/Energy Recovery (Waterside)
Source: Image Courtesy SmithGroup

## Slide 53: Right-Sourcing (GSHP)
Source: Image Courtesy SmithGroup

## Slide 54
Selection and Implementation
04
GHG Emissions Reduction
Evaluate optimal near-term solution strategies
Costs do matter!
This is a journey by 2050
OPTIMIZE
Notes: Now is the really fun part that you get to push into more advanced solutions to really drive performance.

## Slide 55: Advanced Heat Pump Strategies (Pairing with Storage)
Source: Image Courtesy of SmithGroup
Notes: One of the best ways to enable ultra high performance with heat pumps is to pair with storage. Storage allows for smaller heat pumps, and even better, can enable load shifting and enhaced grid alignment for reducing emissions.

## Slide 56: Thermal energy storage potential
Notes: This can be seen in this slide, where we let the thermal storage pick up the peak loads occuring during morning warm up.... and the heat pump can run flat out. Then you can use the lower carbon hours on the grid to recharge the thermal storage.

## Slide 57: Decarb Retrofit Lessons Learned
All GHG emissions matter (operational, embodied, and B1 refrigerants)
Decarbonization retrofits must reduce whole life GHG emissions

## Slide 58
Determine actual peak heating loads and load profiles when decarbonizing existing heating systems
NEVER replace the same size equipment without first determining the actual needs of the existing building
Decarb Retrofit Lessons Learned

## Slide 59: Decarb Retrofit Lessons Learned
There is a paradigm shift in the cost-effectiveness of heat recovery technologies with all-electric buildings
Building envelope and heat recovery options that were not cost-justified with boilers are now often economical with electrification retrofits.

## Slide 60
Use minimum 2-row reheat coils when designing terminal reheat systems today
The future is low-temperature hot water to improve energy efficiency and exergy
Decarb Retrofit Lessons Learned

## Slide 61
Thermal storage is our ally (technical and economical) when providing heating solutions with hydronic heat pumps
Turndown ratios still matter in heating system design
Decarb Retrofit Lessons Learned

## Slide 62: Decarb Retrofit Lessons Learned
Don’t be afraid of partial decarbonization strategies for meeting life cycle cost requirements
An 80% GHG emission reduction is better than NO reduction!

## Slide 63
Four Key Areas
Focused on strategy, thought leadership, industry collaboration, and public advocacy related to building decarbonization
Works with the ASHRAE councils to deliver projects
  Technology
  Education
  Research
  Standards
Center of Excellence for Building Decarbonization (CEBD)

## Slide 64: ASHRAE Published Decarbonization Guides

## Slide 65
Notes: I will leave you with one thought: We can do better and develop solutions that minimize our impact on the environment.

## Slide 66
Thank You