## Slide 1: Zero Heroes
v
2022 Building Performance
Analysis Conference
2022 ASHRAE LowDown Showdown Modeling Competition
2022 ASHRAE Low Down Showdown

## Slide 2: Our Team
Nathan Kegel
Jill Maltby-Abbott
Thu Nguyen
Shona O'Dea
Xuyang Jin
Anthony Montez
Rajat Wadhwa
Andrew Eckhoff
Chris Flynn*
Mahdi Afkhamiaghda
Matt Conway
Zero Heroes
* From Albuquerque
Mural Board
CA
MN
C0
TX
MO
IL
NY
Danielle Steele

## Slide 3: Guiding Principles + Beyond Competition Parameters
Simplicity / Passive / Low maintenance
Future Climate Ready
Not a “one-off” building; strategies can be understood and applied across the District and State of New Mexico
Community Shelter from natural disasters (wildfires, heat waves)
EPDs strongly preferred
Albuquerque Public Schools Standards
City of Albuquerque Climate Action Plan
New Mexico Energy Transition Act of 2019
  Mandates 100% renewable grid by 2045
  50% renewable by 2035
Zero Heroes

## Slide 4: Climate Analysis - Passive Design Thermal Comfort
Climate Character:
  High diurnal swing (30+ F on most days)
  Sunny year-round
  Wind (generally more consistent during day)
  Dry (~8” annual precip. historically)
  High Elevation (negative latent load)
We have: sun, wind, ground with generally high thermal conductivity (limestone base)
We don’t have: water (and even less in the future)
Passive Design Strategies:
  Thermal mass + Night Flush
  Brise Soleil
  Optimized Program (reduce total SF built)
Future Climate: Hotter and Drier – accounted for this in design and modeling assumptions
Zero Heroes

## Slide 5: Future Climate Change and Risk
Zero Heroes
2021 Wildfire Impact on Air Quality
https://climatecheck.com/newmexico

## Slide 6: Site Selection
Zero Heroes
Jimmy Carter Middle School
LOS VOLCANES RD NW
DAYTONA RD NW
ARROYO RD

## Slide 7: Exterior Wind Comfort
Zero Heroes
Landscaping strategically planned to expand comfortable outdoor learning spaces
Chose native plants that are low to no maintenance
Convective losses reduced, decreasing overall cooling and heating costs
Overlay the landscape ?

## Slide 8
72,700 sf Building
Connects to adjacent existing middle school forming K-8 learning campus
3% Reduction from 75,000 sf
Creativity & Innovation Arroyo
2022 ASHRAE LowDown Showdown Modeling Competition

## Slide 9: Daylight & Visual Comfort
Zero Heroes
Clerestories to provide interior daylight and passive solar heating in winter
Minimize WWR (balance natural light, comfort, peak load, and energy)
Designing for comfort utilizing a combination of active and passive systems (WELL)
ASE (1000, 250) = 9.2 %
sDA (300,50%)= 75%
Period = 8:00 – 16:00

## Slide 10: Creativity & Innovation + Passive Design with Thermal Mass
Zero Heroes
Notes: note night flush

## Slide 11: Carbon Mitigation Measures Embodied Carbon x Wall Assemblies
Zero Heroes
Wood-clad CLT
most intensive GWP
realistic to site with optimized GWP
least intensive GWP
PEMB
Steel-supported unreinforced concrete masonry unit (CMU)
(non-loadbearing)
Stucco over wood studs
30' long x 12' tall wall section studies:
Assembly
*does not include structure beyond wall assembly
Tally projections
*biogenic carbon turned on
kgCO2e
EPA equivalency* *US passenger vehicles driven for 1 year
-1,006
35,092
6,050
3,075
3,302
Reinforced compressed earth block (CEB)
(loadbearing)
?
Notes: Clarify regional nature of material CEB / Watershed block.
Here, you'll see the start of an embodied carbon story across our industry specific to schools. The team started with that per discipline breakdown and focused on where we could push / pull on different disciplines and challenge ourselves to optimize.
We took a peek at DLR Group's portfolio for highest to lowest projections. Not surprisingly, CMU was a wonderful fit operationally – but this team found Compressed Earth Block to respect the vernacular, optimize both the architectural wall assembly tied double dipping for structural.

## Slide 12: Carbon Mitigation Measures Embodied Carbon
Zero Heroes
most intensive GWP
reinforced compressed earth block (CEB) as enclosure and interior finish
(loadbearing)
WBLCA:
CLT ceiling deck / structure under insulated standing seam metal roof
Bonded EWF play surface (engineered wood fibers) in lieu of artificial turf for BPA/PFAS/and recycled rubber avoidance (lead)
Notes: - avoidance of finishes at the exterior wall – direct to functional walls as demising partitions
-

## Slide 13: Comfort & Air Quality
Zero Heroes
Good (<=50)
Moderate (51-100)
Moderate for Sensitive Groups (101-150)
Unhealthy (151-200)
Very Unhealthy (201-300)
Hazardous (>=301)
Daily AQI Values, Albuquerque, NM,2000 to 2021
Adaptive model used for most spaces where operable windows and ceiling fans are available
AQI may limit passive availability, especially in a future that has more wildfires which negatively impact AQ. Therefore, need to have hybrid approach to comfort and air quality.
Source: U.S EPA AirData
PMV model
Adaptive model

## Slide 14: Indoor Air Quality & Thermal Comfort
ASHRAE 62.1 IAQP method used for minimum ventilation calculations
Reduced min. OA by 46% relative to VRP method
Reduced HVAC heating and cooling equipment size by ~20%
Sorbent air cleaning technology used
  First Cost Neutral
Continuous IAQ monitoring with demand control ventilation
Night Flush provides fresh air in the space at the start of each morning (outdoor AQ permitting)
Thermal comfort modeled using CFD
Zero Heroes
2022 ASHRAE LowDown Showdown Modeling Competition
Air Change Effectiveness – Passive Night Flush (fans off)

## Slide 15: Comfort – PPD (Design Day Summer afternoon, HVAC on)
Zero Heroes
PPD at 6” AFF (ankles)
PPD at 4’-6” AFF (chest/shoulder/head)

## Slide 16: Comfort and Energy Savings
Zero Heroes
Thermal Mass Effect in Winters on the Room Temperature [ Jan 6]
  Peak temp reduced and delayed
Night Flush effect in Summer on the Room Temperature [ Jul 9]
  “pre-cooling” of mass (“thermal battery”)
No Energy needed to cool the building in summer nighttime – assuming night flush available (Air Quality dependent)
Design Optimizes passive comfort opportunity from climate data and uses thermal mass instead of high levels of insulation (reduced embodied carbon)
Night Flush saves 80.5 Mbtu/h per year in cooling energy
(and reduces night time electrical consumption, reducing “dirtiest” grid hours)

## Slide 17: Water Conservation Strategies
Utilized Roof Rainwater Harvesting (70,000 sf)
75% Annual Rainfall (accounting for reduced annual precip in future) rate at 90% Collection Efficiency resulted in ~275,000 gallons/year of water captured for indoor flush fixtures (non-potable use)
Implementation of Low-Flow Water Closets (1.1 gpf) and Waterless Urinals (1 gallon/72 hours) resulted in annual consumption of 213,000 gallons/year
Rainwater Harvesting ideally offsets water consumption for plumbing flush fixtures.
Leads to 173,000 gallons/year consumed. A 74% reduction in consumption compared to Energy Star’s 10 gal/sf Indoor Water Use Intensity estimate for K-12 Schools
Zero Heroes
2022 ASHRAE LowDown Showdown Modeling Competition
Chart: INTERIOR WATER MONTHLY VOLUMES
| 44774 | 44805 | 44835 | 44866 | 44896 | 44927 | 44958 | 44986 | 45017 | 45047 | 45078 | 45108
Captured | 35635.2029 | 59002.5491 | 17525.5096 | 13144.1322 | 16649.2342 | 17525.5096 | 12559.9486 | 4673.4692 | 12559.9486 | 17525.5096 | 8178.5712 | 59878.8246
Usage | 21000 | 21000 | 21000 | 21000 | 21000 | 21000 | 21000 | 21000 | 21000 | 21000 | 1600 | 1600
Supplement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shortage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chart: INTERIOR WATER STORAGE
| 44774 | 44805 | 44835 | 44866 | 44896 | 44927 | 44958 | 44986 | 45017 | 45047 | 45078 | 45108
Tank Level | 35635.2029 | 73637.7521 | 70163.2617 | 62307.394 | 57956.6281 | 54482.1378 | 46042.0864 | 29715.5556 | 21275.5042 | 17801.0138 | 24379.585 | 77000
Net Inflow | 14635.2029 | 38002.5491 | -3474.4904 | -7855.8678 | -4350.7658 | -3474.4904 | -8440.0514 | -16326.5308 | -8440.0514 | -3474.4904 | 6578.5712 | 58278.8246
Storage Capacity | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000

## Slide 18: Water Conservation Strategies
Native drought resistant plants were selected for the earth berms that shelter the building from wind
Playfield (30,000 sf) – Half-and-Half Mix of Kentucky Bluegrass & Bermudagrass (more drought tolerant and adaptive for future climate)
517,000 gallons/year required for watering.
  21% reduction compared to 100% Kentucky Bluegrass (APS standard)
Utilized Parking Lot for Rainwater Harvesting (70,000 sf): 275,000 gallons/year
243,000 gallons/year supplemented
  63% reduction in watering costs
Below-grade drip irrigation system to reduce water evaporation by 90%.
Zero Heroes
2022 ASHRAE LowDown Showdown Modeling Competition
Chart: SITE WATER STORAGE
| 44774 | 44805 | 44835 | 44866 | 44896 | 44927 | 44958 | 44986 | 45017 | 45047 | 45078 | 45108
Tank Level | 545.7029 | 31778.7521 | 29669.2617 | 30424.644 | 47073.8781 | 64599.3878 | 77000 | 46517.4692 | 308.1678 | 448.6775 | 354.2486 | 784.3233
Net Inflow | -59454.2971 | 31233.0491 | -2109.4904 | 755.3822 | 16649.2342 | 17525.5096 | 12559.9486 | -30482.5308 | -46209.3014 | 140.5096 | -94.4288 | 430.0746
Storage Capacity | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000 | 77000
Chart: SITE WATER MONTHLY VOLUMES
| 44774 | 44805 | 44835 | 44866 | 44896 | 44927 | 44958 | 44986 | 45017 | 45047 | 45078 | 45108
Captured | 35635.2029 | 59002.5491 | 17525.5096 | 13144.1322 | 16649.2342 | 17525.5096 | 12559.9486 | 4673.4692 | 12559.9486 | 17525.5096 | 8178.5712 | 59878.8246
Usage | 95089.5 | 27769.5 | 19635 | 12388.75 | 0 | 0 | 0 | 35156 | 68769.25 | 66385 | 108273 | 83448.75
Supplement | 0 | 0 | 0 | 0 | 10000 | 49000 | 100000 | 24000
Shortage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Slide 19: Carbon Mitigation Measures Total Carbon
Zero Heroes
2022 ASHRAE LowDown Showdown Modeling Competition
TC = ((EUI*A) - (RE)) *CF + ((EC+BC*VBC)/BL)
Total Carbon
Energy Use Intensity
Area
Renewable Energy
Conversion Factor
Embodied Carbon
Biogenic
Carbon
Volume
Expected
Building Life
kgCO2/yr
kwh/ft^2 yr
ft^2
kwh/yr
From electricity to GHG emissions
-
kgCO2
KgCO2/ft^2
ft^2
75 yrs
TC BASELINE = 574,986.6 + 3,606,202
TC PROPOSED = -168,940.8 +2,323,963
88 tree seedlings proposed
(allowed to grow for 10 years min.)
=
-5,420 kgCO2e

## Slide 20: Cleaning the NM Power Grid
Zero Heroes
Source: American Solar Energy Society
Site solar and battery (building as a microgrid) contributes to cleaning the New Mexico power grid

## Slide 21: Resiliency & Operational Carbon Reduction
Solar Hot water for OA preheat (with GSHP backup)
Solar Hot water for DHW (with HPHWH backup)
1 MWh Battery
Helps Reduce the Burden on Grid + backup power
Site as a microgrid
67% of the year capable of operating off-grid
Charged during the Day time (Greener Grid + onsite PV system)
Close to 200 hrs of reliance on grid annually
1356 Hours of Green energy sent to the grid annually
$50,000 worth of extra energy sent to grid ($0.03/kWH)
Zero Heroes

## Slide 22: Carbon Mitigation Measures Total Carbon
Zero Heroes
Carbon Neutral

## Slide 23: Required Metrics
Zero Heroes
 | IP | SI
Total Annual Energy Use | 1,536,599 kBtu | 450,332kWh
Total Annual Water Use | 172,292 Gals | 652,197 Liters
Total Annual Onsite Energy Production | 2,234,402 kBtu | 654,839kWh
Annual Energy & Water Cost | 1.1 $/ft2 | 12 $/m2
Site EUI | 20.4 kBtu/ft2 | 66.68kWh/m2
Source EUI | 66 kBtu/ft2 yr | 208 kWh/m2
Annual CO2e Emissions | -1.7637 IbCO2e/SF | -9 kg CO2e / ft2

## Slide 24: Strategies Explored and Abandoned
Earth tube for preconditioning OA
  Similar in effect to an enthalpy wheel; but more costly
  Maintenance concerns
  Radon concerns
Elimination of mechanical cooling
  Hotter future climate would require mechanical cooling from April-October
  Significantly limits adaptability and durability of the building
Phase Change Materials (PCM)
  Eliminated because no EPD’s available plus cost. Less adaptable than HVAC system.
Transpired Solar Collector for preconditioning of OA
  Less effective than enthalpy wheel, interrupted architectural intent
Evaporative Cooling
  While very effective, the lack of water in Albuquerque (especially in the future) eliminated this from consideration
Zero Heroes

## Slide 25: Conclusions
Zero Heroes
2022 ASHRAE LowDown Showdown Modeling Competition
Start with the end in mind: target date for zero carbon
Understand the grid and the plan for the grid
Understand climate to reduce peaks
Assess future climate risk
  EUI/peak load
  AQI/IAQ
  Extreme weather events
  Water
Prioritize Passive strategies for present and future climates
Understand time of use in the era when the grid is forecast to be dirtiest
Make multiple forecasts and be wrong a lot

## Slide 26
ZERO HEROS

## Slide 27: APPENDIX
Zero Heroes

## Slide 28: Renewable Energy – Wind and Solar
Zero Heroes

## Slide 29: Resources
Zero Heroes
https://watershedmaterials.com/
AIA-CLF Embodied Carbon Toolkit