## Slide 1: 2017 ASHRAE LowDown Showdown Modeling Competition
Retrofit of Existing Storage Warehouse Facility
2017 Building Performance
Analysis Conference
SANDSTORM STOPPERS
Presentation By
Junaid Bin Naseer
Senior Mechanical Engineer [AECOM]

## Slide 2: Team & Software Used
2017 ASHRAE LowDown Showdown Modeling Competition
Name | Role
Junaid Bin Naseer | Captain/Modeler
Christopher King | Coach
Ali Haidar | Mechanical Designer
Hasan Karaway | Architect
Software Name | Purpose
IES VE 2017 | Energy Modeling and Cooling Load
Relux | Lighting Calculations

## Slide 3: Team Collaboration 01
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 4: Team Collaboration 02
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 5: Approach to Achieve Net Zero
2017 ASHRAE LowDown Showdown Modeling Competition
Understanding Climate Zone
Evaluating Potential Savings from Renewables
Modeling and Analyzing Existing Building Energy Consumption
Potential Energy Conservation Measures including Passive and Active
Conclusion

## Slide 6: Understanding Climate Zone
Zone 4A – Warm and Humid
Weather File – Andrews Air Base
Max Temp 37.8°C DB [100.04 °F]
Min Temp -18.9°C DB [-2.02 °F]
Mean Temp 13.0 °C DB [55.4 °F]
Max Humidity Ratio 26.0 g/kg [182 grains/lbs]
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 7: Temperature Distribution
2017 ASHRAE LowDown Showdown Modeling Competition
Temperature is in range of -5 to 15 °C for approximately 4,619 hours ; Heating Requirement
Temperature is in range of 20-35 °C for approximately 2,772 hours; Cooling Requirement
Heating will dominate the energy consumption

## Slide 8: Hot, Cold, & Temperate Months
2017 ASHRAE LowDown Showdown Modeling Competition
November till April – Heating Season
June till August – Cooling Season
May, Sept, & October – Comfortable Season
6 Months of Heating
3 Months of Cooling
3 Months of Temperate Climate

## Slide 9: Renewable Energy
Selected Renewable Type = Photovoltaic Panels
Type of PV Panel = Mono Crystalline
Power Output Range = 320 – 335 W
Dimensions = 1,978 mm Height X 992 mm Width
# of Panels = 491
Inclination = 32°
Azimuth = 32.27 °
Annual Electricity Generated = 231,194 kWh/year [788,834 kBTU/year]
Cost (Retail + Labour) per Watt = $ 3.87
Total Watt = 164,315
Total Cost = $ 635,893
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 10: Renewable Energy Generation Per Month
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: KWh
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Electricty Generated (kWh) | 15404.5 | 11686.5 | 20355.2 | 24131.2 | 26211.7 | 22857.3 | 20130.9 | 21407.3 | 19046 | 23355.4 | 14629.9 | 11978.6

## Slide 11: Modeling Existing Building
Architecture - PDF to CAD with Dimensions
Height of Building
Assumptions
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 12: Modeled Floor Plan
2017 ASHRAE LowDown Showdown Modeling Competition
Dimensions in MM

## Slide 13: Building Architecture Zoning
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 14: Height of Building
2017 ASHRAE LowDown Showdown Modeling Competition
ADMIN BUILDING
Height = 5.40 m
STORAGE AREA HEIGHT = 13.4 m

## Slide 15: Assumptions
Modeled Area of 64,635 ft² does not match with 43,492 ft²
ADMIN Zone Floor to False Ceiling Height of 4.50 meter [14.76 feet]
ADMIN Zone Ceiling Height of 1.00 meter [3.28 feet]
Glazing is considered only for ADMIN Zone
Glazing Sill Height 1.50 meter [4.92 feet]
Glazing Height 2.20 meter [7.20 feet]
Building is oriented 309 due north
Peak Staff Occupancy 41 People
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 16: Existing Building Model 3D Model
2017 ASHRAE LowDown Showdown Modeling Competition
Front Perspective View
Back Perspective View

## Slide 17: Modeled ADMIN Zone Areas
2017 ASHRAE LowDown Showdown Modeling Competition
Sr # | Space Tag | Area (m²) | Area (ft²)
1 | C00: Corridor 01 | 192 | 2,063
2 | M00: Mech 00 | 92 | 987
3 | X01: Sorting Area 01 | 726 | 7,811
4 | X02: Meeting Room 01 | 89 | 957
5 | X03: Lunch Room | 54 | 578
6 | X04: External Office 01 | 139 | 1,492
7 | X05: External Office 02 | 92 | 995
8 | X06: Sorting Area 02 | 371 | 3,995
9 | X07: Internal Office 01 | 95 | 1,019
10 | X08: Meeting Room 02 | 72 | 771
11 | X09: Internal Office 02 | 80 | 866
12 | X10: External Office 03 | 46 | 492
 |  | 2,046 | 22,024

## Slide 18: Modeled STORAGE Zone Areas
2017 ASHRAE LowDown Showdown Modeling Competition
Sr # | Space Tag | Area (m²) | Area (ft²)
1 | M01: Mech 02 & 03 | 192 | 2,063
2 | S00: SCF 01 | 1,202 | 12,943
3 | S01: SCF 02 | 1,221 | 13,143
4 | S02: SCF 03 | 1,346 | 14,487
 |  | 3,961 | 42,637

## Slide 19: Sorting Spaces
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 20: Mechanical Spaces
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 21: Shared Collection Facilities
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 22: Office Spaces
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 23: Corridor
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 24: All Spaces
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 25: Wall & Roof U-Values
2017 ASHRAE LowDown Showdown Modeling Competition
S # | Building Component | Element Type (Outside to Inside) | Thickness (in) | R-Value (°F-ft².h/BTU) | R-Value (m².°K/W)
1 | Roof | Bitumen Roofing Membrane |  |  | 0.00
2 | Roof | Apa Rated Oriented Strand Board | 0.5 | 0.5 | 0.09
3 | Roof | Rigid Polyiso Insulation | 3.2 | 39.6 | 6.97
 |  |  | 3.7 | U-Value | 0.14 W/m².K [0.025 BTU/h. ft².°F]
S # | Building Component | Element Type (Outside to Inside) | Thickness (in) | R-Value (°F-ft².h/BTU) | R-Value (m².°K/W)
1 | Wall Type 1 | Outside Resistance |  |  | 0.04
2 | Wall Type 1 | Nom Insulated CMU | 8 | 5.5 | 0.97
3 | Wall Type 1 | Air, Water, & Vapor Barrier Membrane |  |  | 0.00
4 | Wall Type 1 | Thermal Insulation Board | 3 | 19.5 | 3.43
5 | Wall Type 1 | Cavity | 1 3/8 | 1.9 | 0.33
6 | Wall Type 1 | Nom Split Face CMU | 4 | 1.6 | 0.28
7 | Wall Type 1 | Inside Resistance |  |  | 0.12
 |  |  |  | U-Value | 0.19 [0.033 BTU/h. ft².°F]

## Slide 26: External Glazing, Ground U-Value, & Infiltration
External Glazing – 3.20 W/m².K [0.56 BTU/h. ft².°F] and SHGC 0.40
External Glazing Ratio – 32 % (240 m²/739m² of Admin Area Only)
Sill Height – 1.50 meter
Glazing Height – 2.20 meter
2017 ASHRAE LowDown Showdown Modeling Competition
Ground Edge Insulation Width X Thickness 80mm X 610 mm
Ground Edge Insulation U-Value 0.025 W/m.K [0.014 BTU.ft/h. ft².°F]
Infiltration 1.50 L/s.m².Facade

## Slide 27: Thermal, Lighting & Equipment Input
2017 ASHRAE LowDown Showdown Modeling Competition
Zone Description | Room Temperature Summer (°F) | Room Temperature Winter (°F) | Room Humidity (%) | Lighting (W/ft²) | Equipment (W/ft²) | Occupancy (ft²/person) /[Nos]
Shared Collection Facility | 60 | 60 | 40 | 1.7 |  | 1 each
Mechanical Room | 80 | 55 |  | 1.5 |  | 1 each
Offices | 75 | 70 |  | 1.1 | 0.9 | 28.1 [57]
Circulation | 75 | 70 |  | 0.5 |  | 0
Meeting Rooms | 75 | 70 |  | 1.1 | 0.9 | 13.33 [12]

## Slide 28: Annual Ground Temperature 2011-2016
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Month
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Average Air Temperature (°F) 2011-2016 | 15.0645 | 17.5106 | 26.8903 | 37.22 | 47.7065 | 55.28 | 60.2968 | 56.9968 | 51.65 | 39.7903 | 29 | 24.9989

## Slide 29: Challenges Faced in ADMIN HVAC System
2017 ASHRAE LowDown Showdown Modeling Competition
Data Provided OFFICE VAV REHEAT Installed in 1970
Our Assumptions
Standard Rooftop Package Unit with Variable Speed Fan and VAV Reheat
Outdoor Air Requirement 1,400 L/s [3,000 cfm]
Supply Air Fan 4,419 L/s [3,000 cfm]
VAV Fan maximum turndown of 30%
Fan Power was adjusted to match existing system consumption
Reheat Coil for Spaces Exposed to External Conditions

## Slide 30: HVAC Existing Building Data/ADMIN ZONE
2017 ASHRAE LowDown Showdown Modeling Competition
COMMON RETURN
Reheat Coil for Spaces Exposed to External
DX Cooling Efficiency
6.2 EER
@AHRI
Supply Fan
Flowrate 4,419 L/s
SFP 3.40 W/L/s
THERMAL SPACE

## Slide 31: Challenges Faced in SCF-01 HVAC System
2017 ASHRAE LowDown Showdown Modeling Competition
Data Provided Module 1: Liebert CRAC-type DX System Installed 2011
Unable to find data on this type of system
Our Assumptions
Standard Rooftop Package Unit with Constant Speed Fan
Main Electric Heating Coil Inside the Unit
Fan Power was adjusted to match existing system consumption
Airflow rate similar to AHU-03 i.e. 8,178 L/s [17,400 cfm]

## Slide 32: HVAC Existing Building Data/SCF-01
2017 ASHRAE LowDown Showdown Modeling Competition
Electric Heating Coil
60 kW
DX Cooling Efficiency
7.2 EER
@AHRI
Supply Fan
Flowrate 8,178L/s
SFP 4.50 W/L/s
THERMAL SPACE

## Slide 33: Challenges Faced in SCF-02 HVAC System
2017 ASHRAE LowDown Showdown Modeling Competition
Data Provided AHU-01 is similar to AHU-03
Discrepancies between control schematics and BMS Screenshot
Airflow rate is not similar to AHU-03
Our Assumptions
AHU-01 serving SCF-02 is with Active Desiccant Wheel and Reactivation Air Fan
One Main Electric Heating Coil Inside the Unit
Airflow is 6,323 L/s [13,400 cfm]

## Slide 34: HVAC Existing Building Data/SCF-02
2017 ASHRAE LowDown Showdown Modeling Competition
Reactivation Air Fan
Flowrate 300 L/s
SFP 3.00 W/L/s
OA Coil
16 kW
Reactivation Heater
40 kW
Dehumidification Wheel
SAF
Flowrate 6,323 L/s
SFP 4.50 W/L/s
AHU Coil
71.74 kW
Electric Heating Coil
50 kW

## Slide 35: Challenges Faced in SCF-03 HVAC System
2017 ASHRAE LowDown Showdown Modeling Competition
Data Provided Control Schematics, BMS Screenshot, & Schedule
Discrepancies between control schematics and BMS Screenshot
Our Assumptions
The unit is Performance Climate Changer with CDQ wheel and without Reactivation air fan and heater from Trane
Specific Fan Power per schedule should be 1.40 W/L/s but was adjusted to match metered energy consumption and was increased to 3.00 W/L/s
Airflow is 8,178 L/s [17,400 cfm]

## Slide 36: HVAC Existing Building Data/SCF-03
2017 ASHRAE LowDown Showdown Modeling Competition
Supply Air Fan
Flowrate 8,178 L/s
SFP 3.00 W/L/s
AHU Coil
71.74 kW
Dehumidification Wheel
Electric Heating Coil
60 kW

## Slide 37: Challenges Faced in Hydronic HVAC System
2017 ASHRAE LowDown Showdown Modeling Competition
Data Provided Air Cooled Scroll Chiller from Trane
No Data on Chilled Water Pump Power
Our Assumptions
Efficiencies of Unit were modeled using CGAM Air Cooled Trane Chiller Product Catalogue
Assumed Chilled Water Pump Power 6.30 kW

## Slide 38: Hydronic System
2017 ASHRAE LowDown Showdown Modeling Competition
Air Cooled Chiller
Trane CGAM
COP 2.96 @ AHRI [EER 10]
Variable Chilled Water Pump
Chilled Water Coils of AHU-01 & AHU-03
Delta T 8.89 K
CHWST 4.44 °C [40 °F]
CHWP SPP
1000 W/L/s [63 W/gpm]

## Slide 39: ADMIN ZONE Metered Vs Simulated Energy Consumption (kWh)
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| January | February | March | April | May | June | July | August | September | October | November | December
ADMIN Zone_Metered (kWh) | 51710 | 56188 | 55056 | 56963 | 20405 | 44198 | 43629 | 48065 | 48709 | 44763 | 37493 | 42203
ADMIN Zone_Simulated (kWh) | 62478.5 | 51371.7 | 50693.2 | 36198.8 | 33692.4 | 38234.5 | 43330.4 | 37470.1 | 33800.2 | 34174.2 | 47873.3 | 52089.3
Metered 549,382 kWh
Simulated 521,407 kWh
Error 5.00%

## Slide 40: SCF ZONE Metered Vs Simulated Energy Consumption (kWh)
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| January | February | March | April | May | June | July | August | September | October | November | December
SCF Zone_Metered (kWh) | 256613 | 219636 | 227557 | 228375 | 170576 | 173247 | 190169 | 211641 | 254842 | 267776 | 229855 | 237837
SCF Zone_Simulated (kWh) | 228318.2 | 191681.4 | 204884.2 | 190369.7 | 196694 | 184009.3 | 187787 | 192761.1 | 192493.8 | 195263.3 | 210281.6 | 209382.2
Metered 2,668,124 kWh
Simulated 2,383,926 kWh
Error 11.00%

## Slide 41: Metered Vs Simulated Energy Consumption
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| Energy Consumption All Year
VAV Unit (Office)_Metered | 549382
VAV Unit (Office)_Simulated | 521406.6
AHU 1 & 2 & RTU_Metered | 2668124
AHU 1 & 2 & RTU_Simulated | 2383925.8

## Slide 42: Simulated Energy Consumption Breakdown
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| Heating | Cooling | Interior Lighting | Interior Equipment | Fans | Pumps | Heat Rejection | Heat Recovery | Water System
Existing Building (kWh) | 1392287.4 | 367294 | 164168.6 | 45250.2 | 838104 | 5916.9 | 16035.1 | 32051.7 | 3068
Metered 3,217,506 kWh
Simulated 2,864,176 kWh
Error 11.00%

## Slide 43: Energy Conservation Measures
2017 ASHRAE LowDown Showdown Modeling Competition
Reduction in Window U-Value from 3.2 W/m².K to 0.73 W/m².K
Reduction in Infiltration 1.5 L/s.m².fac to 0.5 L/s.m².fac
Reduced Setpoint of Heating from 16°C (60 °F) to 15°C (59 °F) for Storage Zone Only
Reduction of Current Lighting to LED
Package Outdoor Heat Pump with Energy Recovery Wheel for ADMIN Zone
Replacement of RTU-1 with Package Unit which includes CDQ Wheel
Replacement of Centrifugal Fans with Direct Drive Plenum Fans

## Slide 44: 1. Window U-Value from 3.20 to 0.73 W/m².K
Area of Glazing 240 m² [2,582 ft²]
Cost per ft² $ 52
Installation & Profit $ 52 X 1.34 = $ 70
Total Cost $ 180, 768
Change in EUI - 32 kWh/year
Annual Energy Saved 192,842 kWh [657,977 kBTU]
US Dollars Saved $ 15,427/year [8 cents per kWh]
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 45: ECM_01 Window Monthly Energy Consumption
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| January | February | March | April | May | June | July | August | September | October | November | December
Overall Simulated | 280568.7 | 233441.4 | 247558.3 | 222900.8 | 229969.8 | 222243.7 | 231117.5 | 230231.1 | 226293.9 | 227450.1 | 254154.7 | 255125.3
ADMIN Window U-value | 242288.5 | 204490.9 | 220008 | 211078.2 | 224737.4 | 217156.3 | 223247.8 | 226665.4 | 222715.1 | 219712.8 | 229333.3 | 226779.3
Simulated 2,861,055kWh
Window 2,668,213 kWh
EUI Change -32 kWh/year [7.0%]

## Slide 46: 2. Infiltration from 1.5 L/s.m².fac to 0.5 L/s.m².fac
2017 ASHRAE LowDown Showdown Modeling Competition
Existing Building
Retrofit Building
Assumptions based on Book “Humidity Control Design Guide For Commercial and Institutional Building” by Lewis G. Harriman, G.W. Brundrett, & R. Kittler
Cost $5,000 [Assumed]
Change in EUI -116 kWh/year
Annual Energy Saved -112,351 kWh [383,342 kBTU]
US Dollars Saved $9,000/year

## Slide 47: ECM_02 Infiltration Monthly Energy Consumption
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| January | February | March | April | May | June | July | August | September | October | November | December
Overall Simulated | 280568.7 | 233441.4 | 247558.3 | 222900.8 | 229969.8 | 222243.7 | 231117.5 | 230231.1 | 226293.9 | 227450.1 | 254154.7 | 255125.3
Infiltration Simulated | 251479.3 | 209174.6 | 223130.2 | 212212.4 | 231113.9 | 228545.5 | 237928.4 | 235565.6 | 230140.7 | 223869.4 | 234401.2 | 231143
Simulated 2,861,055 kWh
Infiltration 2,748,704 kWh

## Slide 48: 3. Heating Setpoint from 16 °C to 15 °C [01]
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 49: 3. Heating Setpoint from 16 °C to 15 °C [02]
Change in EUI -33 kWh/year
Annual Energy Saved 199,987 kWh [682,356 kBTU]
US Dollars Saved $16,000/year
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 50: ECM_03 Heating Setpoint Monthly Energy Consumption
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| January | February | March | April | May | June | July | August | September | October | November | December
Overall Simulated | 280568.7 | 233441.4 | 247558.3 | 222900.8 | 229969.8 | 222243.7 | 231117.5 | 230231.1 | 226293.9 | 227450.1 | 254154.7 | 255125.3
Setpoint | 250861.1 | 206516.1 | 215325.7 | 193086.6 | 213374.3 | 229570.3 | 247059 | 235813.2 | 219322.4 | 204351.2 | 221497.5 | 224290.6
Simulated 2,861,055kWh
Setpoint 2,661,068 kWh
EUI Change -33 kWh/year [7.0%]

## Slide 51: 4.Replacement of Current Lighting with LED_01
Lighting calculations based on IES NA.
Software used Relux
Existing Building Lighting Power 98.15 kW
Existing Building Lighting Power Density 16.76 W/m² [1.56 W/ft²]
Retrofit Installed Lighting Power 42.2 kW
Retrofit Installed Lighting Power Density 7.20 W/m² [0.67 W/ft²]
57% Reduction in Installed Lighting
LED Cost Per 60 W Bulb $ 36
LED Cost $ 25,320
Installation & Profit $ 25,320 X 1.38 = $ 35,000
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 52: 4.Replacement of Current Lighting with LED_02
Change in EUI -116 kWh/year
Annual Energy Saved 699,441 kWh [2,386,492 kBTU]
US Dollars Saved $56,000/year
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 53: 4.Replacement of Current Lighting with LED
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| January | February | March | April | May | June | July | August | September | October | November | December
Overall Simulated | 280568.7 | 233441.4 | 247558.3 | 222900.8 | 229969.8 | 222243.7 | 231117.5 | 230231.1 | 226293.9 | 227450.1 | 254154.7 | 255125.3
LED | 203746.5 | 177611.9 | 194762.3 | 179101.1 | 176901.3 | 162357.8 | 164411.1 | 167656.4 | 170020.9 | 179807.1 | 191186 | 194051.7
Simulated 2,861,055kWh
LED 2,161,614kWh
EUI Change -116 kWh/year [24.0%]

## Slide 54: 5. Package Outdoor Heat Pump with Energy Recovery Wheel for ADMIN Zone_01
Cooling Unit Size 51.4 kW [175 kBTU]/Heating Unit Size 51 kW [174 kBTU]
Cooling Efficiency of Unit 3.10 COP [EER 10.6] @ AHRI
COP Heat Pump 3.2 @ 8.33 °C [47 °F] & 2.0 @ -8.33 °C [17 °F]
Energy Recovery Wheel 75% Total Effectiveness
Change in EUI -42 kWh/year
Annual Energy Saved 253,953 kWh [866,488 kBTU]
US Dollars Saved $20,316/year
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 55: 5. Package Outdoor Heat Pump with Energy Recovery Wheel for ADMIN Zone_02
Cost Data Based on Updated Building Sector Appliance & Equipment Costs & Efficiencies
Retail Cost Per 90 kBTU $ 6,400
Installation Cost Per 90 kBTU $ 7,750
Retail Cost Per 175 kBTU $ 12,400 [Estimated]
Installation Cost Per 175 KBTu $ 15,100 [Estimated]
Energy Recovery Wheel Cost $ 1,200 [Estimated]
Gross Cost $ 17,300
Total Cost on Site $ 35,000 [Removing Old Unit, Transportation, & Misc]
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 56: ECM_05 Pkg OA HP ADMIN Monthly Energy Consumption
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| January | February | March | April | May | June | July | August | September | October | November | December
Overall Simulated | 280568.7 | 233441.4 | 247558.3 | 222900.8 | 229969.8 | 222243.7 | 231117.5 | 230231.1 | 226293.9 | 227450.1 | 254154.7 | 255125.3
ADMIN Pkg OA HP | 253186 | 213894.3 | 228815.4 | 208614.9 | 211091.5 | 197846 | 202651.6 | 206804.7 | 206530.6 | 211393.9 | 232703.6 | 233569.8
Simulated 2,861,055kWh
Pkg OA HP 2,607,102 kWh
EUI Change -42kWh/year [9.0%]

## Slide 57: 6. Replacement of RTU-1 with Package Unit that includes CDQ Wheel_01
Cooling Unit Size 43.4 kW [148 kBTU]/Heating Unit Size 21.3 kW [74 kBTU]
Cooling Efficiency of Unit 4.70 COP [EER 16] @ AHRI
Change in EUI -50 kWh/year
Annual Energy Saved 298,599 kWh [866,488 kBTU]
US Dollars Saved $23,888/year
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 58: 6. Replacement of RTU-1 with Package Unit that includes CDQ Wheel_02
Cost Data Based on Updated Building Sector Appliance & Equipment Costs & Efficiencies
Retail Cost Per 90 kBTU $ 22,500
Installation Cost Per 90 kBTU $ 25,500
Retail Cost Per 148 kBTU $ 37,000 [Estimated]
Installation Cost Per 148 KBTu $ 40,800 [Estimated]
Dehumidification Wheel Cost $ 6,000 [Assumed]
Total Cost on Site $ 46,800 [Removing Old Unit, Transportation, & Misc]
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 59: ECM_06 Replacement of RTU-1 Monthly Energy Consumption
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| January | February | March | April | May | June | July | August | September | October | November | December
Overall Simulated | 280568.7 | 233441.4 | 247558.3 | 222900.8 | 229969.8 | 222243.7 | 231117.5 | 230231.1 | 226293.9 | 227450.1 | 254154.7 | 255125.3
Replacement of RTU-01 | 261403.5 | 220106.9 | 238112 | 205080.5 | 197716.4 | 185842.7 | 194999.1 | 192887.1 | 189499.7 | 203552.8 | 232979.6 | 240275.7
Simulated 2,861,055kWh
SCF-01 RTU 2,562,456 kWh
EUI Change -50 kWh/year [10%]

## Slide 60: 7. Replacement of Centrifugal with Plenum Fans
2017 ASHRAE LowDown Showdown Modeling Competition
Location | Existing SFP W/L/s [W/cfm] | Retrofit SFP W/L/s [W/cfm]
ADMIN Zone | 3.40 [1.60] | 1.0 [0.50]
SCF-01 | 4.50 [2.12] | 1.0 [0.50]
SCF-02 | 3.00 [1.41] | 1.2 [0.60]
SCF-03 | 3.00 [1.41] | 1.2 [0.60]
Capital Cost $ 20,000
Change in EUI -104 kWh/year
Annual Energy Saved 623,398 kWh [2,127,034 kBTU]
US Dollars Saved $49,871/year

## Slide 61: 7. Replacement of Centrifugal with Plenum Fans
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: 
| January | February | March | April | May | June | July | August | September | October | November | December
Overall Simulated | 280568.7 | 233441.4 | 247558.3 | 222900.8 | 229969.8 | 222243.7 | 231117.5 | 230231.1 | 226293.9 | 227450.1 | 254154.7 | 255125.3
Plenum Fans | 232798.3 | 189496.5 | 197073.7 | 171403.9 | 174703.9 | 167968.8 | 174943.3 | 174310.6 | 172536 | 173121.9 | 204722.2 | 204578.2
Simulated 2,861,055kWh
Plenum Fan 2,237,657 kWh
EUI Change -104 kWh/year [22%]

## Slide 62: Energy Use Intensity Comparison for ECMs
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Use Intensity (kWh/m²/year)
Overall Simulated | 476.2714
EUI_INFILTRATION | 457.5687
EUI_WINDOW | 444.1695
EUI_SETPOINT | 442.9801
EUI_Pkg_OA | 433.9966
EUI_RTU-01 | 426.5645
EUI_PLENUM | 372.4962
EUI_LED | 359.8375
4.0 %
6.7 %
7.0 %
9.0 %
10 %
24%
22 %

## Slide 63: Retrofit Building with Solar Panels
2017 ASHRAE LowDown Showdown Modeling Competition

## Slide 64: Combined ECMs
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| January | February | March | April | May | June | July | August | September | October | November | December
Energy Consumption (kWh) | 47164.4 | 39922.5 | 40187.5 | 29341.9 | 24041.8 | 29126.5 | 35814 | 29890.1 | 23199.4 | 25305 | 39955.3 | 41284.1
All ECMs 405,233 kWh
EUI Change -409 kWh/year [86%]

## Slide 65: Retrofit Building Energy Consumption by Component
2017 ASHRAE LowDown Showdown Modeling Competition
Chart: Energy Consumption (kWh)
| Energy Consumption Breakdown Per Year (kWh)
Heating | 149499.6
Cooling | 90442.8
Interior Lighting | 78544.5
Interior Equipment | 45250.2
Fans | 18789.3
Pumps | 2875.1
Heat Rejection | 5772.9
Heat Recovery | 14058.1

## Slide 66: Cost Saving Per Year
2017 ASHRAE LowDown Showdown Modeling Competition
ECM Description | Capital Cost | Savings/Year | Payback (Years)
ECM-01 Window | $ 180,768 | $ 15,427 | 12.0
ECM-02 Infiltration | $ 5,000 | $ 9,000 | 0.6
ECM-03 Setpoint | $ 0 | $ 16,000 | 0.0
ECM-04 LED | $ 35,000 | $ 56,000 | 0.6
ECM-05 Pkg HP ADMIN | $ 35,000 | $ 20,316 | 2.0
ECM-06 RTU-1 Replacement | $ 46,800 | $ 23,888 | 2.0
ECM-07 Plenum Fans | $ 20,000 | $ 49,871 | 0.4
Total Cost | $ 322, 568 | $ 190,502 | 1.70

## Slide 67: Total Cost Savings
2017 ASHRAE LowDown Showdown Modeling Competition
ECM Description | Capital Cost | Savings | Energy Saved [kWh]
PV Panel | $ 635,893 | $ 18,500 | 231,193
All ECMS | $ 322,568 | $ 190,502 | 2,380,571
Total Cost | $ 958,461 | $ 209,002 | 
Dollars Saved in First Year $ 209,002
Dollars Saved from Second Year $ 18,500
Total Payback Time 40 Years

## Slide 68: Summary
2017 ASHRAE LowDown Showdown Modeling Competition
LDSd Result Summary | Existing Building_Metered | Existing Building_Simulated | Retrofit Building
Total Energy Usage (kBTus) | 10,978,130 | 9,772,568 | 1,382,655
Site EUI (kBTU/sf) | 170 | 151 | 21
Source EUI (kBTU/sf) | 533 | 475 | 67
Annual Electricity Usage (kWh) | 3,217,506 | 2,864,176 | 405,233
Annual NG Usage (Therms) | 0 | 0 | 0
Annual Water Usage (Gallons) | * | * | *
Annual Electricity Cost (US $) | 404,791 | 360,339 | 85,254
Annual NG Cost (US $) | 0 | 0 | 0
Annual Water Costs (US $) | * | * | *
Total Annual Costs (US $) | 404,791 | 360,339 | 85,254
CPSF (US $/sf) | 6.26 | 5.57 | 1.32
Total Energy Generation (kBTUs) | 0 | 0 | 788,834
Net Zero Energy (kBTUs) | N/A | N/A | 593,821
Carbon Equivalent (0.63 kg/kWh) | 2,027,029 | 1,804,431 | 110,459

## Slide 69: Conclusion
2017 ASHRAE LowDown Showdown Modeling Competition
We are consuming 174,039 kWh [593,821 kBTUs] more than generated electricity through Photovoltaic Panels.
We have not achieved net zero energy but we were able to reduce energy consumption by approximately 87% without using renewable energy.
Possible alternatives to achieve net zero
Increasing area of photovoltaic panel from 10,000 ft² to approximately 18,000 ft².
Exploring possibility of vertical ground source heat pumps to reduce heating energy as heating is approximately 40% of total energy usage in retrofit building model.
Reducing Heating Temperature from 16 °C [60 °F] to 12 °C [53 °F] in months of heating for shared collection facility.

## Slide 70: End
Thank you for your time
Any Questions?
2017 ASHRAE LowDown Showdown Modeling Competition