## Slide 2: ASHRAE Tech Hour
ASHRAE Tech Hour
Commissioning (Cx)

## Slide 3: Jay Enck - Speaker
  Co-Founder and Chief Technical Officer of Commissioning & Green Building Solutions, Inc.
  Mechanical Engineer, credited for the creation of the Holistic Commissioning® process
  Well-established, innovative leader in commissioning, operational efficiencies, building enclosure forensics, green design, and sustainable development, with over 40 years of experience in engineering, construction, building operations and whole building commissioning in multiple market sectors.

## Slide 4: Reinhard Seidl - Speaker
  Principal at Taylor Engineering LLP in Alameda, CA
  Registered Mechanical Engineer with an MS in Mechanical Engineering from the Delft University of Technology in the Netherlands.
  Over 25 years of experience in the construction and commissioning sector, both as a project engineer and project manager for a Design/Build contractor, and as a consulting engineer.
  Focused on commissioning projects for the last 10 years and worked extensively with PG&E and other industry partners to help develop and bring a free trend analysis tool to the engineering community, along with training classes for its use.

## Slide 5: Overview and Learning Objectives
You will learn the following:
Why is Commissioning our existing building stock so important?
What are some of the most important steps to reducing energy consumption? Correct controls, then maintain.
How do new technologies help in implementing higher systems efficiency and ongoing Cx with cloud-based documentation methods and energy monitoring?

## Slide 6: Climate Change – it’s real
Increased fires
      Australia’s fire released carbon exceeding twice their annual fossil fuel emissions. 14.7 million acres burned
      California 58,000 fires total, 8.8 million acres, $24 billion losses
Flooding + Sea Level rise
NOAA shows cost of Hurricanes in 2017 as $306 billion flooding.
Tipping point mechanisms
      The Amazon rainforest is teetering on a tipping point that could turn it into savanna and release 140 billion tons of carbon.
      Arctic permafrost and Siberian bogs are melting and releasing about 5 times as much methane as predicted, further speeding up climate change. Methane’s GWP is 23x that of CO2.
Notes: References
Australian wildfires
https://www.bbc.com/news/world-australia-51101049;
https://www.businessinsider.com/australia-fires-astronaut-photographs-space-station-2020-1; https://www.sciencealert.com/stunning-images-from-space-reveal-the-extent-of-australia-s-bushfire-crisis
About 900 million tons of carbon unleashed by Australian fires: https://www.nbcnews.com/science/environment/australia-wildfires-unleash-millions-tons-carbon-dioxide-n1120186, or roughly twice Australia’s annual fossil fuel emissions
Arctic permafrost melting https://www.washingtonpost.com/weather/2019/12/10/arctic-may-have-crossed-key-threshold-emitting-billions-tons-carbon-into-air-long-dreaded-climate-feedback/
Siberian bogs are melting because arctic permafrost is melting. These bogs are releasing roughly five times the amount of methane that was initially predicted, thus further accelerating global warming https://www.theguardian.com/environment/2006/sep/10/russia.climatechange
https://www.youtube.com/watch?v=YegdEOSQotE Katey Walter Anthony, Univ. of Alaska
https://www.adn.com/arctic/2018/09/24/across-the-arctic-lakes-are-leaking-dangerous-greenhouse-gases/
Further deforestation could send the amazon to a tipping point where massive die-off occurs, releasing up to 140 billion tons of carbon https://www.businessinsider.com/amazon-rainforest-reaching-tipping-point-deforestation-experts-warn-2019-12
https://advances.sciencemag.org/content/5/12/eaba2949
https://www.businessinsider.com/amazon-fires-may-help-dieback-emit-carbon-hurry-climate-change-2019-8
Sea Level Rise: https://www.climatecentral.org/news/report-flooded-future-global-vulnerability-to-sea-level-rise-worse-than-previously-understood
Syrian Refugees https://en.wikipedia.org/wiki/Refugees_of_the_Syrian_Civil_War

## Slide 7: Cost of doing business
Our basic utility costs are not sustainable – the cost of dealing with the effects of our “energy appetite” are not part of the utility bill
Current financial calculations are at the heart of all business transactions and fail to capture the impact of climate change.
They currently fail to capture the impact of climate change on various state or federal budgets, because energy pricing does not even attempt to include these effects so far
How can the built environment reduce its impact?
Notes: Clean Air Act : https://www.kcet.org/history-society/how-los-angeles-began-to-put-its-smoggy-days-behind
Clean water act https://www.alleghenyfront.org/how-a-burning-river-helped-create-the-clean-water-act/

## Slide 8: University Building
Completed in 1997
123,053 Sq Ft
Selected for LEED-EB
  “Good Building”
  “Has Many Green Features”
Only 13 work orders recorded – no significant issues reported
No known occupant complaints
Energy usage monitored since completion
Considered one of university’s “Best”

## Slide 9: Energy Star Benchmark

## Slide 10
Energy Usage
Steady Increase In Electrical Consumption
No Correlation To Operational Parameters
  Schedule
  No. of Occupants
  Climate Variations
  Mechanical System Operation
    System Static
    Fresh Air Fraction
    System Trends
  Electrical System Operation
    Motors
    Lighting
    Plug

## Slide 11: Energy Patterns

## Slide 12
HVAC system consuming +50% more energy than required
  Simultaneous heating & cooling
  Negatively pressurized
  Make-up air restricted
  VFD fans operating at higher than necessary static pressure
Overall utility consumption estimated 40% more than required
  Operating 24/7/365
University Building

## Slide 13
Buildings consume about 40% of US energy in 2018
Energy Consumption
Notes: Full US Energy Information Administration outlook to 2050 https://www.eia.gov/outlooks/aeo/
https://www.eia.gov/tools/faqs/faq.php?id=86&t=1 and
Pie chart created from Table 2.1 in PDF https://www.eia.gov/totalenergy/data/monthly/pdf/sec2_3.pdf

## Slide 14: Overview and Learning Objectives
You will learn the following:
Why is Commissioning our existing building stock so important?
What are some of the most important steps to reducing energy consumption? Correct controls, then maintain.
How do new technologies help in implementing higher systems efficiency and ongoing Cx with cloud-based documentation methods and energy monitoring?

## Slide 15
  Typical control sequence:
“Controls shall automatically reset setpoint to optimize energy use while maintaining comfort.”
Fix Building Control Systems

## Slide 16
“Controls shall automatically reset setpoint to optimize energy use while maintaining comfort.”
Fix Building Control Systems
Notes: Translation steps are difficult:
from a general idea that “we want controls to be efficient” to an actual control sequence (in English) is one step, and much can be lost in translation
From the Sequence of operations in English to a programmed controller is another translation, and again, there are many errors that can creep in along the way

## Slide 17
  Problem:
  HVAC controls are poorly understood
  Last trade on construction jobs
  Tight cost competition
  Re-inventing the wheel
  Typical Result:
  Design intent not achieved
  Poor temperature control
  Increased energy use
Fix Building Control Systems

## Slide 18
  Collection of best practice HVAC control sequences
  Published June 2018
  Benefits:
  Improved energy efficiency
  Improved thermal comfort
  Improved code compliance
  Streamlined product development
ASHRAE Guideline 36

## Slide 19
ASHRAE Guideline 36 – Value Proposition

## Slide 20
  Retrofit of obsolete HVAC control system (2015)
    5-story office building
    140,000 ft2, 1999 construction
    Redwood City, CA
    Pre-existing digital controls
    Scope limited to controls
  Energy Efficiency Measures
    Replaced economizer actuators and reheat valves
    Guideline 36 sequences (pre-publication)
ASHRAE Guideline 36 – Case Study

## Slide 21
2018 ASHRAE Technology Award Winner
  15% whole building electricity savings
ASHRAE Guideline 36 – 555 County Center

## Slide 22
  56% natural gas savings
  7-year simple payback
ASHRAE Guideline 36 – 555 County Center

## Slide 23
  Retrofit of obsolete HVAC control system
    2-story medical office building
    200,000 ft2, 1990/1992 construction
    Pneumatic zone controls
  Energy Efficiency Measures
    Replaced air handling units
    Digital controls at zones
    Guideline 36 sequences
ASHRAE Guideline 36 – Case Study
CBE Occupant Surveys
2021 ASHRAE Technology Award Winner

## Slide 24
Overall Building EUI reduction of 38%
ASHRAE Guideline 36 – Results

## Slide 25
38.5% CHW Energy Reduction
ASHRAE Guideline 36 – Results

## Slide 26
56% Hot Water Energy Savings
ASHRAE Guideline 36 – Results

## Slide 27
Under continuous maintenance
  This is ASHRAE’s way of saying the Guideline will be updated every few years
  Sequences for more complex systems
  Clarifications and Adaptations
    For particular areas in the country
    Addenda
https://www.ashrae.org/technical-resources/standards-and-guidelines/standards-addenda/addenda-to-guideline-36-2018
http://gpc36.ashraepcs.org/
ASHRAE Guideline 36

## Slide 28: Performance Issues Facing Owners
No feed back loop on building performance
    Operational issues affecting building performance
          Behavioral occupants + operators
          Control Issues
          Equipment performance deterioration
Fire Fighting Mode
    Occupant Complaint Focused
          Controls overridden
          Incorrect set points implemented
          Equipment malfunction
    Increased Cost + Carbon Emissions
          Increased utilities
          O&M trouble shooting
          Additional wear & tear
*Reference LBNL “Building analytics and monitoring-based commissioning: industry practice, costs, and savings”

## Slide 29
Metrics to Manage to Evaluate Cost/Benefit
  Costs
        Utilities
        Operation & maintenance
        Labor to execute mission
  Benefits add to bottom-line
        Reduced expenses
        Improve operation & maintenance efficiency
        Increased productivity of occupants
        The right data and tools yield better management opportunities
Ongoing Commissioning

## Slide 30
33K GSF office building
    Vampire plug loads
    High data center consumption
Ongoing Cx - Better Management Tool

## Slide 31
VRF System
  Isolated areas of simultaneous heating & cooling
Occupied period
Ongoing Cx - Better Management Tool

## Slide 32
DOAS with 5 stages of Dx Cooling
  New equipment not performing as intended
Ongoing Cx - Better Management Tool

## Slide 33
Cut up to 30 percent off your energy bill – The LBNL study examined 643 US buildings and found that commissioning resulted in a median of 16 percent whole-building energy savings for existing buildings and 13 percent for new buildings. What’s more, over a quarter of the buildings surveyed in a Lawrence Berkeley National Laboratory study realized a dramatic 30 percent energy savings from commissioning.
Efficiency Increases using Cx

## Slide 34
Marshall Spaceflight Center

## Slide 35
26% reduction ($40K) in HVAC work orders
Marshall Spaceflight Center

## Slide 36
Initial Occupant Survey
Post Occupant Survey
Marshall Spaceflight Center

## Slide 37: The Business Case
Financial Performance
  Lower operating costs increase asset value
    Directly to bottom line
  Owner occupied
    Increased productivity/operational efficiency + lower utility/maintenance expenses
    Higher employee workplace satisfaction
  Landlord leased
    Can be more competitive: lower CAM/marketing/administrative costs
    More efficient utilization of O&M staff + lower utility/maintenance expense

## Slide 38
Van Leer Innovative Design Center

## Slide 39: Example Use of Data

## Slide 40
Continuous Feed Back
  CEO/CFO
    Financial
  Facility Manager
    General and More Specific Information
  Resource Manager
    Specific Types/Category of Issues
  Technician
    Specific Information About the Issue
    Suggested Corrective Actions
Information Available for Decisions

## Slide 41
  Case Study: Mississippi University: Making Changes
    Identification of key issues affecting performance
      Combine institutional knowledge with a powerful computing tool
      Management by exception
MBCx: Tool for Better Stewardship of Resources

## Slide 42
  Case Study: Mississippi University: Making Changes
  Review 39,700 points covering 70 buildings at 15 minute intervals & analyze 3,811,200 pieces of data daily
      Example
      Review of 1,100 VAV boxes identified 30 that are responsible for consuming $22,256/month in additional electricity ($267,072/yr)
MBCx: Tool for Better Stewardship of Resources

## Slide 43
MBCx is cost effective to implement
Facilitates Persistent Performance
  People
    Better occupant productivity
    More efficient operational staff
  Planet
    Reduces utility consumption green house gas emissions
  Financially
    Increases value of the building asset
    Lowers the total cost of ownership
References:
LBNL “Monitoring-Based HVAC Commissioning of an Existing Office Building for Energy Efficiency”
LBNL “Improving Energy Efficiency through Commissioning: Getting Started with Commissioning, Monitoring, and Maintaining Performance”
LBNL “Building Commissioning Costs and Savings Across Three Decades and 1,500 North American Buildings”
Conclusions

## Slide 44
Understanding what changes to make requires an understanding of the building
Systems Assessment, Energy Baseline creation, development of ECM’s (Energy Conservations Measures) typically takes months
Smaller buildings typically have no BAS
Larger buildings often have Legacy BAS systems which still require a lot of conversion
More technology allows better asset valuation
O&M staff has difficulty conveying this value to ownership
Limits of Ongoing Commissioning

## Slide 45
Energy systems data should be managed. It represents value when future projects have to show performance improvements (for rebates) or to guide operations staff by showing consumption baselines.
Building Automation System (BAS) data can be used for troubleshooting when energy data indicates problems.
Existing Building Assessment
This may mean storing data in the cloud, perhaps with 3rd party assistance. Local server data often “disappears” after machine crashes, replacement or software upgrades.

## Slide 46: Overview and Learning Objectives
You will learn the following:
Why is Commissioning our existing building stock so important?
What are some of the most important steps to reducing energy consumption? Correct controls, then maintain.
How do new technologies help in implementing higher systems efficiency and ongoing Cx with cloud-based documentation methods and energy monitoring?

## Slide 47: Changes Building Systems, Controls
Changing to all-electric system makes sense on some areas more than others, for example in Utah, swapping gas for electrical energy would make things worse from a carbon footprint perspective because coal is used to make electricity.
Real-time calculation of the grid emissions (by location) allow devices to use cleaner energy with controls. There is new technology1 now being developed by the Rocky Mountain Institute, recently joined by the original developers WattTime2.
1 https://rmi.org/wp-content/uploads/2017/06/Automated-Emissions-Reduction-Primer_RMI-Validation_June2017.pdf
2 https://rmi.org/helping-consumers-reduce-carbon-emissions-watttime-joins-rmi-subsidiary-organization/
Notes: Note that the real-time monitoring of grid energy in terms of carbon emissions, and the resulting operation of particular devices connected to the internet is very much in its infancy. The presenter has not yet seen this system in action at an actual site, so some caution may be warranted before recommending this to any customers.
However, it is yet another element in the discussion about decarbonization and associated challenges that practitioners may want to be aware of, by involving not just HVAC system choices and commissioning efforts but also ongoing real-time control system effects of the changing energy picture.

## Slide 48: Grid Carbon Emissions, CA
In May of 2019, CO2 emissions for the CA grid were roughly half as much as in 2014
http://www.caiso.com/TodaysOutlook/Pages/emissions.aspx
Notes: Another chart from CAISO illustrating ongoing efforts in California to reduce greenhouse gas emissions, and the fairly breathtaking pace at which this has occurred – grid CO2 emissions have roughly been cut in half in the last 5 years !

## Slide 49
https://www.eia.gov/beta/states/overview
Advances in Dashboards
Notes: Another chart from CAISO illustrating ongoing efforts in California to reduce greenhouse gas emissions, and the fairly breathtaking pace at which this has occurred – grid CO2 emissions have roughly been cut in half in the last 5 years !

## Slide 50: New Technologies support Cx
Documentation that can be made available to Owners:
Electronic Systems manuals including training videos
  Available for online or offline use (during power outages)
  Complete with original drawing files (example Revit) to allow for retrofits without having to spend significant discovery or as-built creation effort by next construction team
  Clear goals for original construction or most recent retrofit, spelled out in a way that allows for check back after a year to see if original goals were met. Objective “lessons learned” from this review, along with issues log

## Slide 51: New Technologies support Cx
Documentation that can be made available to Owners:
Photographic records in Electronic Systems manuals
  Ability to record construction as it progresses using 360 photography over time to record not just what completed systems look like, but also what hidden services look like before being covered up (location of radiant floor piping, electrical and piping in walls)
  Ability to conduct virtual walk-throughs in both time and space, similar to Google Earth for satellite images, but within building
  Ability to link O&M and maintenance information to equipment in virtual walk-through environment

## Slide 52: Record Construction and Issues Log
Virtual walk-through in time and space
  Record construction in progress, allow “walk through” type records, including for off-line use after project completion and for use in next retrofit
  Show hidden utilities in walls and concealed spaces
Notes: This example shows a recent project where your presenter provided Cx services and shows the ability to track issues in a particular location and reference the issues log from the 360-photo tool.
The issues log can also reference the 360-photo tool and allow the reader of the issues log to jump directly to a particular location referenced by an issues log entry, with hyperlinks in either application.
The issue in question related to several VAV terminals located high above a hard lid-ceiling, raising concerns they would not be accessible in future without an access door and possibly walkable ceiling.
The video shows the evolution of the construction over time, the exact location of the actually mounted terminals and actuators, and the placement of the access door as a backcheck. All of this information remains, and can be used in discussions at a conference table or a virtual conference to “walk” through multiple issues of this kind with a project team, with the majority of project team members never having to walk to the location to nevertheless get a complete understanding of what is discussed.
Final resolutions can be documented, and the owner can check at their leisure.
The marketplace offers many competitive solutions with very similar features for this purpose.

## Slide 53: Record Construction and Issues Log
Virtual walk-through in time and space
  Record construction in progress, allow “walk through” type records, including for off-line use after project completion and for use in next retrofit
  Show hidden utilities in walls and concealed spaces
Notes: Some tools are specifically built to allow issue tracking in 3D, so that the information remains after project completion for building engineering staff and the next retrofit team so that the history of changes or particular elements in the construction is not lost.
Instead of using site photographs (like the previous tool) over time, this tool uses a BIM model, whose format is converted to a fast 3D walkthrough model that is easier to use for non-engineering users.

## Slide 54: Walk-through for Progress, Training
https://als.lbl.gov/about/3d-models-virtual-reality/
Virtual walk-through in time and space
  Record construction in progress, allow “walk through” type records, including for off-line use after project completion and for use in next retrofit
  Show hidden utilities in walls and concealed spaces
Notes: Existing buildings can be scanned with a number of different applications using laser distance measurement, as this example shows.
This produces a photo-realistic overlay over a 3D point cloud generated by a laser scan.
The resulting surfaces are measurable since the laser is accurate enough to provide this information in 3D.
For existing building projects, a team can therefore evaluate what kind of replacement components will fit, whether openings have to be made wider, whether service access will be sufficient and the like, without having to re-visit the site every time a new option is discussed and a particular element of the existing building has not yet been reviewed.
Depending on the tool used, the laser-generated point clouds can also be imported into BIM tools like Revit to allow the design coordination of retrofit or equipment replacement elements.

## Slide 55: New Technologies support Cx
Building Performance Data
  Free tool developed for public use with CA ratepayer funding: Universal Translator 3 (UT3)
http://www.utonline.org
https://www.youtube.com/channel/UCBoX0iMkfM7utPckbauKzQA for training videos
Notes: The Universal Translator allows the collection of large amounts of data, for example several months of 1-minute data from a large building, capturing all Building Automation System data.
This data can then be analyzed and made visible using a number of included analysis routines such as setpoint analysis, which automatically steps through all pieces of equipment to determine how well they maintained a certain setpoint.
For example, it can analyze the behavior of all air terminals with respect to temperature and temperature setpoints, or airflow adherence to setpoint. It then ranks all terminals for their performance over the entire trend period.
Using the analysis results, the best and worst performers can be visually shown with time-series, scatter chart or day-of-the-week charts to provide more intuitive feedback.
While this semi-manual approach to building analysis requires some training, both the tool and training sessions are available for free. Commissioning Providers can provide significant added value by performing trend reviews in addition to field-level functional testing.
See http://www.utonline.org and
https://www.youtube.com/channel/UCBoX0iMkfM7utPckbauKzQA for training videos

## Slide 56: New Technologies support Cx
Documentation that can be made available to Owners:
Building Performance Data
  Can be custom energy information system, Building Automation System (BAS) trend data, or even just utility meter data.
  Clear goals for original construction or most recent retrofit, spelled out in a way that allows for check back after a year to see if original goals were met.
  Objective comparison of original expectations and actual performance to judge level of satisfaction, and to guide further actions
Notes: Building performance data is still one of the most under-utilized tools for owners and commissioning providers.
While functional testing is required by most Cx guidelines and LEED, trend reviews are not mandated in any of the current Standards or Guidelines related to commissioning.
The reason for this is likely the fairly high degree of complexity associated with data collection and processing.
However, regular use of this data and familiarity of various stakeholders with their building’s actual performance and shortcomings would do much to reduce overall energy use in the building sector.
There are many tools available to facilitate the use of building automation system and metering data to complement new building and ongoing facility commissioning. They become a central element for monitoring-based commissioning (MBCx)

## Slide 57: New Technologies support Cx
Building Performance Data
  Many commercial tools and Energy Information Systems (EIS) to track and monitor building performance, automatically alert when actual performance is worse than anticipated performance
Notes: Many Energy Information Systems (EIS) exist. The vary from semi-manual where an owner or operator defines the operation of the tool and adds rules for fault detection or alarming, to completely packaged solutions set up by the vendor.
They are centered around the principle that information about a building or campus can be presented at a high level, and where problems are indicated, an owner or building engineer can “drill down” to a lower level of detail to troubleshoot behavior.
Typical Building Automation System (BAS) platforms do not have this capability by and large, and instead display simply a time-series chart of one or more control points such as fan status. Such low-level information is typically insufficient to review a whole building’s worth of data, and even more unsuitable for review of a whole campus.
EIS platforms are therefore useful when fast, daily review of building operation is desired and to maintain a building at a certain operating efficiency once the building has successfully been commissioned.

## Slide 58: New Technologies support Cx
Discuss EIS/FDD with Owner
  Potentially hire a subcontractor for the implementation of initial product deployment
  Discuss impact and expectations for ongoing Cx
  Discuss split between automated and human-dependent tasks in new building and existing building environments