## Sheet1
NO2, CO, CO2, and H2O Analysis for Unvented Heaters
Assumptions
Fuel is pure methane with complete stoichiometric combustion with dry air: CH4 + 2O2 + 7.52N2 -> CO2 + 2H2O +7.52N2
Combustion air is assumed to be 79% N2 and 21% O2 by volume, i.e., 79/21 = 3.76 moles of N2 per mole of O2
All gases are ideal (Pv=RT)
Indoor and outdoor air is 70 F, 14.7 psi
Outdoor air is dry (0% RH) and contains no CO
No internal sources of H2O or CO2 other than the unvented heater
Steady-state conditions
Well-mixed indoor space
NO2 and CO concentrations are considered negligible compared to O2, N2, H2O, and CO2 in the mass and energy balances
Air-free NO2 and CO test values assume dry heater exhaust with no excess air (i.e., no oxygen and no water vapor)
Variable | Value | Units | Description | Assumptions
(Note: The use of underscores in some of the variable names is merely a formatting requirement of Excel and has no technical signficance)
Input cells
Input Parameters
HC | 10000 | Btu/h | Unvented heater capacity | 40000 Btu/h is the upper limit from Z21
ANO2_ | 20 | ppm | Air-free NO2 concentration | 20 ppm is the upper limit from Z21
ACO | 200 | ppm | Air-free CO concentration | 200 ppm is the upper limit from Z21
Afl | 500 | ft2 | Indoor floor area
H | 8 | ft | Indoor ceiling height
ACHinf | 0.35 | 1/h | Infiltration rate | 0.35 /h is assumed to be typical of 62.2 compliance
CCO2oa | 0 | ppm | Outdoor CO2 concentration
CNO2oa | 0 | ppb | Outdoor NO2 concentration
Fixed Constants
DNO2_ | 0.8 | 1/h | Natural decay rate of NO2
LHVCH4 | 21500 | Btu/lb | Lower heating value of methane
MWCH4 | 16 | lb/lbmol | Molecular mass of CH4
MWO2_ | 32 | lb/lbmol | Molecular mass of O2
MWCO2 | 44 | lb/lbmol | Molecular mass of CO2
MWH2O | 18 | lb/lbmol | Molecular mass of H2O
MWN2_ | 28 | lb/lbmol | Molecular mass of N2
MWNO2_ | 46 | lb/lbmol | Molecular mass of NO2
MWCO | 28 | lb/lbmol | Molecular mass of CO
MWair | 29 | lb/lbmol | Molecular mass of air
Runiv | 1545 | ft-lb/lbmol | Universal gas constant
PPM | 1000000 | ppm | Parts per million
PPB | 1000000000 | ppb | Parts per billion
g_lb | 454 | g/lb | Grams per pound
PsH2Oia | 0.363 | psi | Saturation pressure of water at 70 F
P | 14.7 | psi | Atmospheric pressure
T | 70 | F | Indoor Temperature
Variable | Value | Units | Description | Equation
Combustion Analysis
nCH4_ | 0.02907 | lbmol/h | CH4 molar consumption rate | =mCH4_/MWCH4
nO2_ | 0.05814 | lbmol/h | O2 molar consumption rate | =2*nCH4_
nCO2_ | 0.02907 | lbmol/h | CO2 molar production rate | =1*nCH4_
nH2O | 0.05814 | lbmol/h | H2O molar production rate | =2*nCH4_
nN2_ | 0.2186 | lbmol/h | N2 molar rate through heater | =2*3.76*nCH4_
mCH4_ | 0.46512 | lb/h | CH4 mass consumption rate | =HC/LHVCH4
mO2_ | 1.8605 | lb/h | O2 mass consumption rate | =nO2_*MWO2_
mCO2_ | 1.2791 | lb/h | CO2 mass production rate | =nCO2_*MWCO2
mH2O | 1.0465 | lb/h | H2O mass production rate | =nH2O*MWH2O
mN2_ | 6.1209 | lb/h | N2 mass rate through heater | =nN2_*MWN2_
Indoor Air Calculations
Vuh | 4000 | ft3 | Volume of heated space | =Afl*H
Qoa | 23.3333 | ft3/min | Outdoor air volumetric flow rate | =Vuh*ACHinf/60
vair | 13.3391 | ft3/lb | Air specific volume | =Runiv/MWair*(T+460)/(P*144)
moa | 104.9546 | lb/h | Outdoor air mass flow rate | =Qoa/vair*60
HC_Vuh | 2.5 | Btu/h-ft3 | Heater capacity per unit indoor volume | =HC/Vuh
Carbon Dioxide Analysis
CCO2ia | 8032.2654 | ppm | Indoor CO2 concentration | =CCO2oa+(nCO2_)/(moa/MWair)*PPM
Humidity Analysis
yH2Oia | 0.016065 | lbmol/lbmol | Mole fraction of H2O in indoor air | =(nH2O)/(moa/MWair)
PH2Oia | 0.23615 | psi | Partial pressure of indoor water vapor | =yH2Oia*P
DRHia | 65.0547 | % | Increase in indoor relative humidity | =PH2Oia/PsH2Oia*100
Nitrogen Dioxide Analysis
Hcmax_A | 2840 | Btu/h | Maximum HC according to Option A | =0.71*Vuh
Hcmax_B | 3264 | Btu/h | Maximum HC according to Option B | =16.32*Vuh/ANO2_
GNO2_ | 10.3449 | mg/Btu | NO2 generation rate | =(nN2_+nCO2_)*ANO2_/(mCH4_*LHVCH4)*MWNO2*g_lb
CNO2ia | 416.5603 | ppb | Indoor NO2 concentration | =CNO2oa+(GNO2_*HC/PPM/g_lb/MWNO2)/((ACHinf+DNO2_)*Vuh/vair/MWair)*PPB
Carbon Monoxide Analysis
GCO | 62.9687 | mg/Btu | CO generation rate | =(nN2_+nCO2_)*ACO/(mCH4_*LHVCH4)*MWCO*g_lb
CCOia | 13.687 | ppm | Indoor CO concentration | =(GCO*HC/g_lb/MWCO)/(ACHinf*Vuh/vair/MWair)