## Sheet1
Table A-2. Summary of Calculated Hourly Delta T Values by Using U.S. National Weather Service's Reported Hourly Outside Dry Bulb Air Temperature Values and the ASHRAE Method for HVAC Design Heating Load Calculation, for Winter Season 2020-21 in Atlanta, Georgia
Date Interval | Calculated Calendar Day Delta T Values by Using Hourly Temperature Data | Calculated Daytime Delta T Values by Using Hourly Temperature Data | Calculated Nighttime Delta T Values by Using Hourly Temperature Data | Total Number of hours | Daytime Hours (6:00 A.M. to 7.00 P.M.) | Nighttime Hours (7:00 P.M. to 6:00 A.M.)
Dec. 20-22, 2020 | 1616 | 790 | 826 | 72 | 39 | 33
Dec. 23-25, 2020 | 2170 | 1098 | 1072 | 72 | 39 | 33
Dec. 26-28, 2020 | 2189 | 1098 | 1091 | 72 | 39 | 33
Dec. 29-31, 2020 | 1529 | 784 | 745 | 72 | 39 | 33
Jan. 1-3, 2021 | 1200 | 623 | 577 | 72 | 39 | 33
Jan 4-6, 2021 | 1873 | 943 | 930 | 72 | 39 | 33
Jan. 7-9, 2021 | 2391 | 1266 | 1125 | 72 | 39 | 33
Jan. 10-12, 2021 | 2278 | 1197 | 1081 | 72 | 39 | 33
Jan. 13-15, 2021 | 2065 | 1021 | 1044 | 72 | 39 | 33
Jan.16-18, 2021 | 2247 | 1140 | 1107 | 72 | 39 | 33
Jan. 19-21, 2021 | 1679 | 851 | 828 | 72 | 39 | 33
Jan. 22-24, 2021 | 1653 | 842 | 811 | 72 | 39 | 33
Jan. 25-27, 2021) | 996 | 520 | 476 | 71 | 39 | 32
Jan. 28-30, 2021) | 2275 | 1171 | 1104 | 72 | 39 | 33
Jan. 31-Feb. 2, 2021 | 2298 | 1236 | 1062 | 72 | 39 | 33
Feb. 3-5,2021 | 2009 | 1059 | 950 | 72 | 39 | 33
Feb. 6-8, 2021 | 2055 | 1033 | 1022 | 72 | 39 | 33
February 9-11, 2021 | 1043 | 500 | 543 | 72 | 39 | 33
February 12-14, 2021 | 1898 | 1022 | 876 | 72 | 39 | 33
Februay 15-17, 2021 | 2451 | 1331 | 1120 | 72 | 39 | 33
February 18-20, 2021 | 2203 | 1167 | 1036 | 72 | 39 | 33
February 21-23, 2021 | 1456 | 701 | 755 | 72 | 39 | 33
February 24-26, 2021 | 969 | 455 | 514 | 72 | 39 | 33
February 27-March 1, 2021 | 796 | 392 | 404 | 71 | 38 | 33
March 2-4, 2021 | 1540 | 729 | 811 | 72 | 39 | 33
March 5-7, 2021 | 1564 | 752 | 812 | 72 | 39 | 33
March 8-10, 2021 | 1085 | 472 | 613 | 72 | 39 | 33
March 11-13, 2021 | 529 | 258 | 271 | 40 | 18 | 22
March 14-16, 2021 | 745 | 440 | 305 | 72 | 39 | 33
March 17-19, 2021 | 1126 | 536 | 590 | 65 | 32 | 33
March 20-22, 2021 | 1184 | 617 | 567 | 65 | 34 | 31
Total Seasonal Values | 51112 | 26044 | 25068 | 2184 | 1175 | 1009
Total Seasonal Delta T Values by ASHRAE Design Heating Load Method* | 109418 | 58868 | 50551
Ratio of Seasonal Hourly Delta T Values to ASHRAE Method's Seasonal Delta T Values | 46.71% | 44.24% | 49.59%
*These values were calculated by multiplying the seasonal number of hours in each of the three categories by (72-21.9) to arrive at the total seasonal Delta T value per ASHRAE Design Heating Load Calculation Method.