## Sheet1 (hidden)
Total Wine
Ventilation Analysis
|  |  | 76 | people
Space Analysis | [6 empty] | CDC Air Changes/Hour Metric | [5 empty] | ASHRAE CFM/Person Metric
[5 empty] | 500 |  | Design CFM |  | 65% Design CFM |  | 35% Design CFM |  | Design CFM | 65% Design CFM | 35% Design CFM
Zone | Use Type | SF | People | CFM | OA CFM | RA CFM | AC/HR | CAC/HR | AC/Hr | CAC/HR | AC/Hr | CAC/HR | EqOA/Person | EqOA/Person | EqOA/Person | Min clean | max ppl
6/10 | Open | 1519 | 30 | 2500 | 99.167 | 2400.833 | 10.9721 | 8.5486 | 7.1319 | 5.7089 | 3.6559 | 2.9152 | 64.9269 | 43.3595 | 24.686 | 746.1915 | 24.873
8 | Open | 1090 | 22 | 1275 | 50.5752 | 1224.4248 | 7.7982 | 6.0757 | 5.0688 | 4.0575 | 2.5984 | 2.0719 | 45.1537 | 30.1545 | 17.168 | 380.5577 | 12.6853
9/11 | Open | 1217 | 24 | 2300 | 91.2336 | 2208.7664 | 12.5993 | 9.8164 | 8.1895 | 6.5556 | 4.1981 | 3.3475 | 74.666 | 49.8634 | 28.3889 | 686.4962 | 22.8832 | 60.4415
4 | Meeting | 187 | 12 | 450 | 17.8501 | 432.1499 | 16.0428 | 12.4993 | 10.4278 | 8.3473 | 5.3455 | 4.2624 | 29.2171 | 19.5118 | 11.1087 | 134.3145 | 4.4771
5 | Meeting | 302 | 20 | 520 | 20.6267 | 499.3733 | 11.479 | 8.9436 | 7.4614 | 5.9727 | 3.8248 | 3.0498 | 20.2572 | 13.5282 | 7.702 | 155.2078 | 5.1736
7 | Meeting | 414 | 28 | 720 | 28.5601 | 691.4399 | 11.5942 | 9.0333 | 7.5362 | 6.0326 | 3.8632 | 3.0804 | 20.0346 | 13.3795 | 7.6174 | 214.9031 | 7.1634
12 | Meeting | 502 | 33 | 1100 | 43.6335 | 1056.3665 | 14.6082 | 11.3816 | 9.4954 | 7.6009 | 4.8675 | 3.8812 | 25.9708 | 17.3438 | 9.8744 | 328.3243 | 10.9441
13 | Meeting | 396 | 24 | 1190 | 47.2035 | 1142.7965 | 20.0337 | 15.6087 | 13.0219 | 10.4238 | 6.6752 | 5.3227 | 38.6315 | 25.7989 | 14.6882 | 355.1871 | 11.8396
14 | Meeting | 229 | 9 | 475 | 18.8417 | 456.1583 | 13.8282 | 10.7739 | 8.9884 | 7.195 | 4.6076 | 3.674 | 41.1204 | 27.461 | 15.6344 | 141.7764 | 4.7259
3 | Coffee | 617 | 41 | 500 | 19.8334 | 480.1666 | 5.4025 | 4.2092 | 3.5116 | 2.811 | 1.8001 | 1.4354 | 9.5015 | 6.3453 | 3.6126 | 149.2383 | 4.9746
2 | Break | 541 | 36 | 1200 | 47.6002 | 1152.3998 | 14.7874 | 11.5212 | 9.6118 | 7.6941 | 4.9272 | 3.9288 | 25.9708 | 17.3438 | 9.8744 | 358.1719 | 11.9391
1 | Other | 2537 | 17 | 375 | 14.875 | 360.125
|  | 9551 | 296 | 12605 | 500 | 12105 | 8.7984 | 6.855 | 5.7189 | 4.5779 | 2.9316 | 2.3376 | 33.1785 | 22.1573 | 12.6149
0.052351
Space Analysis | [6 empty] | CDC Air Changes/Hour Metric | [5 empty] | ASHRAE CFM/Person Metric
[5 empty] | 1000 |  | Design CFM |  | 65% Design CFM |  | 35% Design CFM |  | Design CFM | 65% Design CFM | 35% Design CFM
Zone | Use Type | SF | People | CFM | OA CFM | RA CFM | AC/HR | CAC/HR | AC/Hr | CAC/HR | AC/Hr | CAC/HR | EqOA/Person | EqOA/Person | EqOA/Person
6/10 | Open | 1519 | 30 | 2500 | 198.334 | 2301.666 | 10.9721 | 8.6487 | 7.1319 | 5.9263 | 3.6559 | 2.899 | 65.6872 | 45.0106 | 27.1084
8 | Open | 1090 | 22 | 1275 | 101.1503 | 1173.8497 | 7.7982 | 6.1469 | 5.0688 | 4.212 | 2.5984 | 2.0604 | 45.6825 | 31.3028 | 18.8527
9/11 | Open | 1217 | 24 | 2300 | 182.4673 | 2117.5327 | 12.5993 | 9.9313 | 8.1895 | 6.8052 | 4.1981 | 3.3289 | 75.5403 | 51.7622 | 31.1747
4 | Meeting | 187 | 12 | 450 | 35.7001 | 414.2999 | 16.0428 | 12.6457 | 10.4278 | 8.6651 | 5.3455 | 4.2387 | 29.5593 | 20.2548 | 12.1988
5 | Meeting | 302 | 20 | 520 | 41.2535 | 478.7465 | 11.479 | 9.0483 | 7.4614 | 6.2001 | 3.8248 | 3.0329 | 20.4944 | 14.0433 | 8.4578
7 | Meeting | 414 | 28 | 720 | 57.1202 | 662.8798 | 11.5942 | 9.1391 | 7.5362 | 6.2623 | 3.8632 | 3.0634 | 20.2692 | 13.889 | 8.3649
12 | Meeting | 502 | 33 | 1100 | 87.267 | 1012.733 | 14.6082 | 11.5149 | 9.4954 | 7.8903 | 4.8675 | 3.8597 | 26.2749 | 18.0042 | 10.8434
13 | Meeting | 396 | 24 | 1190 | 94.407 | 1095.593 | 20.0337 | 15.7915 | 13.0219 | 10.8207 | 6.6752 | 5.2932 | 39.0839 | 26.7813 | 16.1295
14 | Meeting | 229 | 9 | 475 | 37.6835 | 437.3165 | 13.8282 | 10.9001 | 8.9884 | 7.469 | 4.6076 | 3.6536 | 41.6019 | 28.5067 | 17.1687
3 | Coffee | 617 | 41 | 500 | 39.6668 | 460.3332 | 5.4025 | 4.2585 | 3.5116 | 2.918 | 1.8001 | 1.4274 | 9.6128 | 6.5869 | 3.9671
2 | Break | 541 | 36 | 1200 | 95.2003 | 1104.7997 | 14.7874 | 11.6561 | 9.6118 | 7.9871 | 4.9272 | 3.907 | 26.2749 | 18.0042 | 10.8434
1 | Other | 2537 | 17 | 375 | 29.7501 | 345.2499
|  | 9551 | 296 | 12605 | 1000 | 11605 | 8.7984 | 6.9353 | 5.7189 | 4.7522 | 2.9316 | 2.3247 | 33.5671 | 23.001 | 13.8528
Max pop vs design pop
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!

## Instructions
Building Readiness Worksheet |  |  |  | Address
Date |  |  |  | City, State
This worksheet will help HVAC professionals to assess the ability of existing systems, particularly multiple-zone recirculating systems, to deliver the necessary equivalent clean airflow for infection control according to ASHRAE Standard 241-2023. It can also be used to document the Building Readiness Plan for a particular space or system. For more information on ASHRAE Standard 241, visit ashrae.org/241-2023
Assessment Process Tasks |  |  |  | Referenced Section in 241-2023
Step 1 - Gather Data |  |  |  | Section 8.2.3.1 and 8.2.3.2
Obtain the following relevant documents (if available): record or as-built MEP drawings, Cx documents, BAS documentation, TAB reports
Site observations must be performed, but can be done after Step 7 if there's sufficient documentation
Step 2 - Inventory Occupied Spaces |  |  |  | Section 8.2.3.3 and Appendix B.1
Determine space categorization related to Table 5-1 and ASHRAE 62.1 Table 6-1 and relevant occupancy details
Step 3 - Inventory Equipment |  |  |  | Section 8.2.3.4
Note the type and size of equipment serving each zone (e.g. VAV box or fan coil unit). Note the min and max airflow rates from the TAB report.
Note the type and size of the central HVAC equipment serving the building (e.g. rooftop unit or AHU). Note the filter type that is installed, and outdoor airflow setpoints
Step 4 - Inventory other engineering controls
Note quantity, size and location of room air cleaners
Quantify amount of natural ventilation
Identify if other air cleaning technologies are installed (e.g. UV)
Step 5 - Enter information gathered into the spreadsheet |  |  |  | Section 8.2.4.2 and 8.2.4.3
Enter AHU level information into the "AHU Data" table
Enter zone level information into the white cells of the "Zone Data" table
Step 6 - Evaluate results from spreadsheet
Identifty zones which need additional VEACI
If all zones are in compliance, move towards development of building readiness plans (BRP)
Step 7 - Use ECA Calculator to evaluate options for increasing VEACi
Create a copy of the assessment tab to reflect modifications to Vecai
Step 8 - Develop the building readiness plan |  |  |  | Section 8.1
Assumptions
Table 5-1 Min Equivalent Clean Airflow per person in breathing zone in IRMM
Occupancy Category |  | ECAi
|  | CFM/person | L/s/person
Correctional Facilities
| Cell | 30 | 15
| Dayroom | 40 | 20
Commercial/Retail
| Food and Beverage Facilities | 60 | 30
| Gym | 80 | 40
| Office | 30 | 15
| Retail | 40 | 20
| Transportation Waiting | 60 | 30
Educational Facilities
| Classroom | 40 | 20
| Lecture Hall | 50 | 25
Industrial
| Manufacturing | 50 | 25
| Sorting, Packing, light assembly | 20 | 10
| Warehouse | 20 | 10
Healthcare
| Exam Room | 40 | 20
| Group Treatment Area | 70 | 35
| Patient Room | 70 | 35
| Resident Room | 50 | 25
| Waiting Room | 90 | 45
Public Assembly/Sports and Entertainment
| Auditorium | 50 | 25
| Places of Worship | 50 | 25
| Museum | 60 | 30
| Convention | 60 | 30
| Spectator Area | 50 | 25
| Lobbies | 50 | 25
Residential
| Common Space | 50 | 25
| Dwelling | 30 | 15
Table 7-1 Infectious Aerosol Removal Efficiency for Mechanical Fibrous Filters
ANSI/ASHRAE 52.2 MERV RATING |  | ISO 16890 ePM | Weighted Epr
<11 |  | 0% | 0%
11 |  | 50% | 60%
12 |  | 65% | 71%
13 |  | 50% | 77%
14 |  | 70% | 88%
15 |  | 85% | 91%
16 |  | 95% | 95%
HEPA |  | ISO 20E | 99%

## Assessment
AHU Data
AHU Designation | AHU-X | <--From drawings, BAS, or facility managers
AHU-X maximum supply airflow |  | <--This can come from TAB reports, design data, or BAS
AHU-X minimum supply airflow |  | <--This can come from TAB reports, design data, or BAS
AHU-X expected supply airflow |  | <--This airflow rate will be used to evaluate if additional Vecai is needed. The higher the airflow rate towards the maximum setpoint, the more conservative the results.
AHU-X filter MERV rating |  | <--This can be found from submittals, site observations, or design docs
AHU-X filter effectiveness |  | <--Table 7-1
AHU-X minimum OA airflow |  | <--This can come from TAB reports, design data, or BAS
AHU-X maximum OA airflow |  | <--This can come from TAB reports, design data, or BAS
AHU-X expected OA airflow |  | <--This airflow rate will be used to evaluate if additional Vecai is needed. <--The higher the airflow rate towards the minimum setpoint, the more conservative the results.
Zone Level Data
Drawing Takeoffs or TAB Data | [5 empty] | Vacs | Vnv | Veca |  | zf x (Vot + Vmvs) |  |  | Vecai differential | Zone Interventions (if Vecai differential >0)
Zone Designation | Occupancy Category (Table 5-1) | Zone Area (Sq Ft) | People | SA CFM MAX | SA CFM MIN |  |  | ECAi per person | Vecai,target | Zone Fraction (ZF) | ZF Vot | ZF Vmvs |  | Increase airflow in the zone to a minimum setpoint of | Reduce zone population to maximum of | Air Cleaning System Necessary CADR
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
AHU Totals |  | 0 | 0 | 0 | 0 | 0 | 0