## Summary
Yellow areas are intended for your project-specific input. This data center was modeled using a (separate) manufacturer-provided performance tool. That tool must be used again to accurately reflect any changes to my design. | [5 empty] | 1
This example MLC calculation for a indirect evaporative cooling process in a fictitious data center was prepared by a SSPC 90.4 voting member and has been reviewed by two SSPC 90.4 members yet. | [5 empty] | 2
INPUT: Date of calculation summarized below: | Revision 3 - September 2021 |  | TMY3 file used in this MLC calculation (for Quincy, WA site): | 727826TY | Verify my climate zone appropriateness: | 4
INPUT: Elevation of project site: | 1259.52 | SELECT: ASHRAE Std. 169 climate zone for data center site: |  |  | https://openei.org/wiki/Climate_Zone_5B | 5
INPUT: ITE design power (12,000 ft² at 150 W/ft²): | 1800 |  |  |  |  | 6
INPUT: Fuel and water on-site storage criteria: | 72 | SELECT: UPS topography: |  | Assumed ELC used in this calc: | 0.231 | 7
INPUT: MLC calculation method summarized here: | used manuf's tool over & over |  |  |  | (for this MLC calculation to be valid, that ELC assumed value must match or exceed official ELC calculation result) | 8
Results per Standard 90.4 2019: | 0.087442 | Meets 90.4-2019 Section 6 | Meets 90.4-2019 Section 8 | Meets 90.4 section 11 | 0 | 10
Recovered and avoided energy displayed for: |  | Water flows, tank volume displayed for: |  | Design water storage volume: | 83000 | 11
Annual data center site savings due to heat recovery: | 5.0004e-12 | Annual fresh water use: | 7389.3293 | Power, tank below displayed for: |  | 12
|  | Annual wastewater produced: | 2463.1098 | Design fuel storage volume: | 8900 | 13
|  | Peak hourly wastewater flow: | 1310.1 | Modeled peak site inrush power: | 2652.0902 | 14
INPUT: Reason for this calculation: | An operating data center responds to frequent changes in outdoor air conditions. This data center design also automatically resets (predictably adjusts) the indoor air |  |  |  |  | 16
| conditions throughout the year in response to outdoor conditions. The 90.4 Standard requires a data center design to average energy performance across 4 scenarios, |  |  |  |  | 17
| detailed below. See this excel file's "Bins" tabs for each scenario's details. This MLC calculation is intended to be reviewable as a self-contained Excel file. That way, the |  |  |  |  | 18
| described heat recovery options can be "put in" or "taken out" of the displayed MLC Summary (for compliance verification as a credit). See the checkboxes, below. |  |  |  |  | 19
INPUT: Description of data center systems: | This design features a fully-separated aisle (VAV pressure controlled) ITE cooling zone and also a (thermal VAV) UPS cooling zone, each with their own dedicated roof- |  |  |  |  | 21
| top indirect evaporative cooling units. A ventilation system with 2 constant volume draw-through AHUs is configured with a 100% direct evaporative "face" and 100% |  |  |  |  | 22
| DX "bypass" modulating damper (see the excel file's Ventilation AHU Submittal tab). The ventilation air is forced into the ITE hot aisle plenum, normally pressurizing |  |  |  |  | 23
| that room relative to everything else. The UPS room is held negative by exhaust fans. The humidified ITE cold aisle air transfers into UPS room (to ventilate batteries). |  |  |  |  | 24
SELECT: Include checked heat recovery options below:
Electric Preheat of ventilation | Ventilation air is tempered with an electric coil to control humidity, as it is introduced. |  |  |  |  | 26
Ventilation air pressurizes building | No air-to-air recovery in calculation. The generator room is heated using additional electricity, increasing the MLC. |  |  |  |  | 27
The Café heats their own water | No air-to-water recovery included in design, no cooling effect from any water heater in the data center. |  |  |  |  | 28
Reason for each colorful column shown here: | Scenarios used in MLC compliance calculation, to show how system components are deferred by design at each ITE load point considered: |  |  |  | Data center equipment sizing: | 30
Percent of design ITE installed (for each scenario): | 25% | 50% | 75% | 100% | 100% | 31
Calculated annual mechanical energy in typical year: | 407374.9673 | 618763.1408 | 976861.1888 | 1345627.3589 | Critical operation: In this scenario, | 32
Calculated partial MLC for each scenario: | 0.10334 | 0.078483 | 0.082603 | 0.085339 | there is no gen room heating. | 33
Which columns here are for MLC compliance calculation? | Weighed 25% in final MLC | Weighed 25% in final MLC | Weighed 25% in final MLC | Weighed 25% in final MLC | Not used for MLC calculation. | 34
| MLC components (at 25%): | MLC components (at 50%): | MLC components (at 75%): | MLC components (at 100%): |  | 35
MLC component bar chart legend: | [5 empty] | 36
Ventilation system | [5 empty] | 37 | User Note: For most intuative bar chart representation, make certain vertical scales are of the same magnitude, in each energy scenario bar chart.
38
Generator heating | [5 empty] | 39
40
UPS room cooling |  |  |  |  | ITE, | 41
[5 empty] | UPS, | 42
ITE room cooling |  |  |  |  | distrib. | 43
[5 empty] | losses | 44
INPUT :Incoming electrical service segment loss (uncooled): | 15% | 13% | 14.5% | 16% | 17% | 46
INPUT: Electrical losses of operating UPS segment: | 8% | 7% | 8% | 6.2% | 6% | 47
INPUT: Distribution losses: | 2% | 2% | 2% | 2% | 3% | 48
INPUT: Outside air typical occuring and design low temps: | 11.3 | 11.3 | 11.3 | 11.3 | 0 | 50
INPUT: Outside air low typical, design low RH%: | 9.828% | 9.828% | 9.828% | 9.828% | 0% | 51
INPUT: Outside air typical and design peak high temps: | 106 | 106 | 106 | 106 | 110 | 52
INPUT: Outside air typical and design peak wet bulbs: | 73.1 | 73.1 | 73.1 | 73.1 | 75 | 53
INPUT: Owner's criteria for ITE air handlers' quantity: | 2 | 3 | 3 | 3 | 0 | 55
INPUT: Owner's criteria for ventilation air handlers' quantity: | 1 | 1 | 1 | 1 | 0 | 56
INPUT: Owner's criteria for UPS modules' quantity: | 1 | 1 | 1 | 1 | 0 | 57
INPUT: Owner's criteria for UPS air handlers' quantity: | 1 | 1 | 1 | 1 | 0 | 58
INPUT: Owner's criteria for Generators' quantity: | 1 | 1 | 1 | 1 | 0 | 59
INPUT: Negotiated ITE distribution transformer redundancy | 1 | 1 | 1 | 1 | 0 | 60
INPUT: reset ITE cold aisle upper temperature, by design: | 78 | 78 | 78 | 78 | 78 | 62
INPUT: reset ITE cold aisle lower temperature, by design: | 72 | 72 | 72 | 72 | 72 | 63
INPUT: ITE cold aisle low relative humidity setpoint: | 33% | 33% | 33% | 33% | 33% | 64
INPUT: ITE cold aisle high relative humidity setpoint: | 66% | 66% | 66% | 66% | 66% | 65
INPUT: Upper outdoor wet bulb temp for ITE cold aisle reset: | 50 | 50 | 50 | 50 | 50 | 66
INPUT: Lower outdoor wet bulb temp for ITE cold aisle reset: | 20 | 20 | 20 | 20 | 20 | 67
INPUT: ITE air temperature out minus temp. in, "Delta T" | 20 | 20 | 20 | 20 | 20 | 68
INPUT: How will design achieve hot & cold aisle separation? | Drop ceilings & cabinet chimneys | Drop ceilings & cabinet chimneys | Drop ceilings & cabinet chimneys | Drop ceilings & cabinet chimneys | Drop ceilings & cabinet chimneys | 69
INPUT: Airflow capacity, each ITE room rooftop cooling unit: | 32413.2142 | 32413.2142 | 32413.2142 | 32413.2142 | 32413.2142 | 70
INPUT: Hot water export (for recovery) capacity considered: | 933.8 | 933.8 | 1867.6 | 1867.6 |  | 71
Total cooling load within ITE zone: | 459 | 918 | 1377 | 1836 | 1854 | 73
Airflow required to cool ITE zone: | 72192.0276 | 144384.0553 | 216576.0829 | 288768.1106 | 291599.1705 | 74
Quantity of ITE room rooftop cooling units operating: | 5 | 8 | 10 | 12 | 9 | 75
Design operating power of ITE AHUs on standby: | 228.85 | 366.16 | 457.7 | 549.24 | 411.93 | 76
INPUT: portion of ITE that is intended to get UPS power: | 100% | 100% | 100% | 100% | 100% | 78
INPUT: Quantity of operating UPS modules: | 4 | 4 | 4 | 4 | 3 | 79
INPUT: Design low UPS supply temp. (to battery alcove): | 55 | 55 | 55 | 55 | 55 | 80
INPUT: Design high UPS supply temp. (to battery alcove): | 65 | 65 | 65 | 65 | 65 | 81
INPUT: UPS room Return - Supply temp, by design: | 21 | 21 | 21 | 21 | 21 | 82
INPUT: Upper outdoor wet bulb for UPS room reset: | 50 | 50 | 50 | 50 | 50 | 83
INPUT: Lower outdoor wet bulb for UPS room reset: | 40 | 40 | 40 | 40 | 40 | 84
INPUT: How will design keep lead acid batteries cool? | UPS air supplied into battery alcove | UPS air supplied into battery alcove | UPS air supplied into battery alcove | UPS air supplied into battery alcove | UPS air supplied into battery alcove | 85
INPUT: Design airflow, each UPS room cooling unit: | 19611.4484 | 19611.4484 | 19611.4484 | 19611.4484 | 19611.4484 | 86
Total cooling load in UPS room: | 36.72 | 64.26 | 110.16 | 113.832 | 111.24 | 88
Airflow required to cool UPS room: | 5500.345 | 9625.6037 | 16501.0349 | 17051.0694 | 16662.8097 | 89
Quantity of UPS room rooftop cooling units operating: | 1 | 1 | 1 | 1 | 1 | 90
Operating power of UPS AHUs on standby: | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 91
INPUT: Ventilation air supplied to ITE & from UPS | 412.5 | 825 | 1237.5 | 1650 | 1650 | 93 | User note: If you disagree with energy representation for annual energy for ventilation, here is the culprit. Just change this number.
INPUT: Quantity of ventilation AHUs operating: | 1 | 1 | 1 | 1 | 1 | 94
INPUT: Combined draw through fan + motor efficiency | 75% | 75% | 75% | 75% | 75% | 95
INPUT: Evaporative efficiency of direct evap media | 82% | 82% | 82% | 82% | 82% | 96
INPUT: Ventilation + exhaust fans' design total S.P. | 6 | 6 | 6 | 6 | 6 | 97
Operating power of vent AHUs on standby: | 0.21879 | 0.43758 | 0.65638 | 0.87517 | 1.5559 | 99
INPUT: Routine cycles of concentration in all sumps: | 3 | 3 | 3 | 3 | 3 | 101
INPUT: Drought cycles of sump concentration, to size tanks: | 6 | 6 | 6 | 6 | 6 | 102
Total electrical process load on standby: | 495.72 | 982.26 | 1487.16 | 1949.832 | 1965.24 | 104
Total sustained HVAC load on standby: | 264.1688 | 401.6976 | 493.4564 | 585.2152 | 448.5859 | 105
Generator design loading: | 812.7226 | 1464.2971 | 2079.3077 | 2652.0902 | 2503.543 | 106
INPUT: Quantity of 1250 KW diesel generators standing by: | 2 | 2 | 3 | 3 | 3 | 107
INPUT: Generator fuel use was based on this data. | 0.0692 | 0.0582 | 0.0556 | 0.0569 | 0.0569 | 109
INPUT: Generator block heater continuous per generator | 1 | 1 | 1 | 1 | 1 | 110
INPUT: Temperature setpoint in Generator room: | 60 | 60 | 60 | 60 | 60 | 111
INPUT: Temperature setpoint in Generator fluid: | 120 | 120 | 120 | 120 | 120
INPUT: Assumed efficiency of avoided gas heater: | 75% | 75% | 75% | 75% | 75% | 113
INPUT: Generator room typical & design heating peak: | 36.525 | 36.525 | 36.525 | 36.525 | 45 | 114 | User note: If you disagree with energy representation for annual heating of generator room, here is the culprit. Just change this number.
Air-to-air onsite
Air-to-water export
Air-to-air onsite

## 25% Bins
[197 empty] | NO | selected | Resulting | Resulting | Ventilation | Gen | UPS | ITE
| Notes on this 90.4 MLC calculation: | 2°F dry bulb bins (for hours equal or below 65°F dry bulb) | [7 empty] | Annual HW demand of cafeteria: |  |  |  | ITE zone | ITE zone | Properties of IT equipment zone: | [5 empty] | Properties for generic ventilation air handlers. | [17 empty] | Information used for hourly inputs for ITE room IDEC units (shown with heat recovery input) | [27 empty] | Outputs for ITE room IDEC units with heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | HR export |  | Generator room |  |  | Gen | [17 empty] | Outputs for ITE room IDEC units without heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | Without HR | UPS room variables | [13 empty] | Information used for hourly inputs for UPS room IDEC units | [27 empty] | Outputs for UPS units. NOTE: most of the performance values are PER UNIT | [18 empty] | Generator Room |  | Ventilation system |  | ITE and UPS cooling |  | Recovery | recovery | Mechanical | Mechanical | system | room | room | room
1. | This tab shows performance when data center is 25% loaded. There are two | bin | Outdoor | bin | average |  |  |  | Psychrometry for averaged points: | café avg | entering | kw from | H2O heater | delta T | % design | Temp | AHU | Min | Max | min. | max. | control | heat | liquid | Cooling | DX split | room air | Project | Design | Design | Reset | Resulting | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | energy avoided | Room heat | engine block | Recovery | Recovery | heat | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | error | ITE cooling | UPS room | Battery | Project | Design | Design | Design | Alternate | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | with | without | with | without | with | without | whatsoever | savings | Input | energy | HVAC | HVAC | cooling | cooling
| traditional modeling methods that I used here to determine the MLC. | name | dry bulb | hours | °F wb | dewpoint | %rh | moisture | enthalpy | 140 | temp | hot aisle | input energy | w/ HR | w/ HR | into ITE | SAT: | moisture | moisture | enthalpy | enthalpy | mode | power | added | needed | kW input: | dew point | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | elsewhere | need, kWh | heat, kWh | Potential | Savings | power | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | annual kWh | temp | temp | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | recovery | recovery | recovery | recovery | recovery | recovery | at all | kWh: | Power | incl. Recov | Component | component | component | component
|  | AB | 65 | 378 | 51.8048 | 40.53 | 40.64% | 0.0055757 | 21.66 | 554.4034 | 61.7 | 106.0761 | 141.4348 | 19.9289 | 24.67% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 2.4398 | 0.30348 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9289 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 65 | 73.1 | 51.8048 | 4" MERV 8 | 4" MERV 8 | 24.67% | -4 | 168.5455 | 65.3383 | 52.823 | 19.7818 | 48.5459 | 19.7818 | 4.2771 | 0 | 29440.2039 | 11412.7831 | 2.9619 | 1.8741 | 21.4361 | 5.2581 | 29258.1422 | 2851.7172 | 1.3873 | 0.018727 | 12.772 | 0.016804 | 32.8818 | 6.7714 | 5.6475 | 10.2735 | 1.1951 | 1.0256 | 145.8 | 21.3 | 72.9 | 10.65 | 0 | 218.7 | 31.95 | 9.8238 | 1.3722 | 0 | 0 | 0 | 693 | 0 | 0 | 0.91667 | 168.5455 | 65.5714 | 52.7818 | 19.8483 | 48.4834 | 19.8483 | 4.2984 | 0 | 29339.2726 | 11414.2385 | 2.947 | 1.8743 | 21.2555 | 5.2593 | 29156.0382 | 2864.0739 | 1.3788 | 0.018881 | 12.6498 | 0.017016 | 32.6364 | 6.7571 | 5.6868 | 10.3189 | 1.1936 | 1.0255 | 145.4 | 21.4 | 72.7 | 10.7 | 0 | 218.1 | 32.1 | 9.7961 | 1.3769 | 0 | 12771 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 65 | 73.1 | 51.8048 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8323 | 10.6963 | 16.2514 | 10.6963 | 17.5809 | 0 | 18044.9953 | 5956.6004 | 2.1698 | 0.75651 | 9.6251 | 1.1078 | 18611.7148 | 3633.1945 | 0.79749 | 0.035882 | 4.6704 | 0.041022 | 22.3 | 1.9 | 5.3337 | 20.0681 | 1.2005 | 1.0168 | 77.4 | 13.6 | 38.7 | 6.8 | 0 | 116.1 | 20.4 | 7.8993 | 2.0887 | 0 | 693 | 693 | 467.3379 | 1229.7314 | 13516.2 | 13489.2 | 15411.9314 | 1.819e-12 | 40.7723 | 15411.9314 | 1229.7314 | 693 | 2016.1412 | 11473.0588
2. | A 2°F bin hour-grouping method is shown on each of these 25%, 50%, 75% | AC | 63 | 251 | 50.3876 | 39.11 | 41.23% | 0.0052714 | 20.85 | 535.3187 | 61 | 103.3402 | 137.7869 | 19.9285 | 24.67% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 2.8782 | 0.37086 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9285 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 63 | 73.1 | 50.3876 | 4" MERV 8 | 4" MERV 8 | 24.67% | -4 | 168.5455 | 65.3371 | 52.8232 | 19.7814 | 48.5462 | 19.7814 | 4.277 | 0 | 29440.7241 | 11412.7756 | 2.962 | 1.8741 | 21.437 | 5.2581 | 29258.6687 | 2745.8783 | 1.3873 | 0.017391 | 12.7726 | 0.015026 | 32.8909 | 6.7714 | 5.6473 | 10.2756 | 1.1951 | 1.0256 | 145.8 | 20.9 | 72.9 | 10.45 | 0 | 218.7 | 31.35 | 9.8239 | 1.3458 | 0 | 0 | 0 | 476.9 | 0 | 0 | 0.95 | 168.5455 | 65.5714 | 52.7818 | 19.8483 | 48.4834 | 19.8483 | 4.2984 | 0 | 29339.2726 | 11414.2385 | 2.947 | 1.8743 | 21.2555 | 5.2593 | 29156.0382 | 2757.6914 | 1.3788 | 0.017535 | 12.6498 | 0.015215 | 32.6364 | 6.7571 | 5.6868 | 10.3213 | 1.1936 | 1.0255 | 145.4 | 21 | 72.7 | 10.5 | 0 | 218.1 | 31.5 | 9.7961 | 1.3504 | 0 | 8480.2143 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 63 | 73.1 | 50.3876 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8323 | 10.6963 | 16.2514 | 10.6963 | 17.5809 | 0 | 18044.9953 | 5956.6004 | 2.1698 | 0.75651 | 9.6251 | 1.1078 | 18611.7148 | 3279.766 | 0.79749 | 0.029306 | 4.6704 | 0.030245 | 22.3 | 1.9 | 5.3337 | 20.169 | 1.2005 | 1.0168 | 77.4 | 12.9 | 38.7 | 6.45 | 0 | 116.1 | 19.35 | 7.8993 | 1.976 | 0 | 476.9 | 476.9 | 329.3929 | 926.5931 | 8975.0429 | 8957.1143 | 10360.6074 | 0 | 41.2773 | 10360.6074 | 926.5931 | 476.9 | 1338.7604 | 7618.3539
| and 100% load scenario tabs. The bin-group calculation method was | AD | 61 | 308 | 49.6315 | 39.36 | 44.69% | 0.0053243 | 20.42 | 557.1019 | 60.3 | 108.4983 | 144.6643 | 19.9225 | 24.66% | 77.9263 | 77.5263 | 0.006946 | 0.013892 | 26.1505 | 33.4369 | Heat-Hum | 3.1012 | 0.35916 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.9263 | 19.9225 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 61 | 73.1 | 49.6315 | 4" MERV 8 | 4" MERV 8 | 24.66% | -4 | 168.5455 | 65.3173 | 52.8267 | 19.7757 | 48.5515 | 19.7757 | 4.2752 | 0 | 29449.3135 | 11411.1437 | 2.9632 | 1.874 | 21.4524 | 5.2577 | 29267.357 | 2707.0038 | 1.3881 | 0.016861 | 12.7831 | 0.014362 | 32.9091 | 6.7714 | 5.644 | 10.2738 | 1.1953 | 1.0256 | 145.8 | 20.4 | 72.9 | 10.2 | 0 | 218.7 | 30.6 | 9.8262 | 1.3147 | 0 | 0 | 0 | 605.7333 | 0 | 0 | 0.98333 | 168.5455 | 65.5714 | 52.7818 | 19.8483 | 48.4834 | 19.8483 | 4.2984 | 0 | 29339.2726 | 11412.73 | 2.947 | 1.8742 | 21.2555 | 5.259 | 29156.0382 | 2719.5281 | 1.3788 | 0.01701 | 12.6498 | 0.014556 | 32.6364 | 6.7571 | 5.6868 | 10.3234 | 1.1936 | 1.0255 | 145.4 | 20.5 | 72.7 | 10.25 | 0 | 218.1 | 30.75 | 9.7961 | 1.3195 | 0 | 10406 | 85.2261 | 64.2261 | 1259.52 | 111.24 | 65 | 64.2261 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 61 | 73.1 | 49.6315 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8323 | 10.6961 | 16.2514 | 10.6961 | 17.5809 | 0 | 18044.9953 | 5948.1528 | 2.1698 | 0.75594 | 9.6251 | 1.1069 | 18611.7148 | 3321.3084 | 0.79749 | 0.029936 | 4.6704 | 0.031286 | 22.3 | 1.9 | 5.3337 | 20.1808 | 1.2005 | 1.0168 | 77.4 | 12.4 | 38.7 | 6.2 | 0 | 116.1 | 18.6 | 7.8993 | 1.9021 | 0 | 605.7333 | 605.7333 | 416.1029 | 1205.7134 | 11013.2 | 10991.2 | 12802.6468 | -1.5916e-12 | 41.567 | 12802.6468 | 1205.7134 | 605.7333 | 1642.7817 | 9348.4183
| attractive to me because it required only 49 iterations of inputs & outputs per | AE | 59 | 266 | 47.9132 | 37.22 | 44.14% | 0.0048929 | 19.47 | 476.6259 | 59.7 | 93.524 | 124.6986 | 19.9309 | 24.67% | 77.5826 | 77.1826 | 0.006946 | 0.013892 | 26.0673 | 33.3537 | Heat-Hum | 3.5703 | 0.4547 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.5826 | 19.9309 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 59 | 73.1 | 47.9132 | 4" MERV 8 | 4" MERV 8 | 24.67% | -4 | 168.5455 | 65.345 | 52.8218 | 19.7833 | 48.5441 | 19.7833 | 4.2778 | 0 | 29437.3002 | 11404.2822 | 2.9615 | 1.8736 | 21.4309 | 5.2566 | 29255.2051 | 2638.2357 | 1.387 | 0.016014 | 12.7685 | 0.013294 | 32.8818 | 6.7571 | 5.6486 | 10.2863 | 1.1951 | 1.0255 | 145.8 | 20.1 | 72.9 | 10.05 | 0 | 218.7 | 30.15 | 9.823 | 1.295 | 0 | 0 | 215.9033 | 532 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7818 | 19.848 | 48.4834 | 19.848 | 4.2984 | 0 | 29339.2726 | 11405.6959 | 2.947 | 1.8738 | 21.2555 | 5.2577 | 29156.0382 | 2648.9771 | 1.3788 | 0.01614 | 12.6498 | 0.013453 | 32.6364 | 6.7571 | 5.6868 | 10.3305 | 1.1936 | 1.0255 | 145.4 | 20.2 | 72.7 | 10.1 | 0 | 218.1 | 30.3 | 9.7961 | 1.2993 | 0 | 8987 | 81.6176 | 60.6176 | 1259.52 | 111.24 | 65 | 60.6176 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 59 | 73.1 | 47.9132 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8323 | 10.6952 | 16.2514 | 10.6952 | 17.5809 | 0 | 18044.9953 | 5908.7619 | 2.1698 | 0.75328 | 9.6251 | 1.103 | 18611.7148 | 4023.6018 | 0.79749 | 0.0434 | 4.6704 | 0.054948 | 22.3 | 1.9 | 5.3337 | 20.0589 | 1.2005 | 1.0169 | 77.4 | 12.8 | 38.7 | 6.4 | 0 | 116.1 | 19.2 | 7.8993 | 1.9668 | 0 | 532 | 532 | 380.9893 | 1166.0759 | 9492.4 | 9492.4 | 11190.4759 | 1.819e-12 | 42.0695 | 11190.4759 | 1166.0759 | 532 | 1418.766 | 8073.634
| zone per scenario for the manufacturer's tool, as opposed to 8760 iterations | AF | 57 | 282 | 46.766 | 36.61 | 46.29% | 0.0047757 | 18.85 | 510.784 | 59 | 101.1002 | 134.8003 | 19.9227 | 24.66% | 77.3532 | 76.9532 | 0.006946 | 0.013892 | 26.0118 | 33.2982 | Heat-Hum | 3.8758 | 0.48065 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.3532 | 19.9227 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 57 | 73.1 | 46.766 | 4" MERV 8 | 4" MERV 8 | 24.66% | -4 | 168.5455 | 65.318 | 52.8266 | 19.7754 | 48.5513 | 19.7754 | 4.2753 | 0 | 29449.0047 | 11399.418 | 2.9632 | 1.8733 | 21.4519 | 5.2556 | 29267.0365 | 2597.8637 | 1.388 | 0.015493 | 12.7827 | 0.012665 | 32.9091 | 6.7571 | 5.6441 | 10.2856 | 1.1952 | 1.0255 | 145.8 | 19.7 | 72.9 | 9.85 | 0 | 218.7 | 29.55 | 9.8261 | 1.2693 | 0 | 0 | 686.67 | 564 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7818 | 19.8478 | 48.4834 | 19.8478 | 4.2984 | 0 | 29339.2726 | 11400.9998 | 2.947 | 1.8735 | 21.2555 | 5.2569 | 29156.0382 | 2609.5919 | 1.3788 | 0.015628 | 12.6498 | 0.012833 | 32.6364 | 6.7571 | 5.6868 | 10.3351 | 1.1936 | 1.0255 | 145.4 | 19.8 | 72.7 | 9.9 | 0 | 218.1 | 29.7 | 9.7961 | 1.2739 | 0 | 9527.5714 | 79.2085 | 58.2085 | 1259.52 | 111.24 | 65 | 58.2085 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 57 | 73.1 | 46.766 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8323 | 10.6946 | 16.2514 | 10.6946 | 17.5809 | 0 | 18044.9953 | 5882.4637 | 2.1698 | 0.75151 | 9.6251 | 1.1004 | 18611.7148 | 4615.9268 | 0.79749 | 0.056294 | 4.6704 | 0.081766 | 22.3 | 1.9 | 5.3337 | 19.8768 | 1.2005 | 1.017 | 77.4 | 12.9 | 38.7 | 6.45 | 0 | 116.1 | 19.35 | 7.8993 | 1.9735 | 0 | 564 | 564 | 418.8369 | 1322.3577 | 10063.3714 | 10063.3714 | 11949.7292 | 0 | 42.3749 | 11949.7292 | 1322.3577 | 564 | 1504.1053 | 8559.2661
| per zone per scenario... even though that is possible. I did use the full 8760 | AG | 55 | 284 | 45.3053 | 35.21 | 47.08% | 0.0045143 | 18.09 | 521.0732 | 58.4 | 103.9008 | 138.5343 | 19.9177 | 24.66% | 77.0611 | 76.6611 | 0.006946 | 0.013892 | 25.9411 | 33.2275 | Heat-Hum | 4.2488 | 0.53855 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.0611 | 19.9177 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 55 | 73.1 | 45.3053 | 4" MERV 8 | 4" MERV 8 | 24.66% | -4 | 168.5455 | 65.3016 | 52.8461 | 19.7714 | 48.5682 | 19.7714 | 4.2779 | 0 | 29456.1747 | 11393.3357 | 2.9742 | 1.8744 | 21.5372 | 5.2586 | 29274.5065 | 2549.9821 | 1.3886 | 0.014901 | 12.7915 | 0.011956 | 32.9909 | 6.7571 | 5.6323 | 10.2832 | 1.1957 | 1.0255 | 145.9 | 19.4 | 72.95 | 9.7 | 0 | 218.85 | 29.1 | 9.8289 | 1.2474 | 0 | 0 | 1152.5667 | 568 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7818 | 19.8476 | 48.4834 | 19.8476 | 4.2984 | 0 | 29339.2726 | 11395.0205 | 2.947 | 1.8731 | 21.2555 | 5.2558 | 29156.0382 | 2561.9639 | 1.3788 | 0.015038 | 12.6498 | 0.012123 | 32.6364 | 6.7429 | 5.6868 | 10.3409 | 1.1936 | 1.0255 | 145.4 | 19.5 | 72.7 | 9.75 | 0 | 218.1 | 29.25 | 9.7961 | 1.2522 | 0 | 9574.8571 | 76.1411 | 55.1411 | 1259.52 | 111.24 | 65 | 55.1411 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 55 | 73.1 | 45.3053 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8323 | 10.6939 | 16.2514 | 10.6939 | 17.5809 | 0 | 18044.9953 | 5848.9794 | 2.1698 | 0.74945 | 9.6251 | 1.0974 | 18611.7148 | 5574.5853 | 0.79749 | 0.080378 | 4.6704 | 0.14099 | 22.3 | 1.9 | 5.3337 | 19.4254 | 1.2005 | 1.0174 | 77.4 | 13.3 | 38.7 | 6.65 | 0 | 116.1 | 19.95 | 7.8993 | 2.0396 | 0 | 584.5667 | 584.5667 | 440.1694 | 1437.6734 | 10134.7429 | 10114.4571 | 12136.6972 | 0 | 42.7348 | 12136.6972 | 1437.6734 | 584.5667 | 1514.7727 | 8599.6844
| annual hour calculation method to synchronize the data center operation with | AH | 53 | 273 | 44.43 | 35.38 | 51% | 0.0045457 | 17.64 | 542.4212 | 57.7 | 109.0853 | 145.4471 | 19.9103 | 24.65% | 76.886 | 76.486 | 0.0066891 | 0.013378 | 25.6292 | 32.6461 | Heat-Hum | 4.3235 | 0.47468 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.886 | 19.9103 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 53 | 73.1 | 44.43 | 4" MERV 8 | 4" MERV 8 | 24.65% | -4 | 168.5455 | 65.2774 | 52.8511 | 19.7645 | 48.5752 | 19.7645 | 4.2759 | 0 | 29468.4889 | 11390.2986 | 2.9761 | 1.8741 | 21.5593 | 5.2583 | 29298.735 | 2526.9008 | 1.3906 | 0.014581 | 12.8207 | 0.011594 | 33.0364 | 6.7571 | 5.6254 | 10.2811 | 1.196 | 1.0255 | 146 | 19 | 73 | 9.5 | 0 | 219 | 28.5 | 9.8349 | 1.2199 | 0 | 0 | 1551.095 | 546 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7826 | 19.8475 | 48.484 | 19.8475 | 4.2986 | 0 | 29341.0671 | 11392.1343 | 2.9473 | 1.8729 | 21.2587 | 5.2556 | 29169.5822 | 2539.757 | 1.3799 | 0.014726 | 12.6659 | 0.011769 | 32.6545 | 6.7429 | 5.6839 | 10.3435 | 1.1937 | 1.0255 | 145.4 | 19 | 72.7 | 9.5 | 0 | 218.1 | 28.5 | 9.7993 | 1.225 | 0 | 9204 | 74.3031 | 53.3031 | 1259.52 | 111.24 | 65 | 53.3031 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 53 | 73.1 | 44.43 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8326 | 10.6938 | 16.2516 | 10.6938 | 17.581 | 0 | 18046.099 | 5839.7321 | 2.1699 | 0.74892 | 9.6264 | 1.0967 | 18620.2184 | 5642.7552 | 0.79809 | 0.081985 | 4.6761 | 0.14557 | 22.3 | 1.9 | 5.3323 | 19.4054 | 1.2005 | 1.0174 | 77.4 | 12.6 | 38.7 | 6.3 | 0 | 116.1 | 18.9 | 7.9022 | 1.9248 | 0 | 1005.095 | 1005.095 | 426.6572 | 1402.3927 | 9742.2 | 9722.7 | 12130.1877 | 0 | 44.4329 | 12130.1877 | 1402.3927 | 1005.095 | 1455.7137 | 8266.9863
| the cafeteria heat recovery input, and to create chronological tallies of water | AI | 51 | 156 | 42.7795 | 33.57 | 51.07% | 0.0042271 | 16.81 | 573.3808 | 57 | 116.2923 | 155.0564 | 19.9006 | 24.63% | 76.5559 | 76.1559 | 0.0066891 | 0.013378 | 25.5493 | 32.5661 | Heat-Hum | 4.7294 | 0.54524 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.5559 | 19.9006 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 51 | 73.1 | 42.7795 | 4" MERV 8 | 4" MERV 8 | 24.63% | -4 | 168.5455 | 65.2457 | 52.8568 | 19.7551 | 48.5838 | 19.7551 | 4.273 | 0 | 29482.3031 | 11383.3436 | 2.9781 | 1.8737 | 21.5842 | 5.2569 | 29312.7235 | 2479.5859 | 1.3918 | 0.014013 | 12.8375 | 0.010933 | 33.0636 | 6.7571 | 5.6201 | 10.2812 | 1.1962 | 1.0255 | 146 | 18.7 | 73 | 9.35 | 0 | 219 | 28.05 | 9.8387 | 1.2004 | 0 | 0 | 1139.58 | 312 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7826 | 19.8472 | 48.484 | 19.8472 | 4.2986 | 0 | 29341.0671 | 11385.3773 | 2.9473 | 1.8725 | 21.2587 | 5.2544 | 29169.5822 | 2493.4266 | 1.3799 | 0.014167 | 12.6659 | 0.011115 | 32.6545 | 6.7429 | 5.6839 | 10.3498 | 1.1937 | 1.0255 | 145.4 | 18.8 | 72.7 | 9.4 | 0 | 218.1 | 28.2 | 9.7993 | 1.206 | 0 | 5259.4286 | 70.8369 | 49.8369 | 1259.52 | 111.24 | 65 | 49.8369 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 51 | 73.1 | 42.7795 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8326 | 10.6934 | 16.2516 | 10.6934 | 17.581 | 0 | 18046.099 | 5824.3646 | 2.1699 | 0.7479 | 9.6264 | 1.0952 | 18620.2184 | 5623.3171 | 0.79809 | 0.081339 | 4.6761 | 0.14393 | 22.3 | 1.9 | 5.3323 | 19.4555 | 1.2005 | 1.0174 | 77.4 | 12.2 | 38.7 | 6.1 | 0 | 116.1 | 18.3 | 7.9022 | 1.8667 | 0 | 827.58 | 827.58 | 254.7801 | 864.6916 | 5566.9714 | 5555.8286 | 7248.1002 | 0 | 46.4622 | 7248.1002 | 864.6916 | 827.58 | 831.8364 | 4723.9922
| & potential fuel oil use, in order to calculate the tank sizes you see at top of | AJ | 49 | 258 | 41.8876 | 33.83 | 55.6% | 0.0042714 | 16.37 | 558.731 | 56.4 | 114.1402 | 152.187 | 19.8985 | 24.63% | 76.3775 | 75.9775 | 0.0066891 | 0.013378 | 25.5061 | 32.523 | Heat-Hum | 4.9442 | 0.53543 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.3775 | 19.8985 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 49 | 73.1 | 41.8876 | 4" MERV 8 | 4" MERV 8 | 24.63% | -4 | 168.5455 | 65.2387 | 52.858 | 19.753 | 48.5857 | 19.753 | 4.2723 | 0 | 29485.363 | 11379.6485 | 2.9785 | 1.8734 | 21.5897 | 5.2562 | 29315.8108 | 2459.3455 | 1.3921 | 0.013733 | 12.8412 | 0.010628 | 33.0727 | 6.7571 | 5.6189 | 10.2831 | 1.1962 | 1.0255 | 146 | 18.3 | 73 | 9.15 | 0 | 219 | 27.45 | 9.8395 | 1.1741 | 0 | 0 | 2303.51 | 516 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7826 | 19.8471 | 48.484 | 19.8471 | 4.2986 | 0 | 29341.0671 | 11381.7261 | 2.9473 | 1.8722 | 21.2587 | 5.2537 | 29169.5822 | 2473.2748 | 1.3799 | 0.013887 | 12.6659 | 0.010807 | 32.6545 | 6.7429 | 5.6839 | 10.3532 | 1.1937 | 1.0254 | 145.4 | 18.3 | 72.7 | 9.15 | 0 | 218.1 | 27.45 | 9.7993 | 1.1797 | 0 | 8698.2857 | 68.964 | 47.964 | 1259.52 | 111.24 | 65 | 47.964 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 49 | 73.1 | 41.8876 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8326 | 10.6932 | 16.2516 | 10.6932 | 17.581 | 0 | 18046.099 | 5816.0382 | 2.1699 | 0.74735 | 9.6264 | 1.0944 | 18620.2184 | 5612.9644 | 0.79809 | 0.080809 | 4.6761 | 0.14272 | 22.3 | 1.9 | 5.3323 | 19.4853 | 1.2005 | 1.0173 | 77.4 | 11.4 | 38.7 | 5.7 | 0 | 116.1 | 17.1 | 7.9022 | 1.7424 | 0 | 1787.51 | 1787.51 | 430.9703 | 1485.4715 | 9206.9143 | 9188.4857 | 12461.4673 | 0 | 48.3003 | 12461.4673 | 1485.4715 | 1787.51 | 1375.7294 | 7812.7563
| the Summary tab. | AK | 47 | 418 | 40.4057 | 32.57 | 56.99% | 0.00406 | 15.66 | 542.1364 | 55.7 | 111.6775 | 148.9034 | 19.8965 | 24.63% | 76.0811 | 75.6811 | 0.0066891 | 0.013378 | 25.4344 | 32.4512 | Heat-Hum | 5.2896 | 0.58225 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.0811 | 19.8965 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 47 | 73.1 | 40.4057 | 4" MERV 8 | 4" MERV 8 | 24.63% | -4 | 168.5455 | 65.232 | 52.8592 | 19.7508 | 48.5875 | 19.7508 | 4.2717 | 0 | 29488.2725 | 11373.5404 | 2.979 | 1.873 | 21.595 | 5.255 | 29318.7563 | 2424.5564 | 1.3923 | 0.01331 | 12.8448 | 0.010154 | 33.0818 | 6.7571 | 5.6178 | 10.2873 | 1.1963 | 1.0255 | 146 | 17.9 | 73 | 8.95 | 0 | 219 | 26.85 | 9.8403 | 1.154 | 0 | 0 | 4410.5967 | 836 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7826 | 19.8468 | 48.484 | 19.8468 | 4.2986 | 0 | 29341.0671 | 11375.6597 | 2.9473 | 1.8718 | 21.2587 | 5.2526 | 29169.5822 | 2438.4299 | 1.3799 | 0.013461 | 12.6659 | 0.010328 | 32.6545 | 6.7429 | 5.6839 | 10.3587 | 1.1937 | 1.0254 | 145.4 | 18 | 72.7 | 9 | 0 | 218.1 | 27 | 9.7993 | 1.1595 | 0 | 14092.5714 | 65.8521 | 44.8521 | 1259.52 | 111.24 | 65 | 44.8521 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 47 | 73.1 | 40.4057 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8326 | 10.6929 | 16.2516 | 10.6929 | 17.581 | 0 | 18046.099 | 5802.328 | 2.1699 | 0.74644 | 9.6264 | 1.0931 | 18620.2184 | 5595.836 | 0.79809 | 0.0802 | 4.6761 | 0.14122 | 22.3 | 1.9 | 5.3323 | 19.5306 | 1.2005 | 1.0173 | 77.4 | 10.9 | 38.7 | 5.45 | 0 | 116.1 | 16.35 | 7.9022 | 1.6692 | 0 | 3574.5967 | 3574.5967 | 723.264 | 2551.0735 | 14916.6286 | 14886.7714 | 21012.4416 | 0 | 50.269 | 21012.4416 | 2551.0735 | 3574.5967 | 2228.895 | 12657.8764
|  | AL | 45 | 287 | 39.3812 | 32.57 | 61.48% | 0.00406 | 15.18 | 549.785 | 55.1 | 114.0592 | 152.0789 | 19.8896 | 24.62% | 75.8762 | 75.4762 | 0.006485 | 0.01297 | 25.1706 | 31.9734 | Heat-Hum | 5.4066 | 0.53705 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.8762 | 19.8896 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 45 | 73.1 | 39.3812 | 4" MERV 8 | 4" MERV 8 | 24.62% | -4 | 168.5455 | 65.2093 | 52.8639 | 19.7443 | 48.5941 | 19.7443 | 4.2698 | 0 | 29499.7212 | 11369.8109 | 2.9807 | 1.8728 | 21.6156 | 5.2545 | 29340.6149 | 2404.0437 | 1.3941 | 0.013035 | 12.8712 | 0.0098604 | 33.1273 | 6.7429 | 5.6115 | 10.286 | 1.1965 | 1.0255 | 146.1 | 17.6 | 73.05 | 8.8 | 0 | 219.15 | 26.4 | 9.8457 | 1.1292 | 0 | 0 | 3494.225 | 574 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7832 | 19.8467 | 48.4845 | 19.8467 | 4.2987 | 0 | 29342.6315 | 11372.0717 | 2.9475 | 1.8716 | 21.2615 | 5.2522 | 29181.3729 | 2418.6277 | 1.3809 | 0.013192 | 12.68 | 0.01004 | 32.6636 | 6.7286 | 5.6814 | 10.3618 | 1.1938 | 1.0254 | 145.5 | 17.6 | 72.75 | 8.8 | 0 | 218.25 | 26.4 | 9.802 | 1.135 | 0 | 9655.5 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 45 | 73.1 | 39.3812 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8329 | 10.6939 | 16.2518 | 10.6939 | 17.5811 | 0 | 18047.0612 | 5848.1086 | 2.1701 | 0.7492 | 9.6276 | 1.0972 | 18627.6318 | 3567.9021 | 0.79861 | 0.033749 | 4.681 | 0.03789 | 22.3 | 1.8 | 5.331 | 20.373 | 1.2006 | 1.0166 | 77.4 | 9.4 | 38.7 | 4.7 | 0 | 116.1 | 14.1 | 7.9049 | 1.4445 | 0 | 2920.225 | 2920.225 | 502.4171 | 1785.1637 | 10192.6 | 10172.1 | 14877.4887 | 0 | 51.8379 | 14877.4887 | 1785.1637 | 2920.225 | 1530.0098 | 8642.0902
3. | At least one manufacturer of IDEC cooling equipment maintains a | AM | 43 | 392 | 37.6204 | 30.82 | 61.46% | 0.0037586 | 14.37 | 542.2015 | 54.4 | 113.4134 | 151.2178 | 19.8851 | 24.62% | 75.5241 | 75.1241 | 0.006485 | 0.01297 | 25.0854 | 31.8881 | Heat-Hum | 5.7988 | 0.6038 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.5241 | 19.8851 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 43 | 73.1 | 37.6204 | 4" MERV 8 | 4" MERV 8 | 24.62% | -4 | 168.5455 | 65.1946 | 52.8666 | 19.7398 | 48.5981 | 19.7398 | 4.2685 | 0 | 29506.1337 | 11362.5105 | 2.9816 | 1.8723 | 21.6272 | 5.2532 | 29347.1077 | 2367.8039 | 1.3947 | 0.012609 | 12.879 | 0.0093947 | 33.1364 | 6.7429 | 5.6091 | 10.2895 | 1.1966 | 1.0255 | 146.2 | 17.3 | 73.1 | 8.65 | 0 | 219.3 | 25.95 | 9.8475 | 1.112 | 0 | 0 | 5408.9467 | 784 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7832 | 19.8464 | 48.4845 | 19.8464 | 4.2987 | 0 | 29342.6315 | 11364.863 | 2.9475 | 1.8711 | 21.2615 | 5.2509 | 29181.3729 | 2382.5973 | 1.3809 | 0.012767 | 12.68 | 0.0095715 | 32.6636 | 6.7286 | 5.6814 | 10.3683 | 1.1938 | 1.0254 | 145.5 | 17.4 | 72.75 | 8.7 | 0 | 218.25 | 26.1 | 9.802 | 1.1179 | 0 | 13188 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 43 | 73.1 | 37.6204 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8329 | 10.6939 | 16.2518 | 10.6939 | 17.5811 | 0 | 18047.0612 | 5848.1086 | 2.1701 | 0.7492 | 9.6276 | 1.0972 | 18627.6318 | 3219.0337 | 0.79861 | 0.027499 | 4.681 | 0.027854 | 22.3 | 1.8 | 5.331 | 20.4698 | 1.2006 | 1.0165 | 77.4 | 9.1 | 38.7 | 4.55 | 0 | 116.1 | 13.65 | 7.9049 | 1.393 | 0 | 4624.9467 | 4624.9467 | 712.8774 | 2592.0203 | 13921.6 | 13893.6 | 21110.567 | 0 | 53.8535 | 21110.567 | 2592.0203 | 4624.9467 | 2089.7695 | 11803.8305
| spreadsheet-based performance tool. That expert tool is what I used to | AN | 41 | 329 | 36.0012 | 29.5 | 62.46% | 0.0035343 | 13.64 | 482.6416 | 53.7 | 101.7807 | 135.7076 | 19.8918 | 24.62% | 75.2002 | 74.8002 | 0.006485 | 0.01297 | 25.007 | 31.8097 | Heat-Hum | 6.1515 | 0.65347 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.2002 | 19.8918 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 41 | 73.1 | 36.0012 | 4" MERV 8 | 4" MERV 8 | 24.62% | -4 | 168.5455 | 65.2168 | 52.8626 | 19.7458 | 48.5921 | 19.7458 | 4.2705 | 0 | 29496.4688 | 11356.0198 | 2.9802 | 1.8719 | 21.6097 | 5.2521 | 29337.3234 | 2339.4822 | 1.3939 | 0.012269 | 12.8672 | 0.0090319 | 33.1182 | 6.7429 | 5.6128 | 10.2996 | 1.1965 | 1.0255 | 146.1 | 17 | 73.05 | 8.5 | 0 | 219.15 | 25.5 | 9.8449 | 1.0939 | 0 | 0 | 5073.7283 | 658 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7832 | 19.8462 | 48.4845 | 19.8462 | 4.2987 | 0 | 29342.6315 | 11358.234 | 2.9475 | 1.8707 | 21.2615 | 5.2497 | 29181.3729 | 2353.0939 | 1.3809 | 0.012412 | 12.68 | 0.0091905 | 32.6636 | 6.7286 | 5.6814 | 10.3742 | 1.1938 | 1.0254 | 145.5 | 17.1 | 72.75 | 8.55 | 0 | 218.25 | 25.65 | 9.802 | 1.0994 | 0 | 11068.5 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 41 | 73.1 | 36.0012 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8329 | 10.6939 | 16.2518 | 10.6939 | 17.5811 | 0 | 18047.0612 | 5848.1086 | 2.1701 | 0.7492 | 9.6276 | 1.0972 | 18627.6318 | 2958.735 | 0.79861 | 0.02316 | 4.681 | 0.021562 | 22.3 | 1.8 | 5.331 | 20.531 | 1.2006 | 1.0165 | 77.4 | 8.8 | 38.7 | 4.4 | 0 | 116.1 | 13.2 | 7.9049 | 1.3437 | 0 | 4415.7283 | 4415.7283 | 618.4167 | 2291.4609 | 11684.2 | 11660.7 | 18367.8893 | 0 | 55.8295 | 18367.8893 | 2291.4609 | 4415.7283 | 1753.9137 | 9906.7863
| transform each unique bin's "Input" row of data to the horizontally-adjacent | AO | 39 | 281 | 34.1466 | 27.62 | 61.86% | 0.0032371 | 12.84 | 548.5804 | 53.1 | 116.4903 | 155.3204 | 19.8699 | 24.6% | 74.8293 | 74.4293 | 0.0062436 | 0.012487 | 24.664 | 31.2135 | Heat-Hum | 6.3988 | 0.66582 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.8293 | 19.8699 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 39 | 73.1 | 34.1466 | 4" MERV 8 | 4" MERV 8 | 24.6% | -4 | 168.5455 | 65.1447 | 52.8763 | 19.725 | 48.6122 | 19.725 | 4.2641 | 0 | 29529.7964 | 11348.6922 | 2.9851 | 1.8714 | 21.6699 | 5.2508 | 29383.2243 | 2307.2931 | 1.3977 | 0.011895 | 12.9227 | 0.008636 | 33.2091 | 6.7429 | 5.5978 | 10.2913 | 1.1971 | 1.0254 | 146.3 | 16.7 | 73.15 | 8.35 | 0 | 219.45 | 25.05 | 9.8568 | 1.0766 | 0 | 0 | 4789.645 | 562 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.784 | 19.846 | 48.485 | 19.846 | 4.2989 | 0 | 29344.4804 | 11351.3565 | 2.9478 | 1.8703 | 21.2648 | 5.2488 | 29195.3278 | 2323.3123 | 1.3821 | 0.012062 | 12.6967 | 0.0088178 | 32.6818 | 6.7286 | 5.6785 | 10.3801 | 1.1939 | 1.0254 | 145.5 | 16.8 | 72.75 | 8.4 | 0 | 218.25 | 25.2 | 9.8053 | 1.0831 | 0 | 9453.6429 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 39 | 73.1 | 34.1466 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8332 | 10.6939 | 16.252 | 10.6939 | 17.5812 | 0 | 18048.1984 | 5848.4771 | 2.1703 | 0.74922 | 9.629 | 1.0973 | 18636.3949 | 2715.1028 | 0.79923 | 0.019371 | 4.6869 | 0.016549 | 22.3 | 1.8 | 5.3296 | 20.5784 | 1.2006 | 1.0164 | 77.5 | 8.5 | 38.75 | 4.25 | 0 | 116.25 | 12.75 | 7.908 | 1.3085 | 0 | 4227.645 | 4227.645 | 540.2377 | 2026.6415 | 9979.5143 | 9959.4429 | 16213.7294 | 0 | 57.7001 | 16213.7294 | 2026.6415 | 4227.645 | 1497.6117 | 8461.8312
| "output" line of data that you see here. They are recorded like a series of | AP | 37 | 392 | 33.0765 | 27.79 | 67.47% | 0.0032643 | 12.39 | 518.1742 | 52.4 | 110.92 | 147.8933 | 19.8694 | 24.6% | 74.6153 | 74.2153 | 0.0062436 | 0.012487 | 24.6122 | 31.1617 | Heat-Hum | 6.6143 | 0.65981 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.6153 | 19.8694 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 37 | 73.1 | 33.0765 | 4" MERV 8 | 4" MERV 8 | 24.6% | -4 | 168.5455 | 65.1432 | 52.8766 | 19.7244 | 48.6126 | 19.7244 | 4.2639 | 0 | 29530.4775 | 11344.3012 | 2.9852 | 1.8711 | 21.6711 | 5.25 | 29383.9144 | 5615.4071 | 1.3977 | 0.050697 | 12.9235 | 0.08958 | 33.2182 | 4.4714 | 5.5975 | 15.5108 | 1.1971 | 1.0169 | 146.3 | 0 | 73.15 | 0 | 0 | 219.45 | 0 | 9.857 | 0 | 0 | 0 | 7317.9867 | 784 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.784 | 19.8458 | 48.485 | 19.8458 | 4.2989 | 0 | 29344.4804 | 11346.9753 | 2.9478 | 1.87 | 21.2648 | 5.248 | 29195.3278 | 5642.1086 | 1.3821 | 0.051174 | 12.6967 | 0.090853 | 32.6818 | 4.4714 | 5.6785 | 15.608 | 1.1939 | 1.0169 | 145.5 | 0 | 72.75 | 0 | 0 | 218.25 | 0 | 9.8053 | 0 | 0 | 8764 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 37 | 73.1 | 33.0765 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8332 | 10.6942 | 16.252 | 10.6942 | 17.5812 | 0 | 18048.1984 | 5851.9469 | 2.1703 | 0.75012 | 9.629 | 1.0986 | 18636.3949 | 5632.8457 | 0.79923 | 0.070551 | 4.6869 | 0.12505 | 22.3 | 1 | 5.3296 | 36.9605 | 1.2006 | 1.0091 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.908 | 0 | 0 | 6533.9867 | 6533.9867 | 768.2826 | 2911.6728 | 9156 | 9156 | 18601.6595 | 0 | 47.4532 | 18601.6595 | 2911.6728 | 6533.9867 | 2089.1949 | 7066.8051
| snapshots, and there are several scenes occurring in each bin. | AQ | 35 | 453 | 31.6302 | 27 | 70.36% | 0.0031443 | 11.77 | 554.021 | 51.8 | 119.4056 | 159.2074 | 19.8513 | 24.57% | 74.326 | 73.926 | 0.0062436 | 0.012487 | 24.5422 | 31.0917 | Heat-Hum | 6.9119 | 0.68639 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.326 | 19.8513 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 35 | 73.1 | 31.6302 | 4" MERV 8 | 4" MERV 8 | 24.57% | -4 | 168.5455 | 65.0841 | 52.8872 | 19.7073 | 48.6287 | 19.7073 | 4.2585 | 0 | 29556.3403 | 11338.0107 | 2.989 | 1.8707 | 21.7179 | 5.2486 | 29410.1081 | 5385.4723 | 1.3999 | 0.046852 | 12.9552 | 0.079396 | 33.2818 | 4.4571 | 5.5876 | 15.5401 | 1.1974 | 1.0168 | 146.4 | 0 | 73.2 | 0 | 0 | 219.6 | 0 | 9.864 | 0 | 0 | 0 | 9192.125 | 906 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.784 | 19.8455 | 48.485 | 19.8455 | 4.2989 | 0 | 29344.4804 | 11341.0538 | 2.9478 | 1.8696 | 21.2648 | 5.247 | 29195.3278 | 5414.5284 | 1.3821 | 0.047351 | 12.6967 | 0.080675 | 32.6818 | 4.4571 | 5.6785 | 15.65 | 1.1939 | 1.0168 | 145.5 | 0 | 72.75 | 0 | 0 | 218.25 | 0 | 9.8053 | 0 | 0 | 10095.4286 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 35 | 73.1 | 31.6302 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8332 | 10.6939 | 16.252 | 10.6939 | 17.5812 | 0 | 18048.1984 | 5848.4771 | 2.1703 | 0.74922 | 9.629 | 1.0973 | 18636.3949 | 5295.0177 | 0.79923 | 0.062556 | 4.6869 | 0.10423 | 22.3 | 1 | 5.3296 | 37.691 | 1.2006 | 1.009 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.908 | 0 | 0 | 8286.125 | 8286.125 | 911.2063 | 3499.5918 | 10548.4286 | 10548.4286 | 22334.1454 | 0 | 49.3027 | 22334.1454 | 3499.5918 | 8286.125 | 2414.2992 | 8134.1293
|  | AR | 33 | 264 | 30.7235 | 27.56 | 78.25% | 0.0032286 | 11.38 | 482.4932 | 51.1 | 104.8148 | 139.7531 | 19.8616 | 24.59% | 74.1447 | 73.7447 | 0.0062436 | 0.012487 | 24.4983 | 31.0478 | Heat-Hum | 7.0992 | 0.66772 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.1447 | 19.8616 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 33 | 73.1 | 30.7235 | 4" MERV 8 | 4" MERV 8 | 24.59% | -4 | 168.5455 | 65.1177 | 52.8812 | 19.7167 | 48.6196 | 19.7167 | 4.2616 | 0 | 29541.6213 | 11334.5081 | 2.9869 | 1.8705 | 21.6913 | 5.2481 | 29395.2009 | 5172.9123 | 1.3987 | 0.043421 | 12.9372 | 0.070678 | 33.2455 | 4.4429 | 5.5933 | 15.5805 | 1.1972 | 1.0168 | 146.3 | 0 | 73.15 | 0 | 0 | 219.45 | 0 | 9.86 | 0 | 0 | 0 | 5785.56 | 528 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.784 | 19.8454 | 48.485 | 19.8454 | 4.2989 | 0 | 29344.4804 | 11337.3413 | 2.9478 | 1.8694 | 21.2648 | 5.2463 | 29195.3278 | 5198.7456 | 1.3821 | 0.043849 | 12.6967 | 0.07173 | 32.6818 | 4.4429 | 5.6785 | 15.6842 | 1.1939 | 1.0168 | 145.5 | 0 | 72.75 | 0 | 0 | 218.25 | 0 | 9.8053 | 0 | 0 | 5864.5714 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 33 | 73.1 | 30.7235 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8332 | 10.6939 | 16.252 | 10.6939 | 17.5812 | 0 | 18048.1984 | 5848.4771 | 2.1703 | 0.74922 | 9.629 | 1.0973 | 18636.3949 | 4853.4561 | 0.79923 | 0.052776 | 4.6869 | 0.0806 | 22.3 | 1 | 5.3296 | 38.484 | 1.2006 | 1.0088 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.908 | 0 | 0 | 5257.56 | 5257.56 | 539.6047 | 2088.944 | 6128.5714 | 6128.5714 | 13475.0755 | 0 | 51.042 | 13475.0755 | 2088.944 | 5257.56 | 1407.0088 | 4721.5626
4. | Knowing this, it should be possible to review my calculation (for any given | AS | 31 | 424 | 29.216 | 26.62 | 81.64% | 0.00309 | 10.75 | 511.1913 | 50.4 | 111.9235 | 149.2313 | 19.8427 | 24.56% | 73.8432 | 73.4432 | 0.0060517 | 0.012103 | 24.224 | 30.5723 | Heat-Hum | 7.2917 | 0.65592 | 0 | 0 | 42.1 | 1259.52 | 1854 | 78 | 73.8432 | 19.8427 | 42.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 31 | 73.1 | 29.216 | 4" MERV 8 | 4" MERV 8 | 24.56% | -4 | 168.5455 | 65.0557 | 52.893 | 19.6988 | 48.6369 | 19.6988 | 4.2561 | 0 | 29570.2603 | 11328.5134 | 2.9911 | 1.87 | 21.7431 | 5.247 | 29433.8317 | 4987.4173 | 1.4019 | 0.040516 | 12.984 | 0.063584 | 33.3273 | 4.4429 | 5.5806 | 15.5996 | 1.1977 | 1.0168 | 146.5 | 0 | 73.25 | 0 | 0 | 219.75 | 0 | 9.87 | 0 | 0 | 0 | 9980.2533 | 848 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7846 | 19.8452 | 48.4855 | 19.8452 | 4.2991 | 0 | 29345.9429 | 11331.7341 | 2.948 | 1.869 | 21.2674 | 5.2455 | 29206.3583 | 5015.6397 | 1.383 | 0.040967 | 12.7099 | 0.064655 | 32.7 | 4.4429 | 5.6761 | 15.7165 | 1.194 | 1.0168 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8078 | 0 | 0 | 9418.8571 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 42.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 31 | 73.1 | 29.216 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8335 | 10.6939 | 16.2522 | 10.6939 | 17.5812 | 0 | 18049.0979 | 5848.7686 | 2.1704 | 0.74924 | 9.6301 | 1.0974 | 18643.3231 | 4476.5785 | 0.79972 | 0.045022 | 4.6915 | 0.063419 | 22.3 | 1 | 5.3284 | 39.0792 | 1.2007 | 1.0086 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9104 | 0 | 0 | 9132.2533 | 9132.2533 | 880.7864 | 3436.5983 | 9842.8571 | 9842.8571 | 22411.7087 | 0 | 52.8578 | 22411.7087 | 3436.5983 | 9132.2533 | 2259.2498 | 7583.6073
| snapshot) using your own manufacturers' tool. Punch in my input shown for | AT | 29 | 342 | 26.8234 | 23.22 | 76.28% | 0.00263 | 9.78 | 448.1009 | 49.8 | 98.7671 | 131.6894 | 19.8516 | 24.57% | 73.3647 | 72.9647 | 0.0060517 | 0.012103 | 24.1082 | 30.4564 | Heat-Hum | 7.754 | 0.75779 | 0 | 0 | 42.1 | 1259.52 | 1854 | 78 | 73.3647 | 19.8516 | 42.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 29 | 73.1 | 26.8234 | 4" MERV 8 | 4" MERV 8 | 24.57% | -4 | 168.5455 | 65.0849 | 52.8877 | 19.7068 | 48.629 | 19.7068 | 4.2587 | 0 | 29557.4488 | 11318.8994 | 2.9892 | 1.8694 | 21.7199 | 5.2454 | 29420.8512 | 4834.1535 | 1.4008 | 0.038186 | 12.9683 | 0.058085 | 33.2909 | 4.4286 | 5.5855 | 15.6409 | 1.1975 | 1.0167 | 146.4 | 0 | 73.2 | 0 | 0 | 219.6 | 0 | 9.8665 | 0 | 0 | 0 | 8605.29 | 684 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7846 | 19.8448 | 48.4855 | 19.8448 | 4.2991 | 0 | 29345.9429 | 11321.9375 | 2.948 | 1.8684 | 21.2674 | 5.2438 | 29206.3583 | 4859.827 | 1.383 | 0.038584 | 12.7099 | 0.059003 | 32.7 | 4.4286 | 5.6761 | 15.7523 | 1.194 | 1.0167 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8078 | 0 | 0 | 7572.8571 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 42.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 29 | 73.1 | 26.8234 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8335 | 10.6939 | 16.2522 | 10.6939 | 17.5812 | 0 | 18049.0979 | 5848.7686 | 2.1704 | 0.74924 | 9.6301 | 1.0974 | 18643.3231 | 4148.3783 | 0.79972 | 0.038725 | 4.6915 | 0.050549 | 22.3 | 1 | 5.3284 | 39.5393 | 1.2007 | 1.0085 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9104 | 0 | 0 | 7921.29 | 7921.29 | 737.847 | 2930.0612 | 7914.8571 | 7914.8571 | 18766.2083 | 0 | 54.872 | 18766.2083 | 2930.0612 | 7921.29 | 1822.3195 | 6092.5377
| any line of input, you should get close to my output. | AU | 27 | 116 | 24.4672 | 19.74 | 70.89% | 0.0022257 | 8.86 | 422.0578 | 49.1 | 93.7488 | 124.9983 | 19.8487 | 24.57% | 72.8934 | 72.4934 | 0.0058452 | 0.01169 | 23.7775 | 29.9091 | Heat-Hum | 8.0729 | 0.8016 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72.8934 | 19.8487 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 27 | 73.1 | 24.4672 | 4" MERV 8 | 4" MERV 8 | 24.57% | -4 | 168.5455 | 65.0754 | 52.8901 | 19.7038 | 48.6321 | 19.7038 | 4.2581 | 0 | 29563.3453 | 11309.8588 | 2.9901 | 1.8688 | 21.7306 | 5.244 | 29438.1856 | 4693.0013 | 1.4023 | 0.036089 | 12.9893 | 0.053293 | 33.3182 | 4.4143 | 5.5812 | 15.6705 | 1.1977 | 1.0167 | 146.5 | 0 | 73.25 | 0 | 0 | 219.75 | 0 | 9.8706 | 0 | 0 | 0 | 3107.06 | 232 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8445 | 48.486 | 19.8445 | 4.2992 | 0 | 29347.6707 | 11312.9563 | 2.9483 | 1.8678 | 21.2705 | 5.2425 | 29219.3903 | 4718.3011 | 1.3841 | 0.03647 | 12.7255 | 0.054147 | 32.7091 | 4.4143 | 5.6734 | 15.7843 | 1.1941 | 1.0167 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 2560.2857 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 27 | 73.1 | 24.4672 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 3865.8635 | 0.8003 | 0.033634 | 4.6969 | 0.040914 | 22.3 | 0.9 | 5.327 | 39.8876 | 1.2007 | 1.0085 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 2875.06 | 2875.06 | 256.6762 | 1030.8171 | 2664.6857 | 2664.6857 | 6570.5628 | 0 | 56.6428 | 6570.5628 | 1030.8171 | 2875.06 | 617.9377 | 2046.748
|  | AV | 25 | 42 | 22.5357 | 17.51 | 69.9% | 0.0019971 | 8.13 | 501.3952 | 48.5 | 112.1066 | 149.4754 | 19.8046 | 24.52% | 72.5071 | 72.1071 | 0.0058452 | 0.01169 | 23.684 | 29.8156 | Heat-Hum | 8.4173 | 0.85222 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72.5071 | 19.8046 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 25 | 73.1 | 22.5357 | 4" MERV 8 | 4" MERV 8 | 24.52% | -4 | 168.5455 | 64.9308 | 52.9164 | 19.6622 | 48.6716 | 19.6622 | 4.2448 | 0 | 29626.8314 | 11301.0468 | 2.9995 | 1.8682 | 21.8457 | 5.2418 | 29502.5307 | 4549.8933 | 1.4076 | 0.034016 | 13.0677 | 0.048701 | 33.4818 | 4.4143 | 5.557 | 15.6688 | 1.1986 | 1.0167 | 146.8 | 0 | 73.4 | 0 | 0 | 220.2 | 0 | 9.888 | 0 | 0 | 0 | 1193.15 | 84 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8442 | 48.486 | 19.8442 | 4.2992 | 0 | 29347.6707 | 11305.0472 | 2.9483 | 1.8673 | 21.2705 | 5.241 | 29219.3903 | 4581.516 | 1.3841 | 0.034479 | 12.7255 | 0.049707 | 32.7091 | 4.4143 | 5.6734 | 15.8131 | 1.1941 | 1.0167 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 927 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 25 | 73.1 | 22.5357 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 3618.8692 | 0.8003 | 0.029443 | 4.6969 | 0.033527 | 22.3 | 0.9 | 5.327 | 40.1614 | 1.2007 | 1.0084 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 1109.15 | 1109.15 | 95.442 | 387.6936 | 964.8 | 964.8 | 2461.6436 | 0 | 58.6106 | 2461.6436 | 387.6936 | 1109.15 | 223.7361 | 741.0639
5. | I did use generic performance data (excel formulas) for the ventilation units. | AW | 23 | 25 | 19.956 | 12.66 | 60.54% | 0.0015729 | 7.2 | 443.7 | 47.8 | 99.9655 | 133.2873 | 19.8106 | 24.52% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 8.8542 | 0.94618 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8106 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 23 | 73.1 | 19.956 | 4" MERV 8 | 4" MERV 8 | 24.52% | -4 | 168.5455 | 64.9505 | 52.9128 | 19.6674 | 48.6662 | 19.6674 | 4.2466 | 0 | 29618.1622 | 11290.7869 | 2.9982 | 1.8676 | 21.83 | 5.2401 | 29493.7435 | 4433.1714 | 1.4069 | 0.032367 | 13.0569 | 0.04515 | 33.4545 | 4.4 | 5.5603 | 15.7035 | 1.1985 | 1.0166 | 146.7 | 0 | 73.35 | 0 | 0 | 220.05 | 0 | 9.8856 | 0 | 0 | 0 | 750.7917 | 50 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 4462.8775 | 1.3841 | 0.032791 | 12.7255 | 0.046049 | 32.7091 | 4.4 | 5.6734 | 15.8442 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 550 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 23 | 73.1 | 19.956 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 3401.4744 | 0.8003 | 0.02595 | 4.6969 | 0.027774 | 22.3 | 0.9 | 5.327 | 40.3773 | 1.2007 | 1.0084 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 700.7917 | 700.7917 | 58.7037 | 241.6913 | 572.5 | 572.5 | 1514.9829 | 0 | 60.5993 | 1514.9829 | 241.6913 | 700.7917 | 133.1762 | 439.3238
|  | AX | 21 | 23 | 18.4913 | 12.19 | 65.07% | 0.0015371 | 6.68 | 279.3 | 47.1 | 63.404 | 84.5386 | 19.8684 | 24.59% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 9.1356 | 0.95409 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8684 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 21 | 73.1 | 18.4913 | 4" MERV 8 | 4" MERV 8 | 24.59% | -4 | 168.5455 | 65.1401 | 52.8785 | 19.7215 | 48.6145 | 19.7215 | 4.264 | 0 | 29535.0246 | 11291.9707 | 2.9859 | 1.8677 | 21.6793 | 5.241 | 29409.4818 | 4307.3435 | 1.3999 | 0.030629 | 12.9545 | 0.041513 | 33.2455 | 4.4 | 5.592 | 15.7551 | 1.1973 | 1.0166 | 146.4 | 0 | 73.2 | 0 | 0 | 219.6 | 0 | 9.8629 | 0 | 0 | 0 | 728.065 | 46 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 4327.1562 | 1.3841 | 0.030904 | 12.7255 | 0.042079 | 32.7091 | 4.4 | 5.6734 | 15.8566 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 506 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 21 | 73.1 | 18.4913 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 3211.7529 | 0.8003 | 0.023052 | 4.6969 | 0.023296 | 22.3 | 0.9 | 5.327 | 40.5469 | 1.2007 | 1.0083 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 682.065 | 682.065 | 55.1293 | 228.8284 | 526.7 | 526.7 | 1437.5934 | 0 | 62.5041 | 1437.5934 | 228.8284 | 682.065 | 122.5221 | 404.1779
6. | The most difficult task was calculating accurate wet bulb values for TMY data. | AY | 19 | 10 | 16.38 | 8.98 | 61.02% | 0.0013086 | 5.95 | 684.21 | 46.5 | 156.3258 | 208.4345 | 19.6415 | 24.31% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 9.5307 | 1.0047 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.6415 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 19 | 73.1 | 16.38 | 4" MERV 8 | 4" MERV 8 | 24.31% | -4 | 168.5455 | 64.396 | 53.0153 | 19.509 | 48.82 | 19.509 | 4.1954 | 0 | 29864.1252 | 11287.3243 | 3.0348 | 1.8671 | 22.2799 | 5.2372 | 29743.0513 | 4152.6751 | 1.4379 | 0.028739 | 13.457 | 0.037553 | 34.1727 | 4.4 | 5.4549 | 15.609 | 1.2027 | 1.0166 | 147.7 | 0 | 73.85 | 0 | 0 | 221.55 | 0 | 9.953 | 0 | 0 | 0 | 332.7833 | 20 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 4205.1048 | 1.3841 | 0.029247 | 12.7255 | 0.0387 | 32.7091 | 4.4 | 5.6734 | 15.8672 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 220 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 19 | 73.1 | 16.38 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 3043.2299 | 0.8003 | 0.020595 | 4.6969 | 0.019721 | 22.3 | 0.9 | 5.327 | 40.6834 | 1.2007 | 1.0083 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 312.7833 | 312.7833 | 24.654 | 103.4411 | 229 | 229 | 645.2245 | 0 | 64.5224 | 645.2245 | 103.4411 | 312.7833 | 53.2705 | 175.7295
|  | AZ | 17 | 16 | 13.6313 | 1.78 | 46.49% | 0.00090429 | 5.04 | 703.3438 | 45.8 | 161.9005 | 215.8674 | 19.585 | 24.24% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 10.0231 | 1.0942 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.585 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 17 | 73.1 | 13.6313 | 4" MERV 8 | 4" MERV 8 | 24.24% | -4 | 168.5455 | 64.2109 | 53.0503 | 19.4561 | 48.8721 | 19.4561 | 4.1782 | 0 | 29947.1919 | 11286.1683 | 3.0472 | 1.867 | 22.4334 | 5.2362 | 29827.2513 | 4036.9801 | 1.445 | 0.02721 | 13.5618 | 0.034565 | 34.3909 | 4.3857 | 5.4242 | 15.5788 | 1.204 | 1.0166 | 148.1 | 0 | 74.05 | 0 | 0 | 222.15 | 0 | 9.9758 | 0 | 0 | 0 | 558.4267 | 32 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 4095.6704 | 1.3841 | 0.027794 | 12.7255 | 0.03582 | 32.7091 | 4.4 | 5.6734 | 15.8763 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 352 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 17 | 73.1 | 13.6313 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 2893.0556 | 0.8003 | 0.018498 | 4.6969 | 0.016839 | 22.3 | 0.9 | 5.327 | 40.794 | 1.2007 | 1.0083 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 526.4267 | 526.4267 | 40.8121 | 173.3853 | 365.2571 | 366.4 | 1066.2119 | 0 | 66.6382 | 1066.2119 | 173.3853 | 526.4267 | 85.2328 | 281.1672
7. | Because this is a model for an indirect evaporative cooling system, I decided | BA | 15 | 8 | 12.8625 | 5.83 | 63.19% | 0.0011143 | 4.79 | 597.6875 | 45.2 | 138.4562 | 184.6082 | 19.5978 | 24.26% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 10.1584 | 1.0477 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.5978 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 15 | 73.1 | 12.8625 | 4" MERV 8 | 4" MERV 8 | 24.26% | -4 | 168.5455 | 64.2528 | 53.0424 | 19.4681 | 48.8603 | 19.4681 | 4.1821 | 0 | 29928.359 | 11286.4298 | 3.0444 | 1.867 | 22.3985 | 5.2364 | 29808.169 | 3946.8664 | 1.4434 | 0.026045 | 13.538 | 0.032347 | 34.3364 | 4.3857 | 5.4311 | 15.5946 | 1.2037 | 1.0166 | 148 | 0 | 74 | 0 | 0 | 222 | 0 | 9.9707 | 0 | 0 | 0 | 292.2 | 16 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 4001.9525 | 1.3841 | 0.026574 | 12.7255 | 0.033464 | 32.7091 | 4.3857 | 5.6734 | 15.8837 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 175.4286 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 15 | 73.1 | 12.8625 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 2761.7076 | 0.8003 | 0.016736 | 4.6969 | 0.014544 | 22.3 | 0.9 | 5.327 | 40.8826 | 1.2007 | 1.0083 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 276.2 | 276.2 | 20.5937 | 87.775 | 182.6286 | 182.6286 | 546.6035 | 0 | 68.3254 | 546.6035 | 87.775 | 276.2 | 42.6164 | 140.0122
| to "split" the 2°F bin hours into two groupings, to more closely represent the | BB | 13 | 14 | 10.8643 | 3.02 | 60.35% | 0.00096429 | 4.15 | 439.2571 | 44.5 | 102.5066 | 136.6755 | 19.6564 | 24.33% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 10.5048 | 1.081 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.6564 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 13 | 73.1 | 10.8643 | 4" MERV 8 | 4" MERV 8 | 24.33% | -4 | 168.5455 | 64.445 | 53.0062 | 19.523 | 48.8062 | 19.523 | 4.1999 | 0 | 29842.2473 | 11287.6299 | 3.0315 | 1.8672 | 22.2397 | 5.2374 | 29720.8743 | 3872.3444 | 1.436 | 0.025097 | 13.4295 | 0.030581 | 34.1182 | 4.3857 | 5.463 | 15.641 | 1.2024 | 1.0166 | 147.6 | 0 | 73.8 | 0 | 0 | 221.4 | 0 | 9.947 | 0 | 0 | 0 | 534.0767 | 28 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 3917.9252 | 1.3841 | 0.025499 | 12.7255 | 0.031436 | 32.7091 | 4.3857 | 5.6734 | 15.8901 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 307 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 13 | 73.1 | 10.8643 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 2643.3417 | 0.8003 | 0.015206 | 4.6969 | 0.012648 | 22.3 | 0.9 | 5.327 | 40.9561 | 1.2007 | 1.0083 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 506.0767 | 506.0767 | 36.8794 | 158.4551 | 319.6 | 319.6 | 984.1318 | 0 | 70.2951 | 984.1318 | 158.4551 | 506.0767 | 74.5787 | 245.0213
| two phases if an indirect evaporative unit's intended sequence of operation, | BC | 11 | 19 | 8.1211 | -5.46 | 42.65% | 0.00061714 | 3.29 | 620.2421 | 43.8 | 145.8029 | 194.4038 | 19.4224 | 24.04% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 10.9702 | 1.1578 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.4224 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 11 | 73.1 | 8.1211 | 4" MERV 8 | 4" MERV 8 | 24.04% | -4 | 168.5455 | 63.6779 | 53.1531 | 19.3039 | 49.0248 | 19.3039 | 4.1283 | 0 | 30189.0636 | 11282.8396 | 3.0836 | 1.8665 | 22.8844 | 5.2335 | 30072.4432 | 3769.1385 | 1.4658 | 0.023808 | 13.8704 | 0.028236 | 35.0182 | 4.3857 | 5.3362 | 15.4844 | 1.2078 | 1.0165 | 149 | 0 | 74.5 | 0 | 0 | 223.5 | 0 | 10.0422 | 0 | 0 | 0 | 755.6617 | 38 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 3843.8233 | 1.3841 | 0.024566 | 12.7255 | 0.029713 | 32.7091 | 4.3857 | 5.6734 | 15.8955 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 416.6429 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 11 | 73.1 | 8.1211 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 2536.9517 | 0.8003 | 0.013877 | 4.6969 | 0.011078 | 22.3 | 0.9 | 5.327 | 41.0171 | 1.2007 | 1.0082 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 717.6617 | 717.6617 | 51.5833 | 223.8889 | 433.7429 | 433.7429 | 1375.2935 | 0 | 72.3839 | 1375.2935 | 223.8889 | 717.6617 | 101.2139 | 332.5289
| according to this design. See this distinction represented graphically on each | BD | 9 | 25 | 5.576 | -15.93 | 26.54% | 0.00034714 | 2.53 | 630.46 | 43.2 | 149.1292 | 198.8389 | 19.278 | 23.86% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 11.3815 | 1.2176 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.278 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 9 | 73.1 | 5.576 | 4" MERV 8 | 4" MERV 8 | 23.86% | -4 | 168.5455 | 63.2043 | 53.2472 | 19.1687 | 49.1636 | 19.1687 | 4.0836 | 0 | 30407.3822 | 11279.8822 | 3.1166 | 1.8661 | 23.297 | 5.231 | 30293.759 | 3689.5051 | 1.4847 | 0.022834 | 14.1529 | 0.026509 | 35.6 | 4.3857 | 5.2584 | 15.3884 | 1.2112 | 1.0165 | 149.9 | 0 | 74.95 | 0 | 0 | 224.85 | 0 | 10.1021 | 0 | 0 | 0 | 1034.875 | 50 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 3780.488 | 1.3841 | 0.023779 | 12.7255 | 0.028288 | 32.7091 | 4.3857 | 5.6734 | 15.9 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 548.2143 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 9 | 73.1 | 5.576 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 2442.0512 | 0.8003 | 0.012728 | 4.6969 | 0.0097807 | 22.3 | 0.9 | 5.327 | 41.0677 | 1.2007 | 1.0082 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 984.875 | 984.875 | 69.655 | 304.8729 | 570.7143 | 570.7143 | 1860.4622 | 0 | 74.4185 | 1860.4622 | 304.8729 | 984.875 | 133.1762 | 437.5381
| IDEC units' submittal tab. | BE | 7 | 16 | 3.9125 | -16.83 | 27.91% | 0.00033 | 2.03 | 1.9562 | 42.5 | 0.46608 | 0.62144 | 19.9971 | 24.75% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 11.652 | 1.2214 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.9971 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 7 | 73.1 | 3.9125 | 4" MERV 8 | 4" MERV 8 | 24.75% | -4 | 168.5455 | 65.5619 | 52.7869 | 19.841 | 48.4885 | 19.841 | 4.2984 | 0 | 29351.7758 | 11294.6048 | 2.9489 | 1.8666 | 21.2778 | 5.2391 | 29223.5428 | 3727.9752 | 1.3844 | 0.023135 | 12.7304 | 0.027139 | 32.7273 | 4.3857 | 5.6718 | 15.9016 | 1.1942 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8119 | 0 | 0 | 0 | 688.2933 | 32 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 3728.3284 | 1.3841 | 0.02314 | 12.7255 | 0.027147 | 32.7091 | 4.3857 | 5.6734 | 15.9036 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 350.8571 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 7 | 73.1 | 3.9125 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 2357.9287 | 0.8003 | 0.01174 | 4.6969 | 0.0087102 | 22.3 | 0.9 | 5.327 | 41.1095 | 1.2007 | 1.0082 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 656.2933 | 656.2933 | 45.3296 | 199.448 | 365.2571 | 365.2571 | 1220.9985 | 0 | 76.3124 | 1220.9985 | 199.448 | 656.2933 | 85.2328 | 280.0244
|  | BF | 5 | 4 | 1.575 | -31.11 | 13.44% | 0.00014286 | 1.35 | 342.125 | 41.9 | 82.0132 | 109.3509 | 19.2853 | 23.87% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 12.02 | 1.2629 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.2853 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 5 | 73.1 | 1.575 | 4" MERV 8 | 4" MERV 8 | 23.87% | -4 | 168.5455 | 63.2282 | 53.2424 | 19.1755 | 49.1565 | 19.1755 | 4.0859 | 0 | 30396.2877 | 11280.0315 | 3.1149 | 1.8662 | 23.2759 | 5.2312 | 30282.5198 | 3599.5301 | 1.4838 | 0.021752 | 14.1385 | 0.024637 | 35.5727 | 4.3714 | 5.2623 | 15.3992 | 1.2111 | 1.0165 | 149.9 | 0 | 74.95 | 0 | 0 | 224.85 | 0 | 10.0991 | 0 | 0 | 0 | 178.5667 | 8 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 3685.0089 | 1.3841 | 0.022613 | 12.7255 | 0.026221 | 32.7091 | 4.3857 | 5.6734 | 15.9065 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 87.7143 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 5 | 73.1 | 1.575 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 2282.1991 | 0.8003 | 0.010873 | 4.6969 | 0.0078081 | 22.3 | 0.9 | 5.327 | 41.1448 | 1.2007 | 1.0082 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 170.5667 | 170.5667 | 11.5875 | 51.334 | 91.0286 | 91.3143 | 313.2149 | 0 | 78.3037 | 313.2149 | 51.334 | 170.5667 | 21.3082 | 70.0061
8. | There is a "dry" group of hours sorted by dry bulb containing hours below 65°F | BG | 3 | 0
| dry bulb outdoors. Below those a moist group containing the rest of the hours, | BH | 1 | 0
| during which the evaporative process takes place. | BI | -1 | 2 | -3.8 | -44.97 | 7.74% | 6e-05 | -0.18 | 386.4 | 39.9 | 94.515 | 126.0201 | 20 | 29.86% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 12.848 | 1.2812 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -1 | 73.1 | -3.8 | 4" MERV 8 | 4" MERV 8 | 29.86% | -4 | 168.5455 | 79.0736 | 52.7853 | 24.0553 | 48.486 | 24.0553 | 4.2992 | 0 | 29347.6707 | 13620.4065 | 2.9483 | 2.0291 | 21.2705 | 6.868 | 29219.3903 | 4377.1949 | 1.3841 | 0.030444 | 12.7255 | 0.041931 | 32.7091 | 5.7571 | 5.6734 | 14.6924 | 1.1941 | 1.0217 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 99.0233 | 4 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 3614.6067 | 1.3841 | 0.021769 | 12.7255 | 0.024759 | 32.7091 | 4.3857 | 5.6734 | 15.9111 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 43.8571 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -1 | 73.1 | -3.8 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 2102.006 | 0.8003 | 0.0089007 | 4.6969 | 0.0058871 | 22.3 | 0.9 | 5.327 | 41.2202 | 1.2007 | 1.0082 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 95.0233 | 95.0233 | 6.0808 | 27.323 | 59.3714 | 45.6571 | 168.0035 | 0 | 84.0017 | 168.0035 | 27.323 | 95.0233 | 10.6541 | 35.003
|  | BJ | -3 | 0
| Here is the sequence for repeating / reviewing my calculation. | BK | -5 | 1 | -6.7 | -25.11 | 32.42% | 0.00020429 | -0.98 | 0 | 38.6 | 0 | 0 | 20 | 24.76% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 13.281 | 1.2493 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -5 | 73.1 | -6.7 | 4" MERV 8 | 4" MERV 8 | 24.76% | -4 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 3618.3072 | 1.3841 | 0.021813 | 12.7255 | 0.024835 | 32.7091 | 4.3857 | 5.6734 | 15.9109 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 52.7583 | 2 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 3618.3072 | 1.3841 | 0.021813 | 12.7255 | 0.024835 | 32.7091 | 4.3857 | 5.6734 | 15.9109 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 21.9286 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -5 | 73.1 | -6.7 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 2014.4796 | 0.8003 | 0.0079883 | 4.6969 | 0.0050636 | 22.3 | 0.9 | 5.327 | 41.2526 | 1.2007 | 1.0082 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 50.7583 | 50.7583 | 3.1154 | 14.0944 | 22.8286 | 22.8286 | 87.6813 | 0 | 87.6813 | 87.6813 | 14.0944 | 50.7583 | 5.327 | 17.5015
|  | BL | -7 | 4 | -8.125 | -19.29 | 50.54% | 0.00028714 | -1.37 | 507.15 | 37.9 | 126.5295 | 168.7061 | 20 | 25.73% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 13.492 | 1.2309 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -7 | 73.1 | -8.125 | 4" MERV 8 | 4" MERV 8 | 25.73% | -4 | 168.5455 | 68.1537 | 52.7853 | 20.6445 | 48.486 | 20.6445 | 4.2992 | 0 | 29347.6707 | 11739.4537 | 2.9483 | 1.8956 | 21.2705 | 5.5302 | 29219.3903 | 3782.7789 | 1.3841 | 0.023611 | 12.7255 | 0.028104 | 32.7091 | 4.6286 | 5.6734 | 15.6763 | 1.1941 | 1.0175 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 217.5267 | 8 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 3636.688 | 1.3841 | 0.022032 | 12.7255 | 0.025212 | 32.7091 | 4.3857 | 5.6734 | 15.9097 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 87.7143 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -7 | 73.1 | -8.125 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 1979.111 | 0.8003 | 0.0076281 | 4.6969 | 0.0047504 | 22.3 | 0.9 | 5.327 | 41.2649 | 1.2007 | 1.0082 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 209.5267 | 209.5267 | 12.6081 | 57.2219 | 96.1714 | 91.3143 | 358.0629 | 0 | 89.5157 | 358.0629 | 57.2219 | 209.5267 | 21.3082 | 70.0061
9. | Maintain coordination with electrical design. Keep input values in rows 44-46 | BM | -9 | 2 | -10.95 | -54.68 | 6.27% | 3.1429e-05 | -2.12 | 281.75 | 37.2 | 70.7761 | 94.3682 | 20 | 25.18% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 13.8979 | 1.2876 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -9 | 73.1 | -10.95 | 4" MERV 8 | 4" MERV 8 | 25.18% | -4 | 168.5455 | 66.6949 | 52.7853 | 20.1919 | 48.486 | 20.1919 | 4.2992 | 0 | 29347.6707 | 11488.1749 | 2.9483 | 1.8791 | 21.2705 | 5.3646 | 29219.3903 | 3729.7642 | 1.3841 | 0.023072 | 12.7255 | 0.027078 | 32.7091 | 4.4857 | 5.6734 | 15.8063 | 1.1941 | 1.017 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 112.01 | 4 | 0 | 0 | 1 | 168.5455 | 65.5714 | 52.7853 | 19.8438 | 48.486 | 19.8438 | 4.2992 | 0 | 29347.6707 | 11294.6642 | 2.9483 | 1.8666 | 21.2705 | 5.2392 | 29219.3903 | 3665.7314 | 1.3841 | 0.022381 | 12.7255 | 0.025815 | 32.7091 | 4.3857 | 5.6734 | 15.9078 | 1.1941 | 1.0166 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 43.8571 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -9 | 73.1 | -10.95 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8338 | 10.6939 | 16.2525 | 10.6939 | 17.5813 | 0 | 18050.1605 | 5849.113 | 2.1706 | 0.74926 | 9.6314 | 1.0975 | 18651.5104 | 1948.1238 | 0.8003 | 0.0073163 | 4.6969 | 0.0044849 | 22.3 | 0.9 | 5.327 | 41.2754 | 1.2007 | 1.0082 | 77.5 | 0 | 38.75 | 0 | 0 | 116.25 | 0 | 7.9132 | 0 | 0 | 108.01 | 108.01 | 6.4447 | 29.4227 | 46.6571 | 45.6571 | 183.0899 | 0 | 91.5449 | 183.0899 | 29.4227 | 108.01 | 10.6541 | 35.003
| of the Summary tab that are consistent with the electrical design. | BN | -11 | 0
|  |  | total | 6365 | hours
10. | Manual psychrometric solutions appear to the left here, in column 15 (or
| column "O" if you prefer). There are 98 such manual selections in this bin tab; | [195 empty] | NO | selected | Resulting | Resulting | Ventilation | Gen | UPS | ITE
| common psychrometric results may be copied to other scenario tabs | 2°F wet bulb bins (for hours above 65°F dry bulb) | [7 empty] | Annual HW demand of cafeteria: |  |  |  | recovery | zone | Properties of IT equipment zone: | [5 empty] | Properties for generic ventilation air handlers. | [17 empty] | Information used for hourly inputs for ITE room IDEC units (shown with heat recovery input) | [27 empty] | Outputs for ITE room IDEC units with heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | HR export |  | Generator room | [20 empty] | Outputs for ITE room IDEC units without heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | Without HR | UPS room variables | [13 empty] | Information used for hourly inputs for UPS room IDEC units | [27 empty] | Outputs for UPS units. NOTE: most of the performance values are PER UNIT | [18 empty] | Generator Room |  | Ventilation system |  | ITE and UPS cooling |  | Recovery | recovery | Mechanical | Mechanical | system | room | room | room
|  | bin | Average | bin | Outdoor |  |  |  | Psychrometric values for averaged points: | café avg | entering | kwh from | H2O heater | delta T | % design | Temp | AHU | Min | Max | min. | max. | control | heat | liquid | Cooling | DX split | room air | Project | Design | Design | Reset | Resulting | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | energy avoided | Room heat | engine block | Recovery | Recovery |  | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | error | ITE cooling | UPS room | Battery | Project | Design | Design | Design | Alternate | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | with | without | with | without | with | without | whatsoever | savings | Input | energy | HVAC | HVAC | cooling | cooling
11. | Review equipment selections, ensure they are consistent with your design | name | dry bulb | hours | wet bulb | dewpoint | %rh | moisture | enthalpy | 140 | temp | hot aisle | input energy | w/ HR | w/ HR | into ITE | SAT: | moisture | moisture | enthalpy | enthalpy | mode | power | added | needed | kW input: | dew point | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | message | elsewhere | need, kWh | heat, kWh | Potential | Savings |  | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | annual kWh | temp | temp | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | recovery | recovery | recovery | recovery | recovery | recovery | at all | kWh: | Power | incl. Recov | Component | component | component | component
| especially during the extreme climate data. Fill out the remaining user input | CA | 66 | 4 | 46 | 25 | 20.24% | 0.0028629 | 18.95 | 853.3 | 55.4 | 176.4013 | 235.2018 | 19.8835 | 24.61% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 3.9064 | 0.90428 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.8835 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 66 | 73.1 | 46 | 4" MERV 8 | 4" MERV 8 | 24.61% | -4 | 168.5455 | 65.1896 | 52.8661 | 19.7403 | 48.5984 | 19.7403 | 4.2677 | 0 | 29504.9523 | 11411.8548 | 2.9814 | 1.8755 | 21.625 | 5.2615 | 29323.8563 | 2452.3513 | 1.3927 | 0.01421 | 12.8509 | 0.010965 | 33.1091 | 6.7714 | 5.6135 | 10.2472 | 1.1965 | 1.0256 | 146.1 | 22.2 | 73.05 | 11.1 | 0 | 219.15 | 33.3 | 9.8423 | 1.428 | 0 | 0 | 0 | 7.2 | 0 | 0 | 0.9 | 1.9333 | 65.5714 | 52.7818 | 19.8483 | 48.4834 | 19.8483 | 4.2984 | 0 | 29339.2726 | 11414.2385 | 2.947 | 1.8743 | 21.2555 | 5.2593 | 29156.0382 | 2469.1594 | 1.3788 | 0.0144 | 12.6498 | 0.011189 | 32.6364 | 6.7571 | 5.6868 | 10.3266 | 1.1936 | 1.0255 | 145.4 | 22.3 | 72.7 | 11.15 | 0 | 218.1 | 33.45 | 9.7961 | 1.4361 | 0 | 135.1429 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 66 | 73.1 | 46 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8323 | 10.6963 | 16.2514 | 10.6963 | 17.5809 | 0 | 18044.9953 | 5956.6004 | 2.1698 | 0.75651 | 9.6251 | 1.1078 | 18611.7148 | 2545.1571 | 0.79749 | 0.01781 | 4.6704 | 0.014263 | 22.3 | 1.9 | 5.3337 | 20.3205 | 1.2005 | 1.0166 | 77.4 | 13.9 | 38.7 | 6.95 | 0 | 116.1 | 20.85 | 7.8993 | 2.134 | 0 | 7.2 | 7.2 | 5.9622 | 18.8793 | 143.0286 | 142.7429 | 168.8222 | -1.1546e-14 | 42.2055 | 168.8222 | 18.8793 | 7.2 | 21.3348 | 121.408
| (yellow cells in boxes), including how much cooling equipment to install, | CB | 67.7765 | 34 | 48 | 29.1 | 23.04% | 0.0034686 | 20.04 | 805.9118 | 56 | 165.4232 | 220.5643 | 19.8937 | 24.63% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 3.3165 | 0.77013 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.8937 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 67.7765 | 73.1 | 48 | 4" MERV 8 | 4" MERV 8 | 24.63% | -4 | 168.5455 | 65.2228 | 52.8601 | 19.7497 | 48.5894 | 19.7497 | 4.2707 | 0 | 29490.4923 | 11412.0618 | 2.9793 | 1.8755 | 21.599 | 5.2617 | 29309.2209 | 2556.228 | 1.3915 | 0.015421 | 12.8333 | 0.012404 | 33.0727 | 6.7714 | 5.6191 | 10.2518 | 1.1962 | 1.0256 | 146 | 22.5 | 73 | 11.25 | 0 | 219 | 33.75 | 9.8383 | 1.4478 | 0 | 0 | 0 | 59.1867 | 0 | 0 | 0.87039 | 1.4333 | 65.5714 | 52.7818 | 19.8483 | 48.4834 | 19.8483 | 4.2984 | 0 | 29339.2726 | 11414.2385 | 2.947 | 1.8743 | 21.2555 | 5.2593 | 29156.0382 | 2572.4943 | 1.3788 | 0.015611 | 12.6498 | 0.012637 | 32.6364 | 6.7571 | 5.6868 | 10.3247 | 1.1936 | 1.0255 | 145.4 | 22.6 | 72.7 | 11.3 | 0 | 218.1 | 33.9 | 9.7961 | 1.4553 | 0 | 1148.7143 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 67.7765 | 73.1 | 48 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8323 | 10.6963 | 16.2514 | 10.6963 | 17.5809 | 0 | 18044.9953 | 5956.6004 | 2.1698 | 0.75651 | 9.6251 | 1.1078 | 18611.7148 | 2836.1234 | 0.79749 | 0.022288 | 4.6704 | 0.019891 | 22.3 | 1.9 | 5.3337 | 20.2669 | 1.2005 | 1.0167 | 77.4 | 14.6 | 38.7 | 7.3 | 0 | 116.1 | 21.9 | 7.8993 | 2.2284 | 0 | 59.1867 | 59.1867 | 47.2022 | 140.4184 | 1215.7429 | 1213.3143 | 1412.9194 | 0 | 41.5565 | 1412.9194 | 140.4184 | 59.1867 | 181.346 | 1031.9683
| when. Review accuracy of generator room heating load, HW export schedule | CC | 67.3902 | 102 | 50 | 35.69 | 30.93% | 0.0046029 | 21.18 | 714.6784 | 56.7 | 145.474 | 193.9654 | 19.9059 | 24.64% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 2.6996 | 0.51893 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9059 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 67.3902 | 73.1 | 50 | 4" MERV 8 | 4" MERV 8 | 24.64% | -4 | 168.5455 | 65.263 | 52.8529 | 19.7612 | 48.5786 | 19.7612 | 4.2744 | 0 | 29472.9356 | 11412.3133 | 2.9767 | 1.8756 | 21.5673 | 5.2619 | 29291.4599 | 2692.4265 | 1.39 | 0.016956 | 12.8119 | 0.014366 | 33.0273 | 6.7714 | 5.6258 | 10.2571 | 1.196 | 1.0256 | 145.9 | 22.2 | 72.95 | 11.1 | 0 | 218.85 | 33.3 | 9.8335 | 1.4299 | 0 | 0 | 0 | 178.8733 | 0 | 0 | 0.87683 | 0.3 | 65.5714 | 52.7818 | 19.8483 | 48.4834 | 19.8483 | 4.2984 | 0 | 29339.2726 | 11414.2385 | 2.947 | 1.8743 | 21.2555 | 5.2593 | 29156.0382 | 2707.6961 | 1.3788 | 0.017141 | 12.6498 | 0.014604 | 32.6364 | 6.7571 | 5.6868 | 10.3221 | 1.1936 | 1.0255 | 145.4 | 22.3 | 72.7 | 11.15 | 0 | 218.1 | 33.45 | 9.7961 | 1.4364 | 0 | 3446.1429 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 67.3902 | 73.1 | 50 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8323 | 10.6963 | 16.2514 | 10.6963 | 17.5809 | 0 | 18044.9953 | 5956.6004 | 2.1698 | 0.75651 | 9.6251 | 1.1078 | 18611.7148 | 3207.1986 | 0.79749 | 0.028376 | 4.6704 | 0.028637 | 22.3 | 1.9 | 5.3337 | 20.1841 | 1.2005 | 1.0167 | 77.4 | 14.5 | 38.7 | 7.25 | 0 | 116.1 | 21.75 | 7.8993 | 2.2255 | 0 | 178.8733 | 178.8733 | 130.6996 | 358.328 | 3647.2286 | 3639.9429 | 4177.1442 | 0 | 40.9524 | 4177.1442 | 358.328 | 178.8733 | 544.0381 | 3095.9048
| if those heat recovery options are to be considered in your design. | CD | 69.132 | 222 | 52 | 41.82 | 37.04% | 0.0058643 | 22.98 | 628.5946 | 57.4 | 126.8763 | 169.1684 | 19.92 | 24.66% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 1.7255 | 0.23957 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.92 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 69.132 | 73.1 | 52 | 4" MERV 8 | 4" MERV 8 | 24.66% | -4 | 168.5455 | 65.3092 | 52.8282 | 19.7735 | 48.5537 | 19.7735 | 4.2745 | 0 | 29452.8303 | 11412.6017 | 2.9637 | 1.8741 | 21.4588 | 5.258 | 29270.9146 | 2846.564 | 1.3883 | 0.018854 | 12.7874 | 0.016888 | 32.9182 | 6.7714 | 5.6426 | 10.2677 | 1.1953 | 1.0256 | 145.9 | 22.6 | 72.95 | 11.3 | 0 | 218.85 | 33.9 | 9.8272 | 1.4515 | 0 | 0 | 0 | 376.4233 | 0 | 0 | 0.8478 | -1.7 | 65.5714 | 52.7818 | 19.8483 | 48.4834 | 19.8483 | 4.2984 | 0 | 29339.2726 | 11414.2385 | 2.947 | 1.8743 | 21.2555 | 5.2593 | 29156.0382 | 2860.6427 | 1.3788 | 0.019031 | 12.6498 | 0.017131 | 32.6364 | 6.7571 | 5.6868 | 10.3187 | 1.1936 | 1.0255 | 145.4 | 22.7 | 72.7 | 11.35 | 0 | 218.1 | 34.05 | 9.7961 | 1.4572 | 0 | 7500.4286 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 69.132 | 73.1 | 52 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8323 | 10.6963 | 16.2514 | 10.6963 | 17.5809 | 0 | 18044.9953 | 5956.6004 | 2.1698 | 0.75651 | 9.6251 | 1.1078 | 18611.7148 | 3706.9544 | 0.79749 | 0.037679 | 4.6704 | 0.04395 | 22.3 | 1.9 | 5.3337 | 20.0408 | 1.2005 | 1.0169 | 77.4 | 15.4 | 38.7 | 7.7 | 0 | 116.1 | 23.1 | 7.8993 | 2.3579 | 0 | 376.4233 | 376.4233 | 246.9809 | 563.6386 | 7938.0857 | 7922.2286 | 8862.2905 | 0 | 39.9202 | 8862.2905 | 563.6386 | 376.4233 | 1184.0829 | 6738.1457
|  | CE | 71.0419 | 332 | 54 | 47.12 | 42.47% | 0.0071914 | 24.89 | 632.4307 | 58 | 126.7233 | 168.9644 | 19.9223 | 24.66% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 0.69182 | 0 | 0 | 0 | 46.9 | 1259.52 | 1854 | 78 | 78 | 19.9223 | 46.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 71.0419 | 73.1 | 54 | 4" MERV 8 | 4" MERV 8 | 24.66% | -4 | 168.5455 | 65.3166 | 52.8262 | 19.7755 | 48.5512 | 19.7755 | 4.275 | 0 | 29447.9585 | 11411.9992 | 2.963 | 1.8741 | 21.45 | 5.2576 | 29255.0565 | 3031.4791 | 1.387 | 0.021228 | 12.7683 | 0.02025 | 32.8909 | 6.7714 | 5.6465 | 10.2654 | 1.1952 | 1.0256 | 145.8 | 23 | 72.9 | 11.5 | 0 | 218.7 | 34.5 | 9.8234 | 1.4785 | 0 | 0 | 0 | 541.8033 | 0 | 0 | 0.81597 | -3.5333 | 65.5714 | 52.7812 | 19.8483 | 48.4829 | 19.8483 | 4.2982 | 0 | 29337.6056 | 11413.59 | 2.9468 | 1.8743 | 21.2525 | 5.2589 | 29143.4746 | 3046.2598 | 1.3778 | 0.021423 | 12.6348 | 0.020535 | 32.6182 | 6.7714 | 5.6895 | 10.3149 | 1.1935 | 1.0255 | 145.3 | 23.1 | 72.65 | 11.55 | 0 | 217.95 | 34.65 | 9.7933 | 1.4842 | 0 | 11240.5714 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 71.0419 | 73.1 | 54 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.832 | 10.6963 | 16.2512 | 10.6963 | 17.5809 | 0 | 18043.9701 | 5956.262 | 2.1696 | 0.75649 | 9.6238 | 1.1077 | 18603.816 | 4390.5535 | 0.79693 | 0.052174 | 4.6652 | 0.072081 | 22.3 | 1.9 | 5.335 | 19.7842 | 1.2004 | 1.0171 | 77.3 | 16.6 | 38.65 | 8.3 | 0 | 115.95 | 24.9 | 7.8965 | 2.5471 | 0 | 541.8033 | 541.8033 | 309.8778 | 499.752 | 11871.3714 | 11871.3714 | 12912.9267 | 0 | 38.8944 | 12912.9267 | 499.752 | 541.8033 | 1771.2292 | 10100.1423
12. | Commence iterations, using manufacturer's tool. I automated | CF | 73.161 | 351 | 56 | 49.75 | 43.62% | 0.0079457 | 26.23 | 621.6316 | 58.7 | 123.4961 | 164.6615 | 19.9264 | 24.67% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 48.9 | 1259.52 | 1854 | 78 | 78 | 19.9264 | 48.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 73.161 | 73.1 | 56 | 4" MERV 8 | 4" MERV 8 | 24.67% | -4 | 168.5455 | 65.3303 | 52.8222 | 19.7792 | 48.5463 | 19.7792 | 4.2758 | 0 | 29438.1106 | 11410.5726 | 2.9616 | 1.874 | 21.4323 | 5.2567 | 29219.6172 | 3258.8842 | 1.3841 | 0.024295 | 12.7258 | 0.024914 | 32.8455 | 6.7714 | 5.655 | 10.2635 | 1.1949 | 1.0256 | 145.7 | 23.5 | 72.85 | 11.75 | 0 | 218.55 | 35.25 | 9.815 | 1.5143 | 0 | 0 | 0 | 548.0167 | 0 | 0 | 0.78065 | -3.85 | 65.5714 | 52.7796 | 19.848 | 48.4818 | 19.848 | 4.2978 | 0 | 29333.7186 | 11412.0778 | 2.9462 | 1.8742 | 21.2456 | 5.2579 | 29114.1565 | 3274.1112 | 1.3754 | 0.024508 | 12.5999 | 0.025249 | 32.5818 | 6.7714 | 5.6957 | 10.3102 | 1.1933 | 1.0256 | 145.2 | 23.6 | 72.6 | 11.8 | 0 | 217.8 | 35.4 | 9.7865 | 1.5199 | 0 | 11883.8571 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 48.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 73.161 | 73.1 | 56 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8314 | 10.6962 | 16.2507 | 10.6962 | 17.5807 | 0 | 18041.5794 | 5955.4728 | 2.1692 | 0.75644 | 9.6209 | 1.1075 | 18585.397 | 5359.6701 | 0.79563 | 0.076241 | 4.653 | 0.12858 | 22.3 | 1.9 | 5.3381 | 19.2884 | 1.2003 | 1.0175 | 77.3 | 18.5 | 38.65 | 9.25 | 0 | 115.95 | 27.75 | 7.89 | 2.829 | 0 | 548.0167 | 548.0167 | 285.5221 | 285.5221 | 12550.7571 | 12550.7571 | 13384.2959 | 0 | 38.1319 | 13384.2959 | 285.5221 | 548.0167 | 1873.6755 | 10677.0817
| that process to make this example happen. This calculation | CG | 74.8974 | 418 | 58 | 52.59 | 45.72% | 0.00884 | 27.64 | 652.6742 | 59.3 | 128.7063 | 171.6084 | 19.9251 | 24.66% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 53.1 | 1259.52 | 1854 | 78 | 78 | 19.9251 | 53.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 74.8974 | 73.1 | 58 | 4" MERV 8 | 4" MERV 8 | 24.66% | -4 | 168.5455 | 65.3259 | 52.8192 | 19.7774 | 48.5447 | 19.7774 | 4.2745 | 0 | 29430.9275 | 11407.0293 | 2.9605 | 1.8738 | 21.4194 | 5.2544 | 29153.0801 | 3541.8731 | 1.3786 | 0.028298 | 12.6463 | 0.031538 | 32.7636 | 6.7857 | 5.6687 | 10.2576 | 1.1944 | 1.0256 | 145.4 | 24 | 72.7 | 12 | 0 | 218.1 | 36 | 9.7996 | 1.5465 | 0 | 0 | 0 | 628.43 | 0 | 0 | 0.75171 | -4.9667 | 65.5714 | 52.7759 | 19.8475 | 48.479 | 19.8475 | 4.2969 | 0 | 29324.6793 | 11408.5611 | 2.9449 | 1.874 | 21.2295 | 5.2557 | 29045.9682 | 3558.8592 | 1.3697 | 0.02855 | 12.519 | 0.031972 | 32.5 | 6.7714 | 5.7102 | 10.305 | 1.1928 | 1.0256 | 145 | 24.1 | 72.5 | 12.05 | 0 | 217.5 | 36.15 | 9.7707 | 1.5524 | 0 | 14152.2857 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 53.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 74.8974 | 73.1 | 58 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8298 | 10.6961 | 16.2495 | 10.2834 | 17.5803 | 0.4127 | 18036.0198 | 5953.6376 | 2.1684 | 0.75636 | 9.6141 | 1.107 | 18542.5629 | 5795.7246 | 0.79262 | 0.088187 | 4.6246 | 0.16083 | 22.3 | 2.2 | 5.3453 | 17.1425 | 1.2 | 1.0197 | 77.1 | 18.8 | 38.55 | 9.4 | 0 | 115.65 | 28.2 | 7.8749 | 2.8765 | 0 | 628.43 | 628.43 | 340.0235 | 340.0235 | 15101.7429 | 15071.8857 | 16040.3392 | 0 | 38.374 | 16040.3392 | 340.0235 | 628.43 | 2234.32 | 12837.5658
| does not reflect any actual data center. I completed this for | CH | 78.9962 | 338 | 60 | 53.8 | 41.73% | 0.0092486 | 29.09 | 685.0284 | 60 | 133.9147 | 178.553 | 19.9261 | 24.67% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 53.1 | 1259.52 | 1854 | 78 | 78 | 19.9261 | 53.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 78.9962 | 73.1 | 60 | 4" MERV 8 | 4" MERV 8 | 24.67% | -4 | 168.5455 | 65.3293 | 52.8186 | 19.7784 | 48.5438 | 19.7784 | 4.2748 | 0 | 29429.4859 | 11407.05 | 2.9603 | 1.8738 | 21.4169 | 5.2545 | 29151.6363 | 3905.3742 | 1.3785 | 0.033958 | 12.6446 | 0.04173 | 32.7545 | 6.7857 | 5.6693 | 10.2448 | 1.1944 | 1.0256 | 145.4 | 25.7 | 72.7 | 12.85 | 0 | 218.1 | 38.55 | 9.7993 | 1.6507 | 0 | 0 | 0 | 461.9767 | 0 | 0 | 0.6834 | -3.6333 | 65.5714 | 52.7759 | 19.8475 | 48.479 | 19.8475 | 4.2969 | 0 | 29324.6793 | 11408.5611 | 2.9449 | 1.874 | 21.2295 | 5.2557 | 29045.9682 | 3924.1265 | 1.3697 | 0.03426 | 12.519 | 0.042303 | 32.5 | 6.7857 | 5.7102 | 10.2914 | 1.1928 | 1.0256 | 145 | 25.8 | 72.5 | 12.9 | 0 | 217.5 | 38.7 | 9.7707 | 1.657 | 0 | 11467.8571 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 53.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 78.9962 | 73.1 | 60 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8298 | 10.6961 | 16.2495 | 9.6212 | 17.5803 | 1.0749 | 18036.0198 | 5953.6376 | 2.1684 | 0.75641 | 9.6141 | 1.1071 | 18542.5629 | 5834.3768 | 0.79262 | 0.089408 | 4.6246 | 0.16414 | 22.3 | 2.5 | 5.3453 | 14.7804 | 1.2 | 1.0229 | 77.1 | 19.7 | 38.55 | 9.85 | 0 | 115.65 | 29.55 | 7.8749 | 3.0182 | 0 | 461.9767 | 461.9767 | 274.9472 | 274.9472 | 12312.8571 | 12312.8571 | 13049.781 | 0 | 38.6088 | 13049.781 | 274.9472 | 461.9767 | 1806.6989 | 10506.1582
| example purposes only. | CI | 83.3602 | 241 | 62 | 54.97 | 37.78% | 0.0096571 | 30.62 | 751.9813 | 60.7 | 145.7169 | 194.2892 | 19.9238 | 24.66% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 55 | 1259.52 | 1854 | 78 | 78 | 19.9238 | 55 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 83.3602 | 73.1 | 62 | 4" MERV 8 | 4" MERV 8 | 24.66% | -4 | 168.5455 | 65.3217 | 52.8181 | 19.776 | 48.5444 | 19.776 | 4.2737 | 0 | 29428.2388 | 11405.2488 | 2.9601 | 1.8737 | 21.4146 | 5.2533 | 29120.7912 | 4385.2927 | 1.3759 | 0.042069 | 12.6079 | 0.058051 | 32.7273 | 6.8 | 5.6752 | 10.2238 | 1.1941 | 1.0257 | 145.3 | 27.8 | 72.65 | 13.9 | 0 | 217.95 | 41.7 | 9.7922 | 1.7892 | 0 | 0 | 0 | 294.34 | 0 | 0 | 0.61066 | -2.0167 | 65.5714 | 52.7741 | 19.8473 | 48.4776 | 19.8473 | 4.2965 | 0 | 29320.1699 | 11406.8067 | 2.9442 | 1.8739 | 21.2214 | 5.2546 | 29011.9565 | 4407.2801 | 1.3669 | 0.042459 | 12.4788 | 0.058883 | 32.4545 | 6.8 | 5.7174 | 10.2713 | 1.1926 | 1.0257 | 144.9 | 27.9 | 72.45 | 13.95 | 0 | 217.35 | 41.85 | 9.7628 | 1.7964 | 0 | 8194 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 55 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 83.3602 | 73.1 | 62 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.829 | 10.6961 | 16.2489 | 8.9432 | 17.5801 | 1.7529 | 18033.2463 | 5952.7221 | 2.1679 | 0.7564 | 9.6107 | 1.1069 | 18521.194 | 5867.2561 | 0.79111 | 0.09054 | 4.6106 | 0.16716 | 22.2 | 2.9 | 5.3488 | 12.9561 | 1.1999 | 1.0261 | 77.1 | 20.8 | 38.55 | 10.4 | 0 | 115.65 | 31.2 | 7.8674 | 3.1788 | 0 | 294.34 | 294.34 | 196.0423 | 196.0423 | 8892.9 | 8892.9 | 9383.2823 | 0 | 38.9348 | 9383.2823 | 196.0423 | 294.34 | 1289.0683 | 7603.8317
|  | CJ | 87.0126 | 190 | 64 | 56.69 | 35.78% | 0.010289 | 32.19 | 764.4621 | 61.3 | 147.0146 | 196.0195 | 19.9264 | 24.67% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 55.9 | 1259.52 | 1854 | 78 | 78 | 19.9264 | 55.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 87.0126 | 73.1 | 64 | 4" MERV 8 | 4" MERV 8 | 24.67% | -4 | 168.5455 | 65.3301 | 52.8157 | 19.7782 | 48.5415 | 19.7782 | 4.2742 | 0 | 29422.3697 | 11404.4321 | 2.9593 | 1.8736 | 21.4041 | 5.2528 | 29100.2293 | 5051.8963 | 1.3742 | 0.054398 | 12.5834 | 0.086473 | 32.6909 | 6.8286 | 5.6802 | 10.1893 | 1.194 | 1.0258 | 145.3 | 30.3 | 72.65 | 15.15 | 0 | 217.95 | 45.45 | 9.7873 | 1.9472 | 0 | 0 | 0 | 208.92 | 0 | 0 | 0.54979 | -1.1667 | 65.5714 | 52.7732 | 19.8471 | 48.4769 | 19.8471 | 4.2962 | 0 | 29317.9365 | 11405.9378 | 2.9439 | 1.8738 | 21.2174 | 5.254 | 28995.1191 | 5076.408 | 1.3656 | 0.054887 | 12.4589 | 0.087674 | 32.4364 | 6.8143 | 5.721 | 10.2345 | 1.1924 | 1.0257 | 144.8 | 30.4 | 72.4 | 15.2 | 0 | 217.2 | 45.6 | 9.759 | 1.955 | 0 | 6473.5714 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 55.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 87.0126 | 73.1 | 64 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8287 | 10.6961 | 16.2486 | 8.2617 | 17.58 | 2.4344 | 18031.8726 | 5952.2686 | 2.1677 | 0.75642 | 9.609 | 1.1068 | 18510.6106 | 5904.5573 | 0.79037 | 0.091632 | 4.6036 | 0.17025 | 22.2 | 3.3 | 5.3506 | 11.5252 | 1.1998 | 1.0293 | 77 | 21.3 | 38.5 | 10.65 | 0 | 115.5 | 31.95 | 7.8637 | 3.2651 | 0 | 208.92 | 208.92 | 154.5561 | 154.5561 | 7114.1429 | 7100.5714 | 7464.0476 | 0 | 39.2845 | 7464.0476 | 154.5561 | 208.92 | 1016.6135 | 6083.9579
|  | CK | 91.5062 | 97 | 68 | 57.99 | 32.54% | 0.010791 | 33.84 | 778.732 | 62.6 | 147.2851 | 196.3801 | 19.9299 | 24.67% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 0.059294 | 0.047435 | 57.9 | 1259.52 | 1854 | 78 | 78 | 19.9299 | 57.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 91.5062 | 73.1 | 68 | 4" MERV 8 | 4" MERV 8 | 24.67% | -4 | 168.5455 | 65.3415 | 52.8116 | 19.7812 | 48.5368 | 19.7812 | 4.2747 | 0 | 29412.1921 | 11402.4818 | 2.9578 | 1.8735 | 21.3859 | 5.2516 | 29055.897 | 7320.9599 | 1.3706 | 0.10577 | 12.5308 | 0.24366 | 32.6273 | 6.9571 | 5.6904 | 9.9933 | 1.1936 | 1.0263 | 145.1 | 36.2 | 72.55 | 18.1 | 0 | 217.65 | 54.3 | 9.7768 | 2.3262 | 0 | 0 | 0 | 92.13 | 0 | 0 | 0.4749 | 0.38333 | 65.5714 | 52.7711 | 19.8469 | 48.4753 | 19.8469 | 4.2957 | 0 | 29312.7395 | 11403.916 | 2.9431 | 1.8737 | 21.2082 | 5.2527 | 28955.9208 | 7352.8261 | 1.3623 | 0.10665 | 12.4127 | 0.24674 | 32.3818 | 6.9571 | 5.7293 | 10.0329 | 1.1921 | 1.0263 | 144.7 | 36.3 | 72.35 | 18.15 | 0 | 217.05 | 54.45 | 9.7499 | 2.3351 | 0 | 3374.2143 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 57.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 91.5062 | 73.1 | 68 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8278 | 10.696 | 16.248 | 6.8977 | 17.5798 | 3.7984 | 18028.6763 | 5951.2135 | 2.1672 | 0.75645 | 9.6051 | 1.1067 | 18485.9846 | 5981.1064 | 0.78864 | 0.093268 | 4.5874 | 0.17553 | 22.2 | 4 | 5.3547 | 9.4409 | 1.1997 | 1.0358 | 76.9 | 20.5 | 38.45 | 10.25 | 0 | 115.35 | 30.75 | 7.8551 | 3.1463 | 0 | 92.13 | 92.13 | 83.5062 | 83.5062 | 3762.2143 | 3762.2143 | 3937.8505 | 0 | 40.5964 | 3937.8505 | 83.5062 | 92.13 | 519.4065 | 3242.8078
|  | CL | 95.7912 | 34 | 70 | 59.52 | 30.12% | 0.011411 | 35.58 | 805.4382 | 63.3 | 150.9584 | 201.2779 | 19.9313 | 24.67% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 0.32711 | 0.26169 | 59 | 1259.52 | 1854 | 78 | 78 | 19.9313 | 59 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 95.7912 | 73.1 | 70 | 4" MERV 8 | 4" MERV 8 | 24.67% | -4 | 168.5455 | 65.3463 | 52.8095 | 19.7824 | 48.5346 | 19.7824 | 4.2749 | 0 | 29407.0949 | 11401.3445 | 2.957 | 1.8734 | 21.3767 | 5.2508 | 29031.0966 | 9458.4927 | 1.3685 | 0.16898 | 12.5015 | 0.50292 | 32.6 | 7.1857 | 5.696 | 9.6815 | 1.1934 | 1.0271 | 145 | 43.7 | 72.5 | 21.85 | 0 | 217.5 | 65.55 | 9.7711 | 2.812 | 0 | 0 | 0 | 27.4367 | 0 | 0 | 0.40348 | 1.4333 | 65.5714 | 52.7698 | 19.8467 | 48.4744 | 19.8467 | 4.2954 | 0 | 29309.7388 | 11402.7486 | 2.9427 | 1.8736 | 21.2028 | 5.252 | 28933.2873 | 9496.648 | 1.3605 | 0.1703 | 12.3861 | 0.50889 | 32.3545 | 7.1857 | 5.7341 | 9.7155 | 1.192 | 1.0271 | 144.6 | 43.9 | 72.3 | 21.95 | 0 | 216.9 | 65.85 | 9.7446 | 2.8223 | 0 | 1221.5714 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 59 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 95.7912 | 73.1 | 70 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8273 | 10.696 | 16.2476 | 6.1781 | 17.5797 | 4.5179 | 18026.8307 | 5950.6043 | 2.1669 | 0.75646 | 9.6028 | 1.1066 | 18471.767 | 6020.528 | 0.78764 | 0.094536 | 4.5781 | 0.17909 | 22.2 | 4.4 | 5.3571 | 8.6173 | 1.1996 | 1.0392 | 76.9 | 21.4 | 38.45 | 10.7 | 0 | 115.35 | 32.1 | 7.8501 | 3.2806 | 0 | 27.4367 | 27.4367 | 36.5548 | 36.5548 | 1371.1714 | 1371.1714 | 1435.1629 | 4.9738e-14 | 42.2107 | 1435.1629 | 36.5548 | 27.4367 | 182.1407 | 1189.0308
|  | CM | 99.7083 | 24 | 72 | 61.34 | 28.52% | 0.012189 | 37.4 | 819.7083 | 64 | 152.2309 | 202.9745 | 19.9335 | 24.67% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 0.60724 | 0.48579 | 61 | 1259.52 | 1854 | 78 | 78 | 19.9335 | 61 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 99.7083 | 73.1 | 72 | 4" MERV 8 | 4" MERV 8 | 24.67% | -4 | 168.5455 | 65.3533 | 52.8059 | 19.7841 | 48.531 | 19.1829 | 4.2749 | 0.60117 | 29398.3033 | 11399.1607 | 2.9557 | 1.8733 | 21.361 | 5.2496 | 28984.6881 | 11181.6202 | 1.3647 | 0.23005 | 12.4467 | 0.80942 | 32.5364 | 7.7714 | 5.7063 | 8.9585 | 1.193 | 1.0293 | 144.9 | 50.1 | 72.45 | 25.05 | 0 | 217.35 | 75.15 | 9.7601 | 3.2197 | 0 | 0 | 0 | 16.2333 | 0 | 0 | 0.33819 | 1.6 | 65.5714 | 52.7675 | 19.8464 | 48.4727 | 19.23 | 4.2948 | 0.61638 | 29304.0121 | 11400.5206 | 2.9419 | 1.8735 | 21.1926 | 5.2507 | 28890.0932 | 11182.4389 | 1.3569 | 0.23018 | 12.3354 | 0.80993 | 32.3 | 7.7714 | 5.7433 | 8.9849 | 1.1917 | 1.0293 | 144.5 | 50.1 | 72.25 | 25.05 | 0 | 216.75 | 75.15 | 9.7347 | 3.2227 | 0 | 932.5714 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 61 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 99.7083 | 73.1 | 72 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8263 | 10.6959 | 16.2468 | 5.4533 | 17.5794 | 5.2427 | 18023.3085 | 5949.4416 | 2.1664 | 0.75644 | 9.5985 | 1.1063 | 18444.6281 | 6056.8175 | 0.78574 | 0.095646 | 4.5603 | 0.18229 | 22.2 | 4.7 | 5.3616 | 7.9222 | 1.1994 | 1.0427 | 76.8 | 22 | 38.4 | 11 | 0 | 115.2 | 33 | 7.8405 | 3.3723 | 0 | 16.2333 | 16.2333 | 31.1819 | 31.1819 | 1045.3714 | 1045.3714 | 1092.7867 | 3.1974e-14 | 45.5328 | 1092.7867 | 31.1819 | 16.2333 | 128.6785 | 916.693
|  | CN | 103.8875 | 8 | 74 | 63.09 | 26.77% | 0.012983 | 39.31 | 831.1375 | 64.6 | 153.1348 | 204.1798 | 19.9358 | 24.68% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 0.90123 | 0.72098 | 63 | 1259.52 | 1854 | 78 | 78 | 19.9358 | 63 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 103.8875 | 73.1 | 74 | 4" MERV 8 | 4" MERV 8 | 24.68% | -4 | 168.5455 | 65.3609 | 52.8021 | 19.7859 | 48.5271 | 17.8368 | 4.275 | 1.9492 | 29388.926 | 11396.8378 | 2.9543 | 1.8733 | 21.3442 | 5.2483 | 28935.3225 | 11248.8626 | 1.3606 | 0.23288 | 12.3885 | 0.8243 | 32.4727 | 8.4857 | 5.7174 | 8.2002 | 1.1927 | 1.032 | 144.7 | 51.6 | 72.35 | 25.8 | 0 | 217.05 | 77.4 | 9.7487 | 3.3166 | 0 | 0 | 0 | 4.2967 | 0 | 0 | 0.26854 | 1.8667 | 65.5714 | 52.7651 | 19.8461 | 48.4708 | 17.8824 | 4.2942 | 1.9637 | 29297.92 | 11398.1506 | 2.941 | 1.8734 | 21.1818 | 5.2494 | 28844.1336 | 11249.6432 | 1.3532 | 0.23301 | 12.2816 | 0.82481 | 32.2455 | 8.4857 | 5.7531 | 8.2237 | 1.1913 | 1.032 | 144.3 | 51.6 | 72.15 | 25.8 | 0 | 216.45 | 77.4 | 9.7239 | 3.3195 | 0 | 339.4286 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 63 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 103.8875 | 73.1 | 74 | 4" MERV 8 | 4" MERV 8 | 33.01% | 0 | 111.24 | 36.72 | 33.8252 | 10.6959 | 16.2461 | 4.7179 | 17.5792 | 5.978 | 18019.5616 | 5948.2048 | 2.1658 | 0.75641 | 9.594 | 1.1061 | 18415.7597 | 6093.6442 | 0.78372 | 0.096825 | 4.5415 | 0.18566 | 22.2 | 5.1 | 5.3664 | 7.3227 | 1.1992 | 1.0462 | 76.7 | 22.8 | 38.35 | 11.4 | 0 | 115.05 | 34.2 | 7.8304 | 3.4851 | 0 | 4.2967 | 4.2967 | 12.2755 | 12.2755 | 380.2286 | 380.2286 | 396.8007 | 1.5099e-14 | 49.6001 | 396.8007 | 12.2755 | 4.2967 | 42.9313 | 337.2973
|  | CO |  | 0
|  |  | total | 2395 | hours | [195 empty] | Ventilation MLC component | Generator MLC component | UPS room MLC component | ITE room MLC component
[201 empty] | 0.011027 | 0.019634 | 0.011854 | 0.060827

## 50% Bins
[196 empty] | NO | selected | Resulting | Resulting | Ventilation | Gen | UPS | ITE
| Notes on this 90.4 MLC calculation: | 2°F dry bulb bins (for hours equal or below 65°F dry bulb) | [7 empty] | Annual HW demand of cafeteria: |  |  |  | ITE zone | ITE zone | Properties of IT equipment zone: | [5 empty] | Properties for generic ventilation air handlers. | [17 empty] | Information used for hourly inputs for ITE room IDEC units (shown with heat recovery input) | [27 empty] | Outputs for ITE room IDEC units with heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | HR export |  | Generator room | [19 empty] | Outputs for ITE room IDEC units without heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | Without HR | UPS room variables | [13 empty] | Information used for hourly inputs for UPS room IDEC units | [27 empty] | Outputs for UPS units. NOTE: most of the performance values are PER UNIT | [18 empty] | Generator Room |  | Ventilation system |  | ITE and UPS cooling |  | Recovery | recovery | Mechanical | Mechanical | system | room | room | room
1. | This tab shows performance when data center is 50% loaded. There are two | bin | Outdoor | bin | average |  |  |  | Psychrometry for averaged points: | café avg | entering | kw from | H2O heater | delta T | % desigm | Temp | AHU | Min | Max | min. | max. | control | heat | liquid | Cooling | DX split | room air | Project | Design | Design | Reset | Resulting | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | energy avoided | Room heat | engine block | Recovery | Recovery | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | error | ITE cooling | UPS room | Battery | Project | Design | Design | Design | Alternate | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | with | without | with | without | with | without | whatsoever | savings | Input | energy | HVAC | HVAC | cooling | cooling
| traditional modeling methods that I used here to determine the MLC. | name | dry bulb | hours | °F wb | dewpoint | %rh | moisture | enthalpy | 140 | temp | hot aisle | input energy | w/ HR | w/ HR | into ITE | SAT: | moisture | moisture | enthalpy | enthalpy | mode | power | added | needed | kW input: | dew point | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | elsewhere | need, kWh | heat, kWh | Potential | Savings | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | annual kWh | temp | temp | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | recovery | recovery | recovery | recovery | recovery | recovery | at all | kWh: | Power | incl. Recov | Component | component | component | component
|  | AB | 65 | 378 | 51.8048 | 40.53 | 40.64% | 0.0055757 | 21.66 | 831.6052 | 61.7 | 106.0761 | 141.4348 | 19.9644 | 49.43% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 4.8796 | 0.60695 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9644 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 65 | 73.1 | 51.8048 | 4" MERV 8 | 4" MERV 8 | 49.43% | -1 | 168.5455 | 91.6368 | 52.8024 | 27.3749 | 48.5146 | 27.3749 | 4.2878 | 0 | 29389.6484 | 15978.9151 | 2.9544 | 1.4653 | 21.3455 | 5.7558 | 29207.0033 | 3933.2731 | 1.383 | 0.032772 | 12.7107 | 0.04056 | 32.7636 | 6.51 | 5.6671 | 14.7888 | 1.1944 | 1.0351 | 145.6 | 29.5 | 72.8 | 14.75 | 0 | 218.4 | 44.25 | 9.81 | 2.712 | 0 | 0 | 0 | 693 | 0 | 0 | 168.5455 | 91.8 | 52.7818 | 27.4216 | 48.4834 | 27.4216 | 4.2984 | 0 | 29339.2726 | 15979.9339 | 2.947 | 1.4655 | 21.2555 | 5.7569 | 29156.0382 | 3941.8907 | 1.3788 | 0.032905 | 12.6498 | 0.040815 | 32.6364 | 6.51 | 5.6868 | 14.8181 | 1.1936 | 1.0351 | 145.4 | 29.6 | 72.7 | 14.8 | 0 | 218.1 | 44.4 | 9.7961 | 2.7167 | 0 | 12303.9 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 65 | 75 | 51.8048 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8525 | 18.946 | 14.1507 | 18.946 | 19.7018 | 0 | 18044.9953 | 10424.0507 | 2.1898 | 1.146 | 9.7138 | 2.9367 | 18747.7842 | 6453.6167 | 0.80802 | 0.10472 | 4.7667 | 0.21266 | 23.6 | 3.6 | 5.049 | 18.6954 | 1.2119 | 1.032 | 79.7 | 24.2 | 39.85 | 12.1 | 0 | 119.55 | 36.3 | 8.1341 | 3.7029 | 0 | 693 | 693 | 627.1905 | 2151.9775 | 21047.04 | 21047.04 | 23892.0175 | 0 | 63.2064 | 23892.0175 | 2151.9775 | 693 | 1908.5046 | 19138.5354
2. | A 2°F bin hour-grouping method is shown on each of these 25%, 50%, 75% | AC | 63 | 251 | 50.3876 | 39.11 | 41.23% | 0.0052714 | 20.85 | 802.9781 | 61 | 103.3402 | 137.7869 | 19.9643 | 49.43% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 5.7563 | 0.74173 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9643 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 63 | 73.1 | 50.3876 | 4" MERV 8 | 4" MERV 8 | 49.43% | -1 | 168.5455 | 91.636 | 52.8025 | 27.3747 | 48.5147 | 27.3747 | 4.2877 | 0 | 29389.9076 | 15978.9099 | 2.9545 | 1.4653 | 21.346 | 5.7558 | 29207.2574 | 3788.0311 | 1.3831 | 0.030508 | 12.711 | 0.036364 | 32.7636 | 6.5 | 5.667 | 14.797 | 1.1944 | 1.0351 | 145.6 | 29 | 72.8 | 14.5 | 0 | 218.4 | 43.5 | 9.81 | 2.66 | 0 | 0 | 0 | 476.9 | 0 | 0 | 168.5455 | 91.8 | 52.7818 | 27.4216 | 48.4834 | 27.4216 | 4.2984 | 0 | 29339.2726 | 15979.9339 | 2.947 | 1.4655 | 21.2555 | 5.7569 | 29156.0382 | 3796.2682 | 1.3788 | 0.030632 | 12.6498 | 0.036591 | 32.6364 | 6.5 | 5.6868 | 14.8264 | 1.1936 | 1.0351 | 145.4 | 29 | 72.7 | 14.5 | 0 | 218.1 | 43.5 | 9.7961 | 2.6647 | 0 | 13052 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 63 | 75 | 50.3876 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8525 | 18.946 | 14.1507 | 18.946 | 19.7018 | 0 | 18044.9953 | 10424.0507 | 2.1898 | 1.146 | 9.7138 | 2.9367 | 18747.7842 | 5827.1461 | 0.80802 | 0.086011 | 4.7667 | 0.15771 | 23.6 | 3.5 | 5.049 | 18.9496 | 1.2119 | 1.0316 | 79.7 | 22.9 | 39.85 | 11.45 | 0 | 119.55 | 34.35 | 8.1341 | 3.5029 | 0 | 476.9 | 476.9 | 454.6091 | 1649.0094 | 13930.5 | 13930.5 | 16056.4094 | 0 | 63.9698 | 16056.4094 | 1649.0094 | 476.9 | 1267.2874 | 12663.2126
| and 100% load scenario tabs. The bin-group calculation method was | AD | 61 | 308 | 49.6315 | 39.36 | 44.69% | 0.0053243 | 20.42 | 835.6529 | 60.3 | 108.4983 | 144.6643 | 19.9612 | 49.42% | 77.9263 | 77.5263 | 0.006946 | 0.013892 | 26.1505 | 33.4369 | Heat-Hum | 6.2024 | 0.71832 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.9263 | 19.9612 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 61 | 73.1 | 49.6315 | 4" MERV 8 | 4" MERV 8 | 49.42% | -1 | 168.5455 | 91.6221 | 52.8042 | 27.3706 | 48.5174 | 27.3706 | 4.2868 | 0 | 29394.1862 | 15976.7116 | 2.9551 | 1.4651 | 21.3536 | 5.755 | 29211.5857 | 3735.5319 | 1.3834 | 0.029623 | 12.7162 | 0.03482 | 32.7727 | 6.5 | 5.6654 | 14.8003 | 1.1944 | 1.0351 | 145.6 | 28.3 | 72.8 | 14.15 | 0 | 218.4 | 42.45 | 9.8111 | 2.599 | 0 | 0 | 0 | 605.7333 | 0 | 0 | 168.5455 | 91.8 | 52.7818 | 27.4214 | 48.4834 | 27.4214 | 4.2984 | 0 | 29339.2726 | 15977.822 | 2.947 | 1.4653 | 21.2555 | 5.7561 | 29156.0382 | 3744.266 | 1.3788 | 0.029753 | 12.6498 | 0.035054 | 32.6364 | 6.5 | 5.6868 | 14.8322 | 1.1936 | 1.0351 | 145.4 | 28.3 | 72.7 | 14.15 | 0 | 218.1 | 42.45 | 9.7961 | 2.6039 | 0 | 16016 | 85.2261 | 64.2261 | 1259.52 | 111.24 | 65 | 64.2261 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 61 | 75 | 49.6315 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8525 | 18.9451 | 14.1507 | 18.9451 | 19.7018 | 0 | 18044.9953 | 10409.2674 | 2.1898 | 1.1444 | 9.7138 | 2.9327 | 18747.7842 | 5900.2372 | 0.80802 | 0.087784 | 4.7667 | 0.16298 | 23.6 | 3.5 | 5.049 | 18.9609 | 1.2119 | 1.0316 | 79.7 | 22 | 39.85 | 11 | 0 | 119.55 | 33 | 8.1341 | 3.3716 | 0 | 605.7333 | 605.7333 | 581.6621 | 2160.8832 | 17094 | 17094 | 19860.6165 | 0 | 64.4825 | 19860.6165 | 2160.8832 | 605.7333 | 1555.0778 | 15538.9222
| attractive to me because it required only 49 iterations of inputs & outputs per | AE | 59 | 266 | 47.9132 | 37.22 | 44.14% | 0.0048929 | 19.47 | 714.9389 | 59.7 | 93.524 | 124.6986 | 19.9655 | 49.43% | 77.5826 | 77.1826 | 0.006946 | 0.013892 | 26.0673 | 33.3537 | Heat-Hum | 7.1406 | 0.90941 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.5826 | 19.9655 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 59 | 73.1 | 47.9132 | 4" MERV 8 | 4" MERV 8 | 49.43% | -1 | 168.5455 | 91.6415 | 52.8018 | 27.3753 | 48.5137 | 27.3753 | 4.2881 | 0 | 29388.2016 | 15966.9847 | 2.9542 | 1.4643 | 21.3429 | 5.7517 | 29205.5403 | 3640.3211 | 1.3829 | 0.028181 | 12.7089 | 0.032281 | 32.7545 | 6.49 | 5.6677 | 14.8217 | 1.1943 | 1.035 | 145.6 | 27.9 | 72.8 | 13.95 | 0 | 218.4 | 41.85 | 9.8096 | 2.5598 | 0 | 0 | 215.9033 | 532 | 0 | 0 | 168.5455 | 91.8 | 52.7818 | 27.4207 | 48.4834 | 27.4207 | 4.2984 | 0 | 29339.2726 | 15967.9743 | 2.947 | 1.4644 | 21.2555 | 5.7528 | 29156.0382 | 3647.8114 | 1.3788 | 0.02829 | 12.6498 | 0.032472 | 32.6364 | 6.49 | 5.6868 | 14.8503 | 1.1936 | 1.035 | 145.4 | 27.9 | 72.7 | 13.95 | 0 | 218.1 | 41.85 | 9.7961 | 2.5641 | 0 | 13810.72 | 81.6176 | 60.6176 | 1259.52 | 111.24 | 65 | 60.6176 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 59 | 75 | 47.9132 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8525 | 18.9408 | 14.1507 | 18.9408 | 19.7018 | 0 | 18044.9953 | 10340.3334 | 2.1898 | 1.1372 | 9.7138 | 2.9142 | 18747.7842 | 7142.9796 | 0.80802 | 0.12621 | 4.7667 | 0.28367 | 23.6 | 3.6 | 5.049 | 18.5696 | 1.2119 | 1.0322 | 79.7 | 22.8 | 39.85 | 11.4 | 0 | 119.55 | 34.2 | 8.1341 | 3.4857 | 0 | 532 | 532 | 545.5999 | 2115.7731 | 14768.32 | 14768.32 | 17416.0931 | 0 | 65.474 | 17416.0931 | 2115.7731 | 532 | 1343.0217 | 13425.2983
| zone per scenario for the manufacturer's tool, as opposed to 8760 iterations | AF | 57 | 282 | 46.766 | 36.61 | 46.29% | 0.0047757 | 18.85 | 766.1761 | 59 | 101.1002 | 134.8003 | 19.9614 | 49.42% | 77.3532 | 76.9532 | 0.006946 | 0.013892 | 26.0118 | 33.2982 | Heat-Hum | 7.7515 | 0.9613 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.3532 | 19.9614 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 57 | 73.1 | 46.766 | 4" MERV 8 | 4" MERV 8 | 49.42% | -1 | 168.5455 | 91.6226 | 52.8041 | 27.3694 | 48.5173 | 27.3694 | 4.2869 | 0 | 29394.0324 | 15960.2924 | 2.9551 | 1.4637 | 21.3533 | 5.7494 | 29211.4379 | 3585.9237 | 1.3834 | 0.027317 | 12.716 | 0.030824 | 32.7727 | 6.49 | 5.6654 | 14.8297 | 1.1944 | 1.035 | 145.6 | 27.3 | 72.8 | 13.65 | 0 | 218.4 | 40.95 | 9.8111 | 2.5095 | 0 | 0 | 686.67 | 564 | 0 | 0 | 168.5455 | 91.8 | 52.7818 | 27.4202 | 48.4834 | 27.4202 | 4.2984 | 0 | 29339.2726 | 15961.3997 | 2.947 | 1.4639 | 21.2555 | 5.7505 | 29156.0382 | 3594.1009 | 1.3788 | 0.027434 | 12.6498 | 0.031026 | 32.6364 | 6.49 | 5.6868 | 14.8618 | 1.1936 | 1.035 | 145.4 | 27.4 | 72.7 | 13.7 | 0 | 218.1 | 41.1 | 9.7961 | 2.5141 | 0 | 14641.44 | 79.2085 | 58.2085 | 1259.52 | 111.24 | 65 | 58.2085 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 57 | 75 | 46.766 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8525 | 18.938 | 14.1507 | 18.938 | 19.7018 | 0 | 18044.9953 | 10294.3114 | 2.1898 | 1.1324 | 9.7138 | 2.9019 | 18747.7842 | 8189.8224 | 0.80802 | 0.16339 | 4.7667 | 0.42107 | 23.6 | 3.7 | 5.049 | 18.0706 | 1.2119 | 1.0331 | 79.7 | 22.8 | 39.85 | 11.4 | 0 | 119.55 | 34.2 | 8.1341 | 3.4969 | 0 | 564 | 564 | 608.2799 | 2415.3216 | 15684.84 | 15684.84 | 18664.1616 | -1.819e-12 | 66.185 | 18664.1616 | 2415.3216 | 564 | 1423.805 | 14261.035
| per zone per scenario... even though that is possible. I did use the full 8760 | AG | 55 | 284 | 45.3053 | 35.21 | 47.08% | 0.0045143 | 18.09 | 781.6099 | 58.4 | 103.9008 | 138.5343 | 19.9588 | 49.41% | 77.0611 | 76.6611 | 0.006946 | 0.013892 | 25.9411 | 33.2275 | Heat-Hum | 8.4976 | 1.0771 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.0611 | 19.9588 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 55 | 73.1 | 45.3053 | 4" MERV 8 | 4" MERV 8 | 49.41% | -1 | 168.5455 | 91.6111 | 52.8056 | 27.3655 | 48.5195 | 27.3655 | 4.2861 | 0 | 29397.6031 | 15951.8493 | 2.9556 | 1.4629 | 21.3597 | 5.7464 | 29215.0407 | 3520.6221 | 1.3837 | 0.026327 | 12.7203 | 0.029165 | 32.7818 | 6.48 | 5.6641 | 14.8418 | 1.1945 | 1.035 | 145.6 | 26.8 | 72.8 | 13.4 | 0 | 218.4 | 40.2 | 9.8121 | 2.4665 | 0 | 0 | 1152.5667 | 568 | 0 | 0 | 168.5455 | 91.8 | 52.7818 | 27.4195 | 48.4834 | 27.4195 | 4.2984 | 0 | 29339.2726 | 15953.0286 | 2.947 | 1.4631 | 21.2555 | 5.7477 | 29156.0382 | 3529.0804 | 1.3788 | 0.026446 | 12.6498 | 0.029367 | 32.6364 | 6.48 | 5.6868 | 14.876 | 1.1936 | 1.035 | 145.4 | 26.9 | 72.7 | 13.45 | 0 | 218.1 | 40.35 | 9.7961 | 2.4714 | 0 | 14722.56 | 76.1411 | 55.1411 | 1259.52 | 111.24 | 65 | 55.1411 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 55 | 75 | 45.3053 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8525 | 18.9348 | 14.1507 | 18.9348 | 19.7018 | 0 | 18044.9953 | 10235.7139 | 2.1898 | 1.1269 | 9.7138 | 2.8877 | 18747.7842 | 9882.3889 | 0.80802 | 0.2335 | 4.7667 | 0.7261 | 23.6 | 3.9 | 5.049 | 16.9633 | 1.2119 | 1.0353 | 79.7 | 23.6 | 39.85 | 11.8 | 0 | 119.55 | 35.4 | 8.1341 | 3.6129 | 0 | 584.5667 | 584.5667 | 649.3181 | 2644.326 | 15830.16 | 15830.16 | 19059.0527 | 0 | 67.1093 | 19059.0527 | 2644.326 | 584.5667 | 1433.9029 | 14396.2571
| annual hour calculation method to sychronize the data center operation with | AH | 53 | 273 | 44.43 | 35.38 | 51% | 0.0045457 | 17.64 | 813.6319 | 57.7 | 109.0853 | 145.4471 | 19.9552 | 49.4% | 76.886 | 76.486 | 0.0066891 | 0.013378 | 25.6292 | 32.6461 | Heat-Hum | 8.647 | 0.94937 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.886 | 19.9552 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 53 | 73.1 | 44.43 | 4" MERV 8 | 4" MERV 8 | 49.4% | -1 | 168.5455 | 91.5942 | 52.8085 | 27.3604 | 48.5233 | 27.3604 | 4.2852 | 0 | 29404.6348 | 15947.7031 | 2.9566 | 1.4625 | 21.3723 | 5.7453 | 29233.9085 | 3489.8309 | 1.3853 | 0.0258 | 12.7429 | 0.028332 | 32.8091 | 6.48 | 5.6592 | 14.8455 | 1.1947 | 1.035 | 145.7 | 26.3 | 72.85 | 13.15 | 0 | 218.55 | 39.45 | 9.8167 | 2.4127 | 0 | 0 | 1551.095 | 546 | 0 | 0 | 168.5455 | 91.8 | 52.7826 | 27.4193 | 48.484 | 27.4193 | 4.2986 | 0 | 29341.0671 | 15948.9881 | 2.9473 | 1.4628 | 21.2587 | 5.7466 | 29169.5822 | 3498.8974 | 1.3799 | 0.025927 | 12.6659 | 0.028545 | 32.6545 | 6.48 | 5.6839 | 14.8828 | 1.1937 | 1.0349 | 145.4 | 26.3 | 72.7 | 13.15 | 0 | 218.1 | 39.45 | 9.7993 | 2.4178 | 0 | 14152.32 | 74.3031 | 53.3031 | 1259.52 | 111.24 | 65 | 53.3031 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 53 | 75 | 44.43 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8529 | 18.934 | 14.1509 | 18.934 | 19.7019 | 0 | 18046.099 | 10221.7384 | 2.1899 | 1.1254 | 9.7151 | 2.8842 | 18756.3342 | 9877.3187 | 0.80863 | 0.23253 | 4.7725 | 0.7227 | 23.6 | 3.9 | 5.0477 | 17.0024 | 1.212 | 1.0352 | 79.7 | 22.2 | 39.85 | 11.1 | 0 | 119.55 | 33.3 | 8.1373 | 3.3947 | 0 | 1005.095 | 1005.095 | 631.2416 | 2582.7126 | 15217.02 | 15217.02 | 18804.8276 | 1.1369e-12 | 68.8822 | 18804.8276 | 2582.7126 | 1005.095 | 1378.011 | 13839.009
| the cafeteria heat recovery input, and to create chronological tallies of water | AI | 51 | 156 | 42.7795 | 33.57 | 51.07% | 0.0042271 | 16.81 | 860.0712 | 57 | 116.2923 | 155.0564 | 19.9503 | 49.39% | 76.5559 | 76.1559 | 0.0066891 | 0.013378 | 25.5493 | 32.5661 | Heat-Hum | 9.4589 | 1.0905 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.5559 | 19.9503 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 51 | 73.1 | 42.7795 | 4" MERV 8 | 4" MERV 8 | 49.39% | -1 | 168.5455 | 91.572 | 52.8113 | 27.3533 | 48.5275 | 27.3533 | 4.2837 | 0 | 29411.5092 | 15938.1046 | 2.9577 | 1.4617 | 21.3846 | 5.7419 | 29240.865 | 3425.8951 | 1.3859 | 0.02486 | 12.7513 | 0.026799 | 32.8273 | 6.47 | 5.6565 | 14.8569 | 1.1948 | 1.0349 | 145.7 | 25.8 | 72.85 | 12.9 | 0 | 218.55 | 38.7 | 9.8186 | 2.3747 | 0 | 0 | 1139.58 | 312 | 0 | 0 | 168.5455 | 91.8 | 52.7826 | 27.4185 | 48.484 | 27.4185 | 4.2986 | 0 | 29341.0671 | 15939.5282 | 2.9473 | 1.4619 | 21.2587 | 5.7434 | 29169.5822 | 3435.6447 | 1.3799 | 0.024993 | 12.6659 | 0.027019 | 32.6545 | 6.47 | 5.6839 | 14.8983 | 1.1937 | 1.0349 | 145.4 | 25.9 | 72.7 | 12.95 | 0 | 218.1 | 38.85 | 9.7993 | 2.3803 | 0 | 8074.56 | 70.8369 | 49.8369 | 1259.52 | 111.24 | 65 | 49.8369 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 51 | 75 | 42.7795 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8529 | 18.9324 | 14.1509 | 18.9324 | 19.7019 | 0 | 18046.099 | 10194.8895 | 2.1899 | 1.1227 | 9.7151 | 2.8771 | 18756.3342 | 9843.3335 | 0.80863 | 0.23068 | 4.7725 | 0.71449 | 23.6 | 3.9 | 5.0477 | 17.0848 | 1.212 | 1.035 | 79.7 | 21.5 | 39.85 | 10.75 | 0 | 119.55 | 32.25 | 8.1373 | 3.2925 | 0 | 827.58 | 827.58 | 382.6615 | 1602.4845 | 8682.96 | 8682.96 | 11113.0245 | 0 | 71.2373 | 11113.0245 | 1602.4845 | 827.58 | 787.4348 | 7895.5252
| & potential fuel oil use, in order to calculate the tank sizes you see at top of | AJ | 49 | 258 | 41.8876 | 33.83 | 55.6% | 0.0042714 | 16.37 | 838.0965 | 56.4 | 114.1402 | 152.187 | 19.9493 | 49.39% | 76.3775 | 75.9775 | 0.0066891 | 0.013378 | 25.5061 | 32.523 | Heat-Hum | 9.8884 | 1.0709 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.3775 | 19.9493 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 49 | 73.1 | 41.8876 | 4" MERV 8 | 4" MERV 8 | 49.39% | -1 | 168.5455 | 91.5671 | 52.8119 | 27.3515 | 48.5285 | 27.3515 | 4.2834 | 0 | 29413.0315 | 15932.9622 | 2.9579 | 1.4612 | 21.3874 | 5.7401 | 29242.3966 | 3398.4237 | 1.386 | 0.024394 | 12.7531 | 0.026086 | 32.8273 | 6.47 | 5.6559 | 14.8641 | 1.1948 | 1.0349 | 145.7 | 25.3 | 72.85 | 12.65 | 0 | 218.55 | 37.95 | 9.8189 | 2.3229 | 0 | 0 | 2303.51 | 516 | 0 | 0 | 168.5455 | 91.8 | 52.7826 | 27.4181 | 48.484 | 27.4181 | 4.2986 | 0 | 29341.0671 | 15934.4165 | 2.9473 | 1.4615 | 21.2587 | 5.7417 | 29169.5822 | 3408.2336 | 1.3799 | 0.024527 | 12.6659 | 0.026304 | 32.6545 | 6.47 | 5.6839 | 14.9065 | 1.1937 | 1.0349 | 145.4 | 25.3 | 72.7 | 12.65 | 0 | 218.1 | 37.95 | 9.7993 | 2.3284 | 0 | 13354.08 | 68.964 | 47.964 | 1259.52 | 111.24 | 65 | 47.964 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 49 | 75 | 41.8876 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8529 | 18.9315 | 14.1509 | 18.9315 | 19.7019 | 0 | 18046.099 | 10180.3416 | 2.1899 | 1.1212 | 9.7151 | 2.8733 | 18756.3342 | 9825.2334 | 0.80863 | 0.22917 | 4.7725 | 0.7085 | 23.6 | 3.9 | 5.0477 | 17.1356 | 1.212 | 1.0349 | 79.7 | 20.1 | 39.85 | 10.05 | 0 | 119.55 | 30.15 | 8.1373 | 3.0746 | 0 | 1787.51 | 1787.51 | 652.0697 | 2761.0721 | 14360.28 | 14360.28 | 18908.8621 | 0 | 73.2902 | 18908.8621 | 2761.0721 | 1787.51 | 1302.2961 | 13057.9839
| the Summary tab. | AK | 47 | 418 | 40.4057 | 32.57 | 56.99% | 0.00406 | 15.66 | 813.2045 | 55.7 | 111.6775 | 148.9034 | 19.9482 | 49.39% | 76.0811 | 75.6811 | 0.0066891 | 0.013378 | 25.4344 | 32.4512 | Heat-Hum | 10.5792 | 1.1645 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.0811 | 19.9482 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 47 | 73.1 | 40.4057 | 4" MERV 8 | 4" MERV 8 | 49.39% | -1 | 168.5455 | 91.5624 | 52.8125 | 27.3495 | 48.5294 | 27.3495 | 4.2831 | 0 | 29414.4788 | 15924.4401 | 2.9581 | 1.4605 | 21.39 | 5.7372 | 29243.862 | 3350.9302 | 1.3861 | 0.023688 | 12.7549 | 0.024977 | 32.8364 | 6.46 | 5.6553 | 14.8766 | 1.1948 | 1.0349 | 145.7 | 24.8 | 72.85 | 12.4 | 0 | 218.55 | 37.2 | 9.8193 | 2.2831 | 0 | 0 | 4410.5967 | 836 | 0 | 0 | 168.5455 | 91.8 | 52.7826 | 27.4175 | 48.484 | 27.4175 | 4.2986 | 0 | 29341.0671 | 15925.9236 | 2.9473 | 1.4608 | 21.2587 | 5.7388 | 29169.5822 | 3360.6982 | 1.3799 | 0.023818 | 12.6659 | 0.025188 | 32.6545 | 6.46 | 5.6839 | 14.9199 | 1.1937 | 1.0348 | 145.4 | 24.9 | 72.7 | 12.45 | 0 | 218.1 | 37.35 | 9.7993 | 2.2887 | 0 | 21602.24 | 65.8521 | 44.8521 | 1259.52 | 111.24 | 65 | 44.8521 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 47 | 75 | 40.4057 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8529 | 18.9301 | 14.1509 | 18.9301 | 19.7019 | 0 | 18046.099 | 10156.3894 | 2.1899 | 1.1187 | 9.7151 | 2.867 | 18756.3342 | 9795.2875 | 0.80863 | 0.22743 | 4.7725 | 0.70098 | 23.6 | 3.9 | 5.0477 | 17.2108 | 1.212 | 1.0348 | 79.7 | 19.2 | 39.85 | 9.6 | 0 | 119.55 | 28.8 | 8.1373 | 2.946 | 0 | 3574.5967 | 3574.5967 | 1106.5044 | 4762.1235 | 23232.44 | 23232.44 | 31569.1601 | 0 | 75.5243 | 31569.1601 | 4762.1235 | 3574.5967 | 2109.9215 | 21122.5185
|  | AL | 45 | 287 | 39.3812 | 32.57 | 61.48% | 0.00406 | 15.18 | 824.6775 | 55.1 | 114.0592 | 152.0789 | 19.9448 | 49.38% | 75.8762 | 75.4762 | 0.006485 | 0.01297 | 25.1706 | 31.9734 | Heat-Hum | 10.8133 | 1.0741 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.8762 | 19.9448 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 45 | 73.1 | 39.3812 | 4" MERV 8 | 4" MERV 8 | 49.38% | -1 | 168.5455 | 91.5465 | 52.8151 | 27.3447 | 48.5329 | 27.3447 | 4.2822 | 0 | 29420.9589 | 15919.3178 | 2.9591 | 1.46 | 21.4016 | 5.7357 | 29260.6732 | 3323.4853 | 1.3875 | 0.023236 | 12.775 | 0.0243 | 32.8636 | 6.46 | 5.6509 | 14.8815 | 1.195 | 1.0348 | 145.8 | 24.3 | 72.9 | 12.15 | 0 | 218.7 | 36.45 | 9.8235 | 2.2345 | 0 | 0 | 3494.225 | 574 | 0 | 0 | 168.5455 | 91.8 | 52.7832 | 27.4171 | 48.4845 | 27.4171 | 4.2987 | 0 | 29342.6315 | 15920.9004 | 2.9475 | 1.4603 | 21.2615 | 5.7373 | 29181.3729 | 3333.7477 | 1.3809 | 0.023372 | 12.68 | 0.024517 | 32.6636 | 6.46 | 5.6814 | 14.9277 | 1.1938 | 1.0348 | 145.5 | 24.4 | 72.75 | 12.2 | 0 | 218.25 | 36.6 | 9.802 | 2.2403 | 0 | 14832.16 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 45 | 75 | 39.3812 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8531 | 18.9345 | 14.1512 | 18.9345 | 19.702 | 0 | 18047.0612 | 10234.1901 | 2.1901 | 1.1262 | 9.7163 | 2.8863 | 18763.7881 | 6334.2761 | 0.80916 | 0.098563 | 4.7775 | 0.19645 | 23.6 | 3.5 | 5.0465 | 19.2289 | 1.212 | 1.0311 | 79.7 | 16.7 | 39.85 | 8.35 | 0 | 119.55 | 25.05 | 8.1401 | 2.5583 | 0 | 2920.225 | 2920.225 | 771.3732 | 3336.8664 | 15836.66 | 15836.66 | 22093.7514 | 0 | 76.9817 | 22093.7514 | 3336.8664 | 2920.225 | 1448.3542 | 14388.3058
3. | At least one manufacturer of IDEC cooling equipment maintains a | AM | 43 | 392 | 37.6204 | 30.82 | 61.46% | 0.0037586 | 14.37 | 813.3023 | 54.4 | 113.4134 | 151.2178 | 19.9425 | 49.37% | 75.5241 | 75.1241 | 0.006485 | 0.01297 | 25.0854 | 31.8881 | Heat-Hum | 11.5977 | 1.2076 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.5241 | 19.9425 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 43 | 73.1 | 37.6204 | 4" MERV 8 | 4" MERV 8 | 49.37% | -1 | 168.5455 | 91.5362 | 52.8164 | 27.341 | 48.5349 | 27.341 | 4.2816 | 0 | 29424.147 | 15909.1615 | 2.9595 | 1.4592 | 21.4073 | 5.7322 | 29263.892 | 3274.1842 | 1.3878 | 0.022529 | 12.7789 | 0.023211 | 32.8727 | 6.45 | 5.6497 | 14.8951 | 1.195 | 1.0348 | 145.8 | 24 | 72.9 | 12 | 0 | 218.7 | 36 | 9.8243 | 2.2006 | 0 | 0 | 5408.9467 | 784 | 0 | 0 | 168.5455 | 91.8 | 52.7832 | 27.4164 | 48.4845 | 27.4164 | 4.2987 | 0 | 29342.6315 | 15910.8083 | 2.9475 | 1.4594 | 21.2615 | 5.7339 | 29181.3729 | 3284.5896 | 1.3809 | 0.022665 | 12.68 | 0.023425 | 32.6636 | 6.45 | 5.6814 | 14.9432 | 1.1938 | 1.0348 | 145.5 | 24 | 72.75 | 12 | 0 | 218.25 | 36 | 9.802 | 2.2066 | 0 | 20227.2 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 43 | 75 | 37.6204 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8531 | 18.9345 | 14.1512 | 18.9345 | 19.702 | 0 | 18047.0612 | 10234.1901 | 2.1901 | 1.1262 | 9.7163 | 2.8863 | 18763.7881 | 5715.9334 | 0.80916 | 0.080834 | 4.7775 | 0.14539 | 23.6 | 3.4 | 5.0465 | 19.4789 | 1.212 | 1.0307 | 79.7 | 16.1 | 39.85 | 8.05 | 0 | 119.55 | 24.15 | 8.1401 | 2.4668 | 0 | 4624.9467 | 4624.9467 | 1106.881 | 4865.167 | 21560 | 21560 | 31050.1136 | 0 | 79.2095 | 31050.1136 | 4865.167 | 4624.9467 | 1978.2398 | 19581.7602
| spreadsheet-based performance tool. That expert tool is what I used to | AN | 41 | 329 | 36.0012 | 29.5 | 62.46% | 0.0035343 | 13.64 | 723.9625 | 53.7 | 101.7807 | 135.7076 | 19.9459 | 49.38% | 75.2002 | 74.8002 | 0.006485 | 0.01297 | 25.007 | 31.8097 | Heat-Hum | 12.3029 | 1.3069 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.2002 | 19.9459 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 41 | 73.1 | 36.0012 | 4" MERV 8 | 4" MERV 8 | 49.38% | -1 | 168.5455 | 91.5518 | 52.8145 | 27.3447 | 48.5319 | 27.3447 | 4.2826 | 0 | 29419.3416 | 15899.9777 | 2.9588 | 1.4584 | 21.3987 | 5.7291 | 29259.0269 | 3234.7812 | 1.3874 | 0.021953 | 12.7731 | 0.022346 | 32.8545 | 6.45 | 5.6516 | 14.9119 | 1.1949 | 1.0348 | 145.8 | 23.6 | 72.9 | 11.8 | 0 | 218.7 | 35.4 | 9.8229 | 2.1646 | 0 | 0 | 5073.7283 | 658 | 0 | 0 | 168.5455 | 91.8 | 52.7832 | 27.4156 | 48.4845 | 27.4156 | 4.2987 | 0 | 29342.6315 | 15901.5277 | 2.9475 | 1.4586 | 21.2615 | 5.7307 | 29181.3729 | 3244.3605 | 1.3809 | 0.022077 | 12.68 | 0.022538 | 32.6636 | 6.44 | 5.6814 | 14.9572 | 1.1938 | 1.0348 | 145.5 | 23.6 | 72.75 | 11.8 | 0 | 218.25 | 35.4 | 9.802 | 2.1701 | 0 | 16950.08 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 41 | 75 | 36.0012 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8531 | 18.9345 | 14.1512 | 18.9345 | 19.702 | 0 | 18047.0612 | 10234.1901 | 2.1901 | 1.1262 | 9.7163 | 2.8863 | 18763.7881 | 5254.2157 | 0.80916 | 0.068619 | 4.7775 | 0.11345 | 23.6 | 3.4 | 5.0465 | 19.6385 | 1.212 | 1.0305 | 79.7 | 15.5 | 39.85 | 7.75 | 0 | 119.55 | 23.25 | 8.1401 | 2.3793 | 0 | 4415.7283 | 4415.7283 | 969.2072 | 4315.2957 | 18095 | 18068.68 | 26799.704 | 0 | 81.4581 | 26799.704 | 4315.2957 | 4415.7283 | 1660.3084 | 16408.3716
| transform each unique bin's "Input" row of data to the horizontally-adjacent | AO | 39 | 281 | 34.1466 | 27.62 | 61.86% | 0.0032371 | 12.84 | 822.8706 | 53.1 | 116.4903 | 155.3204 | 19.9349 | 49.35% | 74.8293 | 74.4293 | 0.0062436 | 0.012487 | 24.664 | 31.2135 | Heat-Hum | 12.7976 | 1.3316 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.8293 | 19.9349 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 39 | 73.1 | 34.1466 | 4" MERV 8 | 4" MERV 8 | 49.35% | -1 | 168.5455 | 91.5013 | 52.8216 | 27.3296 | 48.5421 | 27.3296 | 4.2795 | 0 | 29436.836 | 15890.0341 | 2.9614 | 1.4575 | 21.43 | 5.7259 | 29288.8592 | 3192.5232 | 1.3898 | 0.021352 | 12.8089 | 0.02145 | 32.9182 | 6.44 | 5.6426 | 14.9169 | 1.1953 | 1.0347 | 145.9 | 23.2 | 72.95 | 11.6 | 0 | 218.85 | 34.8 | 9.8305 | 2.1313 | 0 | 0 | 4789.645 | 562 | 0 | 0 | 168.5455 | 91.8 | 52.784 | 27.415 | 48.485 | 27.415 | 4.2989 | 0 | 29344.4804 | 15891.8991 | 2.9478 | 1.4578 | 21.2648 | 5.7278 | 29195.3278 | 3203.7792 | 1.3821 | 0.021496 | 12.6967 | 0.02167 | 32.6818 | 6.44 | 5.6785 | 14.9716 | 1.1939 | 1.0347 | 145.5 | 23.3 | 72.75 | 11.65 | 0 | 218.25 | 34.95 | 9.8053 | 2.1379 | 0 | 14477.12 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 39 | 75 | 34.1466 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8534 | 18.9346 | 14.1514 | 18.9346 | 19.7021 | 0 | 18048.1984 | 10234.835 | 2.1903 | 1.1263 | 9.7177 | 2.8866 | 18772.5974 | 4821.7866 | 0.80979 | 0.058031 | 4.7835 | 0.088048 | 23.6 | 3.4 | 5.0452 | 19.7655 | 1.2121 | 1.0303 | 79.8 | 15.1 | 39.9 | 7.55 | 0 | 119.7 | 22.65 | 8.1434 | 2.3168 | 0 | 4227.645 | 4227.645 | 851.8949 | 3824.7026 | 15432.52 | 15432.52 | 23484.8676 | 0 | 83.576 | 23484.8676 | 3824.7026 | 4227.645 | 1417.7 | 14014.82
| "output" line of data that you see here. They are recorded like a series of | AP | 37 | 392 | 33.0765 | 27.79 | 67.47% | 0.0032643 | 12.39 | 777.2614 | 52.4 | 110.92 | 147.8933 | 19.9347 | 49.35% | 74.6153 | 74.2153 | 0.0062436 | 0.012487 | 24.6122 | 31.1617 | Heat-Hum | 13.2286 | 1.3196 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.6153 | 19.9347 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 37 | 73.1 | 33.0765 | 4" MERV 8 | 4" MERV 8 | 49.35% | -1 | 168.5455 | 91.5002 | 52.8218 | 27.3288 | 48.5424 | 27.3288 | 4.2794 | 0 | 29437.1743 | 15883.8936 | 2.9614 | 1.4569 | 21.4306 | 5.7238 | 29289.2023 | 7809.6657 | 1.3899 | 0.09086 | 12.8093 | 0.22328 | 32.9182 | 4.98 | 5.6424 | 19.2795 | 1.1953 | 1.0269 | 145.9 | 0 | 72.95 | 0 | 0 | 218.85 | 0 | 9.8306 | 0 | 0 | 0 | 7317.9867 | 784 | 0 | 0 | 168.5455 | 91.8 | 52.784 | 27.4145 | 48.485 | 27.4145 | 4.2989 | 0 | 29344.4804 | 15885.7654 | 2.9478 | 1.4573 | 21.2648 | 5.7257 | 29195.3278 | 7828.6131 | 1.3821 | 0.091306 | 12.6967 | 0.22492 | 32.6818 | 4.99 | 5.6785 | 19.3281 | 1.1939 | 1.0269 | 145.5 | 0 | 72.75 | 0 | 0 | 218.25 | 0 | 9.8053 | 0 | 0 | 15648.64 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 37 | 75 | 33.0765 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8534 | 18.936 | 14.1514 | 18.936 | 19.7021 | 0 | 18048.1984 | 10245.0428 | 2.1903 | 1.1287 | 9.7177 | 2.8928 | 18772.5974 | 9862.3384 | 0.80979 | 0.20192 | 4.7835 | 0.62664 | 23.6 | 2.9 | 5.0452 | 22.6578 | 1.2121 | 1.0264 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1434 | 0 | 0 | 6533.9867 | 6533.9867 | 1217.6915 | 5504.4719 | 16754.08 | 16785.44 | 28823.8985 | 0 | 73.5304 | 28823.8985 | 5504.4719 | 6533.9867 | 1977.7167 | 14807.7233
| snapshots, and there are several scenes occuring in each bin. | AQ | 35 | 453 | 31.6302 | 27 | 70.36% | 0.0031443 | 11.77 | 831.0315 | 51.8 | 119.4056 | 159.2074 | 19.9257 | 49.33% | 74.326 | 73.926 | 0.0062436 | 0.012487 | 24.5422 | 31.0917 | Heat-Hum | 13.8238 | 1.3728 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.326 | 19.9257 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 35 | 73.1 | 31.6302 | 4" MERV 8 | 4" MERV 8 | 49.33% | -1 | 168.5455 | 91.4588 | 52.827 | 27.3163 | 48.5503 | 27.3163 | 4.2767 | 0 | 29450.0153 | 15875.3451 | 2.9633 | 1.4562 | 21.4537 | 5.7207 | 29302.1981 | 7491.1179 | 1.3909 | 0.083903 | 12.825 | 0.19777 | 32.9455 | 4.96 | 5.6375 | 19.3768 | 1.1955 | 1.0267 | 146 | 0 | 73 | 0 | 0 | 219 | 0 | 9.8341 | 0 | 0 | 0 | 9192.125 | 906 | 0 | 0 | 168.5455 | 91.8 | 52.784 | 27.4139 | 48.485 | 27.4139 | 4.2989 | 0 | 29344.4804 | 15877.4753 | 2.9478 | 1.4566 | 21.2648 | 5.7229 | 29195.3278 | 7511.7214 | 1.3821 | 0.084367 | 12.6967 | 0.19942 | 32.6818 | 4.96 | 5.6785 | 19.4331 | 1.1939 | 1.0268 | 145.5 | 0 | 72.75 | 0 | 0 | 218.25 | 0 | 9.8053 | 0 | 0 | 17975.04 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 35 | 75 | 31.6302 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8534 | 18.9346 | 14.1514 | 18.9346 | 19.7021 | 0 | 18048.1984 | 10234.835 | 2.1903 | 1.1263 | 9.7177 | 2.8866 | 18772.5974 | 9322.0783 | 0.80979 | 0.18081 | 4.7835 | 0.53037 | 23.6 | 2.8 | 5.0452 | 23.3825 | 1.2121 | 1.0256 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1434 | 0 | 0 | 8286.125 | 8286.125 | 1453.9183 | 6630.6893 | 19243.44 | 19243.44 | 34160.2543 | 0 | 75.4089 | 34160.2543 | 6630.6893 | 8286.125 | 2285.4736 | 16957.9664
|  | AR | 33 | 264 | 30.7235 | 27.56 | 78.25% | 0.0032286 | 11.38 | 723.7398 | 51.1 | 104.8148 | 139.7531 | 19.9308 | 49.34% | 74.1447 | 73.7447 | 0.0062436 | 0.012487 | 24.4983 | 31.0478 | Heat-Hum | 14.1984 | 1.3354 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.1447 | 19.9308 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 33 | 73.1 | 30.7235 | 4" MERV 8 | 4" MERV 8 | 49.34% | -1 | 168.5455 | 91.4824 | 52.824 | 27.3226 | 48.5458 | 27.3226 | 4.2782 | 0 | 29442.7087 | 15870.2946 | 2.9623 | 1.4558 | 21.4406 | 5.7191 | 29294.8071 | 7192.9787 | 1.3903 | 0.07763 | 12.8161 | 0.1757 | 32.9273 | 4.93 | 5.6403 | 19.4681 | 1.1954 | 1.0266 | 145.9 | 0 | 72.95 | 0 | 0 | 218.85 | 0 | 9.8321 | 0 | 0 | 0 | 5785.56 | 528 | 0 | 0 | 168.5455 | 91.8 | 52.784 | 27.4135 | 48.485 | 27.4135 | 4.2989 | 0 | 29344.4804 | 15872.2778 | 2.9478 | 1.4561 | 21.2648 | 5.7211 | 29195.3278 | 7211.3081 | 1.3821 | 0.078027 | 12.6967 | 0.17705 | 32.6818 | 4.94 | 5.6785 | 19.5213 | 1.1939 | 1.0266 | 145.5 | 0 | 72.75 | 0 | 0 | 218.25 | 0 | 9.8053 | 0 | 0 | 10433.28 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 33 | 75 | 30.7235 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8534 | 18.9346 | 14.1514 | 18.9346 | 19.7021 | 0 | 18048.1984 | 10234.835 | 2.1903 | 1.1263 | 9.7177 | 2.8866 | 18772.5974 | 8547.0706 | 0.80979 | 0.1525 | 4.7835 | 0.41014 | 23.6 | 2.7 | 5.0452 | 24.2744 | 1.2121 | 1.0247 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1434 | 0 | 0 | 5257.56 | 5257.56 | 864.4578 | 3963.1364 | 11124.96 | 11146.08 | 20366.7764 | 0 | 77.1469 | 20366.7764 | 3963.1364 | 5257.56 | 1331.9317 | 9814.1483
4. | Knowing this, it should be possible to review my calculation (for any given | AS | 31 | 424 | 29.216 | 26.62 | 81.64% | 0.00309 | 10.75 | 766.7869 | 50.4 | 111.9235 | 149.2313 | 19.9213 | 49.32% | 73.8432 | 73.4432 | 0.0060517 | 0.012103 | 24.224 | 30.5723 | Heat-Hum | 14.5835 | 1.3118 | 0 | 0 | 42.1 | 1259.52 | 1854 | 78 | 73.8432 | 19.9213 | 42.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 31 | 73.1 | 29.216 | 4" MERV 8 | 4" MERV 8 | 49.32% | -1 | 168.5455 | 91.439 | 52.8467 | 27.3123 | 48.567 | 27.3123 | 4.2797 | 0 | 29457.6588 | 15862.1733 | 2.9745 | 1.4579 | 21.5398 | 5.7277 | 29319.7434 | 6936.8462 | 1.3924 | 0.072412 | 12.8459 | 0.15806 | 33.0364 | 4.92 | 5.6237 | 19.5032 | 1.196 | 1.0266 | 146 | 0 | 73 | 0 | 0 | 219 | 0 | 9.8391 | 0 | 0 | 0 | 9980.2533 | 848 | 0 | 0 | 168.5455 | 91.8 | 52.7846 | 27.4129 | 48.4855 | 27.4129 | 4.2991 | 0 | 29345.9429 | 15864.4277 | 2.948 | 1.4554 | 21.2674 | 5.7187 | 29206.3583 | 6956.398 | 1.383 | 0.072822 | 12.7099 | 0.1594 | 32.7 | 4.92 | 5.6761 | 19.6002 | 1.194 | 1.0265 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8078 | 0 | 0 | 16688.64 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 42.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 31 | 75 | 29.216 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8537 | 18.9346 | 14.1516 | 18.9346 | 19.7021 | 0 | 18049.0979 | 10235.345 | 2.1904 | 1.1263 | 9.7188 | 2.8869 | 18779.5653 | 7885.3897 | 0.81029 | 0.13015 | 4.7882 | 0.32294 | 23.6 | 2.7 | 5.0441 | 24.9629 | 1.2121 | 1.024 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.146 | 0 | 0 | 9132.2533 | 9132.2533 | 1416.6686 | 6528.2923 | 17833.44 | 17833.44 | 33493.9856 | 0 | 78.9952 | 33493.9856 | 6528.2923 | 9132.2533 | 2138.7153 | 15694.7247
| snapshot) using your own manufacturers' tool. Punch in my input shown for | AT | 29 | 342 | 26.8234 | 23.22 | 76.28% | 0.00263 | 9.78 | 672.1513 | 49.8 | 98.7671 | 131.6894 | 19.9258 | 49.33% | 73.3647 | 72.9647 | 0.0060517 | 0.012103 | 24.1082 | 30.4564 | Heat-Hum | 15.508 | 1.5156 | 0 | 0 | 42.1 | 1259.52 | 1854 | 78 | 73.3647 | 19.9258 | 42.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 29 | 73.1 | 26.8234 | 4" MERV 8 | 4" MERV 8 | 49.33% | -1 | 168.5455 | 91.4594 | 52.8276 | 27.3145 | 48.5507 | 27.3145 | 4.2769 | 0 | 29451.302 | 15848.5858 | 2.9635 | 1.4539 | 21.456 | 5.7119 | 29313.095 | 6721.2792 | 1.3919 | 0.068159 | 12.8381 | 0.14415 | 32.9636 | 4.89 | 5.6352 | 19.6221 | 1.1956 | 1.0264 | 146 | 0 | 73 | 0 | 0 | 219 | 0 | 9.8366 | 0 | 0 | 0 | 8605.29 | 684 | 0 | 0 | 168.5455 | 91.8 | 52.7846 | 27.4118 | 48.4855 | 27.4118 | 4.2991 | 0 | 29345.9429 | 15850.7124 | 2.948 | 1.4542 | 21.2674 | 5.7141 | 29206.3583 | 6739.4909 | 1.383 | 0.068528 | 12.7099 | 0.14532 | 32.7 | 4.9 | 5.6761 | 19.6806 | 1.194 | 1.0264 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8078 | 0 | 0 | 13406.4 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 42.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 29 | 75 | 26.8234 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8537 | 18.9346 | 14.1516 | 18.9346 | 19.7021 | 0 | 18049.0979 | 10235.345 | 2.1904 | 1.1263 | 9.7188 | 2.8869 | 18779.5653 | 7308.9785 | 0.81029 | 0.11209 | 4.7882 | 0.25779 | 23.6 | 2.6 | 5.0441 | 25.505 | 1.2121 | 1.0235 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.146 | 0 | 0 | 7921.29 | 7921.29 | 1197.4929 | 5581.9213 | 14268.24 | 14295.6 | 27798.8113 | 0 | 81.2831 | 27798.8113 | 5581.9213 | 7921.29 | 1725.0959 | 12570.5041
| any line of input, you should get close to my output. | AU | 27 | 116 | 24.4672 | 19.74 | 70.89% | 0.0022257 | 8.86 | 633.0866 | 49.1 | 93.7488 | 124.9983 | 19.9244 | 49.33% | 72.8934 | 72.4934 | 0.0058452 | 0.01169 | 23.7775 | 29.9091 | Heat-Hum | 16.1458 | 1.6032 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72.8934 | 19.9244 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 27 | 73.1 | 24.4672 | 4" MERV 8 | 4" MERV 8 | 49.33% | -1 | 168.5455 | 91.4528 | 52.8456 | 27.3142 | 48.5649 | 27.3142 | 4.2807 | 0 | 29455.0985 | 15835.9705 | 2.9741 | 1.4556 | 21.5352 | 5.7191 | 29328.483 | 6524.9719 | 1.3931 | 0.06438 | 12.8565 | 0.13218 | 33.0455 | 4.89 | 5.6227 | 19.6557 | 1.1961 | 1.0264 | 146.1 | 0 | 73.05 | 0 | 0 | 219.15 | 0 | 9.8411 | 0 | 0 | 0 | 3107.06 | 232 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.4109 | 48.486 | 27.4109 | 4.2992 | 0 | 29347.6707 | 15838.1388 | 2.9483 | 1.4531 | 21.2705 | 5.7101 | 29219.3903 | 6542.4791 | 1.3841 | 0.064726 | 12.7255 | 0.13325 | 32.7091 | 4.88 | 5.6734 | 19.752 | 1.1941 | 1.0263 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 4528.64 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 27 | 75 | 24.4672 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 6812.688 | 0.81088 | 0.097551 | 4.7938 | 0.20912 | 23.6 | 2.6 | 5.0429 | 25.9229 | 1.2122 | 1.0231 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 2875.06 | 2875.06 | 418.9919 | 1967.2736 | 4839.52 | 4830.24 | 9672.5736 | 0 | 83.3843 | 9672.5736 | 1967.2736 | 2875.06 | 584.9755 | 4245.2645
|  | AV | 25 | 42 | 22.5357 | 17.51 | 69.9% | 0.0019971 | 8.13 | 752.0929 | 48.5 | 112.1066 | 149.4754 | 19.9023 | 49.27% | 72.5071 | 72.1071 | 0.0058452 | 0.01169 | 23.684 | 29.8156 | Heat-Hum | 16.8347 | 1.7044 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72.5071 | 19.9023 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 25 | 73.1 | 22.5357 | 4" MERV 8 | 4" MERV 8 | 49.27% | -1 | 168.5455 | 91.3516 | 52.8585 | 27.2844 | 48.5844 | 27.2844 | 4.2741 | 0 | 29486.5658 | 15824.2658 | 2.9787 | 1.4546 | 21.5919 | 5.7147 | 29360.3757 | 6330.1251 | 1.3958 | 0.060732 | 12.895 | 0.12097 | 33.1273 | 4.87 | 5.6105 | 19.702 | 1.1965 | 1.0263 | 146.2 | 0 | 73.1 | 0 | 0 | 219.3 | 0 | 9.8497 | 0 | 0 | 0 | 1193.15 | 84 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.4101 | 48.486 | 27.4101 | 4.2992 | 0 | 29347.6707 | 15827.0661 | 2.9483 | 1.4522 | 21.2705 | 5.7064 | 29219.3903 | 6352.0939 | 1.3841 | 0.061152 | 12.7255 | 0.12223 | 32.7091 | 4.86 | 5.6734 | 19.8165 | 1.1941 | 1.0262 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 1632.96 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 25 | 75 | 22.5357 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 6378.681 | 0.81088 | 0.085638 | 4.7938 | 0.17189 | 23.6 | 2.5 | 5.0429 | 26.2541 | 1.2122 | 1.0228 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 1109.15 | 1109.15 | 156.719 | 741.2222 | 1741.32 | 1737.96 | 3588.3322 | 0 | 85.4365 | 3588.3322 | 741.2222 | 1109.15 | 211.8015 | 1526.1585
5. | I did use generic performance data (excel formulas) for the ventilation units. | AW | 23 | 25 | 19.956 | 12.66 | 60.54% | 0.0015729 | 7.2 | 665.55 | 47.8 | 99.9655 | 133.2873 | 19.9053 | 49.28% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 17.7084 | 1.8924 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.9053 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 23 | 73.1 | 19.956 | 4" MERV 8 | 4" MERV 8 | 49.28% | -1 | 168.5455 | 91.3654 | 52.8568 | 27.2873 | 48.5817 | 27.2873 | 4.275 | 0 | 29482.2731 | 15809.8157 | 2.9781 | 1.4533 | 21.5842 | 5.7098 | 29356.017 | 6166.3348 | 1.3954 | 0.057743 | 12.8897 | 0.11204 | 33.1182 | 4.85 | 5.6122 | 19.7698 | 1.1965 | 1.0262 | 146.2 | 0 | 73.1 | 0 | 0 | 219.3 | 0 | 9.8484 | 0 | 0 | 0 | 750.7917 | 50 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 6186.9597 | 1.3841 | 0.058127 | 12.7255 | 0.11316 | 32.7091 | 4.85 | 5.6734 | 19.8826 | 1.1941 | 1.0261 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 970 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 23 | 75 | 19.956 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 5996.5961 | 0.81088 | 0.075754 | 4.7938 | 0.14294 | 23.6 | 2.5 | 5.0429 | 26.5174 | 1.2122 | 1.0226 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 700.7917 | 700.7917 | 97.0711 | 463.0462 | 1032.5 | 1032.5 | 2196.3379 | 0 | 87.8535 | 2196.3379 | 463.0462 | 700.7917 | 126.0723 | 906.4277
|  | AX | 21 | 23 | 18.4913 | 12.19 | 65.07% | 0.0015371 | 6.68 | 418.95 | 47.1 | 63.404 | 84.5386 | 19.9342 | 49.35% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 18.2712 | 1.9082 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.9342 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 21 | 73.1 | 18.4913 | 4" MERV 8 | 4" MERV 8 | 49.35% | -1 | 168.5455 | 91.4981 | 52.8234 | 27.3226 | 48.5438 | 27.3226 | 4.2796 | 0 | 29441.0385 | 15810.6445 | 2.962 | 1.4506 | 21.4376 | 5.6995 | 29314.0162 | 5984.0492 | 1.3919 | 0.054501 | 12.8392 | 0.10262 | 32.9455 | 4.84 | 5.6371 | 19.8643 | 1.1955 | 1.0261 | 146 | 0 | 73 | 0 | 0 | 219 | 0 | 9.8364 | 0 | 0 | 0 | 728.065 | 46 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5998.1241 | 1.3841 | 0.054754 | 12.7255 | 0.10334 | 32.7091 | 4.84 | 5.6734 | 19.9177 | 1.1941 | 1.0261 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 890.56 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 21 | 75 | 18.4913 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 5663.0895 | 0.81088 | 0.067591 | 4.7938 | 0.12044 | 23.6 | 2.5 | 5.0429 | 26.7258 | 1.2122 | 1.0224 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 682.065 | 682.065 | 91.5491 | 438.9473 | 948.06 | 948.06 | 2069.0723 | 0 | 89.9597 | 2069.0723 | 438.9473 | 682.065 | 115.9865 | 832.0735
6. | The most difficult task was calculating accurate wet bulb values for TMY data. | AY | 19 | 10 | 16.38 | 8.98 | 61.02% | 0.0013086 | 5.95 | 1026.315 | 46.5 | 156.3258 | 208.4345 | 19.8207 | 49.07% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 19.0613 | 2.0094 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8207 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 19 | 73.1 | 16.38 | 4" MERV 8 | 4" MERV 8 | 49.07% | -1 | 168.5455 | 90.9772 | 52.9067 | 27.1763 | 48.6571 | 27.1763 | 4.2496 | 0 | 29603.5626 | 15807.392 | 2.996 | 1.4529 | 21.8035 | 5.7072 | 29478.9461 | 5791.6856 | 1.4057 | 0.051158 | 13.0389 | 0.093231 | 33.4182 | 4.83 | 5.5658 | 19.7649 | 1.1983 | 1.0261 | 146.7 | 0 | 73.35 | 0 | 0 | 220.05 | 0 | 9.8816 | 0 | 0 | 0 | 332.7833 | 20 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5828.3166 | 1.3841 | 0.051798 | 12.7255 | 0.094996 | 32.7091 | 4.83 | 5.6734 | 19.9477 | 1.1941 | 1.0261 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 386.4 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 19 | 75 | 16.38 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 5366.7896 | 0.81088 | 0.0607 | 4.7938 | 0.10251 | 23.6 | 2.5 | 5.0429 | 26.8943 | 1.2122 | 1.0223 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 312.7833 | 312.7833 | 41.1735 | 198.7478 | 411.4 | 411.4 | 922.9311 | 0 | 92.2931 | 922.9311 | 198.7478 | 312.7833 | 50.4289 | 360.9711
|  | AZ | 17 | 16 | 13.6313 | 1.78 | 46.49% | 0.00090429 | 5.04 | 1055.0156 | 45.8 | 161.9005 | 215.8674 | 19.7925 | 49% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 20.0463 | 2.1885 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.7925 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 17 | 73.1 | 13.6313 | 4" MERV 8 | 4" MERV 8 | 49% | -1 | 168.5455 | 90.8476 | 52.9236 | 27.1392 | 48.6825 | 27.1392 | 4.2411 | 0 | 29644.2889 | 15806.5827 | 3.0021 | 1.4527 | 21.8775 | 5.7064 | 29520.225 | 5635.0307 | 1.4091 | 0.048512 | 13.0893 | 0.086018 | 33.5273 | 4.83 | 5.5504 | 19.7665 | 1.1989 | 1.026 | 146.8 | 0 | 73.4 | 0 | 0 | 220.2 | 0 | 9.8928 | 0 | 0 | 0 | 558.4267 | 32 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5676.0662 | 1.3841 | 0.04921 | 12.7255 | 0.087892 | 32.7091 | 4.82 | 5.6734 | 19.9732 | 1.1941 | 1.026 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 616.96 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 17 | 75 | 13.6313 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 5102.7043 | 0.81088 | 0.054844 | 4.7938 | 0.08806 | 23.6 | 2.5 | 5.0429 | 27.0315 | 1.2122 | 1.0221 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 526.4267 | 526.4267 | 68.609 | 333.7553 | 658.24 | 656.96 | 1517.142 | 0 | 94.8214 | 1517.142 | 333.7553 | 526.4267 | 80.6863 | 576.2737
7. | Because this is a model for an indirect evaporative cooling system, I decided | BA | 15 | 8 | 12.8625 | 5.83 | 63.19% | 0.0011143 | 4.79 | 896.5313 | 45.2 | 138.4562 | 184.6082 | 19.7989 | 49.02% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 20.3168 | 2.0955 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.7989 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 15 | 73.1 | 12.8625 | 4" MERV 8 | 4" MERV 8 | 49.02% | -1 | 168.5455 | 90.877 | 52.9198 | 27.1476 | 48.6767 | 27.1476 | 4.2431 | 0 | 29635.0658 | 15806.7658 | 3.0007 | 1.4528 | 21.8607 | 5.7066 | 29510.8859 | 5507.156 | 1.4083 | 0.046401 | 13.0779 | 0.080409 | 33.5 | 4.82 | 5.5539 | 19.792 | 1.1988 | 1.026 | 146.8 | 0 | 73.4 | 0 | 0 | 220.2 | 0 | 9.8903 | 0 | 0 | 0 | 292.2 | 16 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5545.6598 | 1.3841 | 0.047042 | 12.7255 | 0.082088 | 32.7091 | 4.82 | 5.6734 | 19.9941 | 1.1941 | 1.026 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 308.48 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 15 | 75 | 12.8625 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 4871.7015 | 0.81088 | 0.049945 | 4.7938 | 0.076563 | 23.6 | 2.5 | 5.0429 | 27.1417 | 1.2122 | 1.022 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 276.2 | 276.2 | 34.6797 | 169.0423 | 328.48 | 328.48 | 773.7223 | 0 | 96.7153 | 773.7223 | 169.0423 | 276.2 | 40.3431 | 288.1369
| to "split" the 2°F bin hours into two groupings, to more closely represent the | BB | 13 | 14 | 10.8643 | 3.02 | 60.35% | 0.00096429 | 4.15 | 658.8857 | 44.5 | 102.5066 | 136.6755 | 19.8282 | 49.09% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 21.0095 | 2.1619 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8282 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 13 | 73.1 | 10.8643 | 4" MERV 8 | 4" MERV 8 | 49.09% | -1 | 168.5455 | 91.0115 | 52.9023 | 27.1861 | 48.6504 | 27.1861 | 4.2519 | 0 | 29592.8165 | 15807.6059 | 2.9944 | 1.4529 | 21.784 | 5.7075 | 29468.0559 | 5396.9103 | 1.4048 | 0.044615 | 13.0256 | 0.075766 | 33.3909 | 4.82 | 5.5699 | 19.8336 | 1.1981 | 1.026 | 146.6 | 0 | 73.3 | 0 | 0 | 219.9 | 0 | 9.8787 | 0 | 0 | 0 | 534.0767 | 28 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5428.7339 | 1.3841 | 0.045133 | 12.7255 | 0.077098 | 32.7091 | 4.82 | 5.6734 | 20.0122 | 1.1941 | 1.026 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 539.84 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 13 | 75 | 10.8643 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 4663.4978 | 0.81088 | 0.045706 | 4.7938 | 0.067071 | 23.6 | 2.4 | 5.0429 | 27.2334 | 1.2122 | 1.022 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 506.0767 | 506.0767 | 62.3704 | 305.5218 | 573.44 | 573.44 | 1385.0385 | 0 | 98.9313 | 1385.0385 | 305.5218 | 506.0767 | 70.6005 | 502.8395
| two phases if an indirect evaporative unit's intended sequence of operation, | BC | 11 | 19 | 8.1211 | -5.46 | 42.65% | 0.00061714 | 3.29 | 930.3632 | 43.8 | 145.8029 | 194.4038 | 19.7112 | 48.8% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 21.9403 | 2.3157 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.7112 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 11 | 73.1 | 8.1211 | 4" MERV 8 | 4" MERV 8 | 48.8% | -1 | 168.5455 | 90.4745 | 52.9727 | 27.0325 | 48.7561 | 27.0325 | 4.2166 | 0 | 29762.2038 | 15804.2527 | 3.0196 | 1.4523 | 22.0927 | 5.7039 | 29639.7502 | 5273.3444 | 1.4292 | 0.042966 | 13.3291 | 0.071295 | 33.9091 | 4.81 | 5.4928 | 19.7498 | 1.2012 | 1.026 | 147.3 | 0 | 73.65 | 0 | 0 | 220.95 | 0 | 9.9251 | 0 | 0 | 0 | 755.6617 | 38 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5325.6072 | 1.3841 | 0.043479 | 12.7255 | 0.072861 | 32.7091 | 4.81 | 5.6734 | 20.0275 | 1.1941 | 1.026 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 731.12 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 11 | 75 | 8.1211 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 4476.3351 | 0.81088 | 0.042039 | 4.7938 | 0.059214 | 23.6 | 2.4 | 5.0429 | 27.3098 | 1.2122 | 1.0219 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 717.6617 | 717.6617 | 87.711 | 432.3222 | 776.72 | 776.72 | 1926.7039 | 0 | 101.4055 | 1926.7039 | 432.3222 | 717.6617 | 95.815 | 680.905
| according to this design. See this distinction represented graphically on each | BD | 9 | 25 | 5.576 | -15.93 | 26.54% | 0.00034714 | 2.53 | 945.69 | 43.2 | 149.1292 | 198.8389 | 19.639 | 48.62% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 22.7629 | 2.4353 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.639 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 9 | 73.1 | 5.576 | 4" MERV 8 | 4" MERV 8 | 48.62% | -1 | 168.5455 | 90.143 | 53.0169 | 26.9377 | 48.8223 | 26.9377 | 4.1946 | 0 | 29867.7867 | 15802.1825 | 3.0353 | 1.4519 | 22.2867 | 5.7017 | 29746.7705 | 5173.7659 | 1.4382 | 0.041396 | 13.4616 | 0.067393 | 34.1818 | 4.81 | 5.4535 | 19.702 | 1.2028 | 1.0259 | 147.7 | 0 | 73.85 | 0 | 0 | 221.55 | 0 | 9.9541 | 0 | 0 | 0 | 1034.875 | 50 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5237.4392 | 1.3841 | 0.042086 | 12.7255 | 0.069359 | 32.7091 | 4.81 | 5.6734 | 20.0402 | 1.1941 | 1.0259 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 962 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 9 | 75 | 5.576 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 4309.3695 | 0.81088 | 0.038882 | 4.7938 | 0.052725 | 23.6 | 2.4 | 5.0429 | 27.3732 | 1.2122 | 1.0219 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 984.875 | 984.875 | 118.9736 | 589.4095 | 1022 | 1022 | 2596.2845 | 0 | 103.8514 | 2596.2845 | 589.4095 | 984.875 | 126.0723 | 895.9277
| IDEC units' submittal tab. | BE | 7 | 16 | 3.9125 | -16.83 | 27.91% | 0.00033 | 2.03 | 2.9344 | 42.5 | 0.46608 | 0.62144 | 19.9985 | 49.51% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 23.3041 | 2.4429 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.9985 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 7 | 73.1 | 3.9125 | 4" MERV 8 | 4" MERV 8 | 49.51% | -1 | 168.5455 | 91.7933 | 52.7861 | 27.4071 | 48.4873 | 27.4071 | 4.2988 | 0 | 29349.7231 | 15812.4883 | 2.9486 | 1.4509 | 21.2741 | 5.7014 | 29221.4703 | 5164.5412 | 1.3842 | 0.04095 | 12.728 | 0.066547 | 32.7182 | 4.81 | 5.6726 | 20.0491 | 1.1941 | 1.0259 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8114 | 0 | 0 | 0 | 688.2933 | 32 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5164.7907 | 1.3841 | 0.040954 | 12.7255 | 0.066557 | 32.7091 | 4.81 | 5.6734 | 20.0503 | 1.1941 | 1.0259 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 615.68 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 7 | 75 | 3.9125 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 4161.3581 | 0.81088 | 0.036175 | 4.7938 | 0.047368 | 23.6 | 2.4 | 5.0429 | 27.4257 | 1.2122 | 1.0218 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 656.2933 | 656.2933 | 77.6439 | 385.8808 | 654.08 | 654.08 | 1696.2542 | 0 | 106.0159 | 1696.2542 | 385.8808 | 656.2933 | 80.6863 | 573.3937
|  | BF | 5 | 4 | 1.575 | -31.11 | 13.44% | 0.00014286 | 1.35 | 513.1875 | 41.9 | 82.0132 | 109.3509 | 19.6426 | 48.63% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 24.0401 | 2.5258 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.6426 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 5 | 73.1 | 1.575 | 4" MERV 8 | 4" MERV 8 | 48.63% | -1 | 168.5455 | 90.1597 | 53.0146 | 26.9425 | 48.8189 | 26.9425 | 4.1957 | 0 | 29862.4405 | 15802.287 | 3.0345 | 1.452 | 22.2768 | 5.7018 | 29741.3511 | 5044.6139 | 1.4377 | 0.039403 | 13.4549 | 0.062546 | 34.1636 | 4.8 | 5.4555 | 19.7224 | 1.2027 | 1.0259 | 147.7 | 0 | 73.85 | 0 | 0 | 221.55 | 0 | 9.9526 | 0 | 0 | 0 | 178.5667 | 8 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5104.4193 | 1.3841 | 0.040023 | 12.7255 | 0.064283 | 32.7091 | 4.8 | 5.6734 | 20.0586 | 1.1941 | 1.0259 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 153.6 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 5 | 75 | 1.575 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 4028.1033 | 0.81088 | 0.03381 | 4.7938 | 0.042853 | 23.6 | 2.4 | 5.0429 | 27.4702 | 1.2122 | 1.0218 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 170.5667 | 170.5667 | 19.9213 | 99.4142 | 163.2 | 163.2 | 433.1808 | 0 | 108.2952 | 433.1808 | 99.4142 | 170.5667 | 20.1716 | 143.0284
8. | There is a "dry" group of hours sorted by dry bulb containing hours below 65°F | BG | 3 | 0
| dry bulb outdoors. Below those a moist group containing the rest of the hours, | BH | 1 | 0
| during which the evaporative process takes place. | BI | -1 | 2 | -3.8 | -44.97 | 7.74% | 6e-05 | -0.18 | 579.6 | 39.9 | 94.515 | 126.0201 | 20 | 54.61% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 25.6961 | 2.5625 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -1 | 73.1 | -3.8 | 4" MERV 8 | 4" MERV 8 | 54.61% | -1 | 168.5455 | 101.2515 | 52.7853 | 30.3762 | 48.486 | 30.3762 | 4.2992 | 0 | 29347.6707 | 17440.5495 | 2.9483 | 1.598 | 21.2705 | 6.9256 | 29219.3903 | 5542.6499 | 1.3841 | 0.046032 | 12.7255 | 0.080283 | 32.7091 | 5.84 | 5.6734 | 18.2945 | 1.1941 | 1.0315 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 99.0233 | 4 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5005.9538 | 1.3841 | 0.038524 | 12.7255 | 0.060683 | 32.7091 | 4.8 | 5.6734 | 20.0717 | 1.1941 | 1.0259 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 76.8 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -1 | 75 | -3.8 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 3711.0234 | 0.81088 | 0.028459 | 4.7938 | 0.033232 | 23.6 | 2.4 | 5.0429 | 27.5654 | 1.2122 | 1.0217 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 95.0233 | 95.0233 | 10.5347 | 53.0191 | 98.24 | 81.6 | 229.6424 | 0 | 114.8212 | 229.6424 | 53.0191 | 95.0233 | 10.0858 | 71.5142
|  | BJ | -3 | 0
| Here is the sequence for repeating / reviewing my calculation. | BK | -5 | 1 | -6.7 | -25.11 | 32.42% | 0.00020429 | -0.98 | 0 | 38.6 | 0 | 0 | 20 | 49.51% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 26.5619 | 2.4985 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -5 | 73.1 | -6.7 | 4" MERV 8 | 4" MERV 8 | 49.51% | -1 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5010.5363 | 1.3841 | 0.038594 | 12.7255 | 0.060848 | 32.7091 | 4.8 | 5.6734 | 20.0711 | 1.1941 | 1.0259 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 52.7583 | 2 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5010.5363 | 1.3841 | 0.038594 | 12.7255 | 0.060848 | 32.7091 | 4.8 | 5.6734 | 20.0711 | 1.1941 | 1.0259 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 38.4 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -5 | 75 | -6.7 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 3557.0222 | 0.81088 | 0.026001 | 4.7938 | 0.029102 | 23.6 | 2.4 | 5.0429 | 27.6065 | 1.2122 | 1.0217 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 50.7583 | 50.7583 | 5.4174 | 27.3754 | 40.8 | 40.8 | 118.9337 | 0 | 118.9337 | 118.9337 | 27.3754 | 50.7583 | 5.0429 | 35.7571
|  | BL | -7 | 4 | -8.125 | -19.29 | 50.54% | 0.00028714 | -1.37 | 760.725 | 37.9 | 126.5295 | 168.7061 | 20 | 50.49% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 26.9841 | 2.4618 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -7 | 73.1 | -8.125 | 4" MERV 8 | 4" MERV 8 | 50.49% | -1 | 168.5455 | 93.6076 | 52.7853 | 27.9734 | 48.486 | 27.9734 | 4.2992 | 0 | 29347.6707 | 16123.8825 | 2.9483 | 1.478 | 21.2705 | 5.9223 | 29219.3903 | 5138.6041 | 1.3841 | 0.040377 | 12.7255 | 0.065287 | 32.7091 | 4.99 | 5.6734 | 19.7132 | 1.1941 | 1.0269 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 217.5267 | 8 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5035.7412 | 1.3841 | 0.038975 | 12.7255 | 0.061759 | 32.7091 | 4.8 | 5.6734 | 20.0678 | 1.1941 | 1.0259 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 153.6 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -7 | 75 | -8.125 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 3494.8046 | 0.81088 | 0.025034 | 4.7938 | 0.02753 | 23.6 | 2.4 | 5.0429 | 27.6221 | 1.2122 | 1.0217 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 209.5267 | 209.5267 | 21.9624 | 111.19 | 169.28 | 163.2 | 483.9167 | 0 | 120.9792 | 483.9167 | 111.19 | 209.5267 | 20.1716 | 143.0284
9. | Maintain coordination with electrical design. Keep input values in rows 44-46 | BM | -9 | 2 | -10.95 | -54.68 | 6.27% | 3.1429e-05 | -2.12 | 422.625 | 37.2 | 70.7761 | 94.3682 | 20 | 49.94% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 27.7958 | 2.5751 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -9 | 73.1 | -10.95 | 4" MERV 8 | 4" MERV 8 | 49.94% | -1 | 168.5455 | 92.5864 | 52.7853 | 27.6544 | 48.486 | 27.6544 | 4.2992 | 0 | 29347.6707 | 15947.9873 | 2.9483 | 1.4627 | 21.2705 | 5.7968 | 29219.3903 | 5120.8101 | 1.3841 | 0.0402 | 12.7255 | 0.064775 | 32.7091 | 4.88 | 5.6734 | 19.9073 | 1.1941 | 1.0263 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 112.01 | 4 | 0 | 0 | 168.5455 | 91.8 | 52.7853 | 27.409 | 48.486 | 27.409 | 4.2992 | 0 | 29347.6707 | 15812.5299 | 2.9483 | 1.4509 | 21.2705 | 5.7014 | 29219.3903 | 5075.7219 | 1.3841 | 0.039583 | 12.7255 | 0.06322 | 32.7091 | 4.8 | 5.6734 | 20.0625 | 1.1941 | 1.0259 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 76.8 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -9 | 75 | -10.95 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.854 | 18.9347 | 14.1518 | 18.9347 | 19.7022 | 0 | 18050.1605 | 10235.9477 | 2.1906 | 1.1264 | 9.7201 | 2.8872 | 18787.7997 | 3440.3022 | 0.81088 | 0.024199 | 4.7938 | 0.026196 | 23.6 | 2.4 | 5.0429 | 27.6354 | 1.2122 | 1.0217 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 108.01 | 108.01 | 11.2626 | 57.2185 | 82.88 | 81.6 | 246.8285 | 0 | 123.4143 | 246.8285 | 57.2185 | 108.01 | 10.0858 | 71.5142
| of the Summary tab that are consistant with the electrical design. | BN | -11 | 0
|  |  | total | 6365 | hours
10. | Manual psychrometric solutions appear to the left here, in column 15 (or
| column "O" if you prefer). There are 98 such manual selections in this bin tab; | [194 empty] | NO | selected | Resulting | Resulting | Ventilation | Gen | UPS | ITE
| common psychrometric results may be copied to other scenario tabs | 2°F wet bulb bins (for hours above 65°F dry bulb) | [7 empty] | Annual HW demand of cafeteria: |  |  |  | recovery | zone | Properties of IT equipment zone: | [5 empty] | Properties for generic ventilation air handlers. | [17 empty] | Information used for hourly inputs for ITE room IDEC units (shown with heat recovery input) | [27 empty] | Outputs for ITE room IDEC units with heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | HR export |  | Generator room | [19 empty] | Outputs for ITE room IDEC units without heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | Without HR | UPS room variables | [13 empty] | Information used for hourly inputs for UPS room IDEC units | [27 empty] | Outputs for UPS units. NOTE: most of the performance values are PER UNIT | [18 empty] | Generator Room |  | Ventilation system |  | ITE and UPS cooling |  | Recovery | recovery | Mechanical | Mechanical | system | room | room | room
|  | bin | Average | bin | Outdoor |  |  |  | Psychrometric values for averaged points: | café avg | entering | kwh from | H2O heater | delta T | % desigm | Temp | AHU | Min | Max | min. | max. | control | heat | liquid | Cooling | DX split | room air | Project | Design | Design | Reset | Resulting | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | energy avoided | Room heat | engine block | Recovery | Recovery | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | error | ITE cooling | UPS room | Battery | Project | Design | Design | Design | Alternate | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | with | without | with | without | with | without | whatsoever | savings | Input | energy | HVAC | HVAC | cooling | cooling
11. | Review equipment selections, ensure they are consistent with your design | name | dry bulb | hours | wet bulb | dewpoint | %rh | moisture | enthalpy | 140 | temp | hot aisle | input energy | w/ HR | w/ HR | into ITE | SAT: | moisture | moisture | enthalpy | enthalpy | mode | power | added | needed | kW input: | dew point | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | elsewhere | need, kWh | heat, kWh | Potential | Savings | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | annual kWh | temp | temp | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | recovery | recovery | recovery | recovery | recovery | recovery | at all | kWh: | Power | incl. Recov | Component | component | component | component
| especially during the extreme climate data. Fill out the remaining user input | CA | 66 | 4 | 46 | 25 | 20.24% | 0.0028629 | 18.95 | 1279.95 | 55.4 | 176.4013 | 235.2018 | 19.9418 | 49.37% | 77.2 | 76.8 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 7.8128 | 1.8086 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.2 | 19.9418 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 66 | 73.1 | 46 | 4" MERV 8 | 4" MERV 8 | 49.37% | -1 | 168.5455 | 91.5327 | 52.8155 | 27.3434 | 48.5345 | 27.3434 | 4.281 | 0 | 29421.8706 | 15955.3415 | 2.9592 | 1.4632 | 21.4032 | 5.7473 | 29239.5973 | 3490.9121 | 1.3857 | 0.026615 | 12.7497 | 0.029235 | 32.8364 | 6.49 | 5.6546 | 14.8221 | 1.1948 | 1.035 | 145.7 | 30.9 | 72.85 | 15.45 | 0 | 218.55 | 46.35 | 9.8188 | 2.8359 | 0 | 0 | 0 | 7.2 | 0 | 0 | 168.5455 | 91.8 | 52.7818 | 27.4198 | 48.4834 | 27.4198 | 4.2984 | 0 | 29339.2726 | 15957.01 | 2.947 | 1.4635 | 21.2555 | 5.749 | 29156.0382 | 3503.1533 | 1.3788 | 0.02679 | 12.6498 | 0.029531 | 32.6364 | 6.48 | 5.6868 | 14.8705 | 1.1936 | 1.035 | 145.4 | 31 | 72.7 | 15.5 | 0 | 218.1 | 46.5 | 9.7961 | 2.8441 | 0 | 129.6 | 77.6 | 56.6 | 1259.52 | 111.24 | 65 | 56.6 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 66 | 75 | 46 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8525 | 18.9362 | 14.1507 | 18.9362 | 19.7018 | 0 | 18044.9953 | 10263.5837 | 2.1898 | 1.1292 | 9.7138 | 2.8937 | 18747.7842 | 9202.034 | 0.80802 | 0.20898 | 4.7667 | 0.60511 | 23.6 | 3.8 | 5.049 | 17.3796 | 1.2119 | 1.0344 | 79.7 | 34.1 | 39.85 | 17.05 | 0 | 119.55 | 51.15 | 8.1341 | 5.2174 | 0 | 7.2 | 7.2 | 8.6705 | 34.5048 | 222.88 | 222.56 | 264.2648 | 1.6875e-14 | 66.0662 | 264.2648 | 34.5048 | 7.2 | 20.1958 | 202.3642
| (yellow cells in boxes), including how much cooling equipment to install, | CB | 67.7765 | 34 | 48 | 29.1 | 23.04% | 0.0034686 | 20.04 | 1208.8676 | 56 | 165.4232 | 220.5643 | 19.9468 | 49.38% | 77.6 | 77.2 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 6.633 | 1.5403 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.6 | 19.9468 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 67.7765 | 73.1 | 48 | 4" MERV 8 | 4" MERV 8 | 49.38% | -1 | 168.5455 | 91.5559 | 52.8126 | 27.3509 | 48.5301 | 27.3509 | 4.2825 | 0 | 29414.6809 | 15966.9483 | 2.9581 | 1.4642 | 21.3903 | 5.7514 | 29232.3245 | 3587.271 | 1.3851 | 0.02803 | 12.741 | 0.031639 | 32.8182 | 6.49 | 5.6574 | 14.8067 | 1.1947 | 1.035 | 145.7 | 31.2 | 72.85 | 15.6 | 0 | 218.55 | 46.8 | 9.8168 | 2.8697 | 0 | 0 | 0 | 59.1867 | 0 | 0 | 168.5455 | 91.8 | 52.7818 | 27.4207 | 48.4834 | 27.4207 | 4.2984 | 0 | 29339.2726 | 15968.472 | 2.947 | 1.4645 | 21.2555 | 5.753 | 29156.0382 | 3598.9335 | 1.3788 | 0.0282 | 12.6498 | 0.031935 | 32.6364 | 6.49 | 5.6868 | 14.8507 | 1.1936 | 1.035 | 145.4 | 31.3 | 72.7 | 15.65 | 0 | 218.1 | 46.95 | 9.7961 | 2.8773 | 0 | 1765.28 | 81.8 | 60.8 | 1259.52 | 111.24 | 65 | 60.8 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 67.7765 | 75 | 48 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8525 | 18.9411 | 14.1507 | 18.9411 | 19.7018 | 0 | 18044.9953 | 10343.8172 | 2.1898 | 1.1376 | 9.7138 | 2.9151 | 18747.7842 | 7163.6323 | 0.80802 | 0.12961 | 4.7667 | 0.29216 | 23.6 | 3.6 | 5.049 | 18.5234 | 1.2119 | 1.0323 | 79.7 | 29.9 | 39.85 | 14.95 | 0 | 119.55 | 44.85 | 8.1341 | 4.5827 | 0 | 59.1867 | 59.1867 | 66.7471 | 253.1795 | 1887.68 | 1887.68 | 2200.0461 | 0 | 64.7072 | 2200.0461 | 253.1795 | 59.1867 | 171.6644 | 1716.0156
| when. Review accuracy of generator room heating load, HW export schedule | CC | 67.3902 | 102 | 50 | 35.69 | 30.93% | 0.0046029 | 21.18 | 1072.0176 | 56.7 | 145.474 | 193.9654 | 19.953 | 49.4% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 5.3991 | 1.0379 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.953 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 67.3902 | 73.1 | 50 | 4" MERV 8 | 4" MERV 8 | 49.4% | -1 | 168.5455 | 91.5841 | 52.809 | 27.3599 | 48.5247 | 27.3599 | 4.2844 | 0 | 29405.9466 | 15978.5863 | 2.9568 | 1.4652 | 21.3747 | 5.7555 | 29223.4802 | 3715.9649 | 1.3844 | 0.02979 | 12.7304 | 0.034833 | 32.8 | 6.5 | 5.6608 | 14.7905 | 1.1946 | 1.0351 | 145.7 | 30.8 | 72.85 | 15.4 | 0 | 218.55 | 46.2 | 9.8143 | 2.8271 | 0 | 0 | 0 | 178.8733 | 0 | 0 | 168.5455 | 91.8 | 52.7818 | 27.4216 | 48.4834 | 27.4216 | 4.2984 | 0 | 29339.2726 | 15979.9339 | 2.947 | 1.4655 | 21.2555 | 5.7569 | 29156.0382 | 3726.7265 | 1.3788 | 0.029952 | 12.6498 | 0.035123 | 32.6364 | 6.5 | 5.6868 | 14.8293 | 1.1936 | 1.0351 | 145.4 | 30.8 | 72.7 | 15.4 | 0 | 218.1 | 46.2 | 9.7961 | 2.8337 | 0 | 5304 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 67.3902 | 75 | 50 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8525 | 18.946 | 14.1507 | 18.946 | 19.7018 | 0 | 18044.9953 | 10424.0507 | 2.1898 | 1.146 | 9.7138 | 2.9367 | 18747.7842 | 5699.8164 | 0.80802 | 0.083399 | 4.7667 | 0.14958 | 23.6 | 3.5 | 5.049 | 18.9878 | 1.2119 | 1.0315 | 79.7 | 25.8 | 39.85 | 12.9 | 0 | 119.55 | 38.7 | 8.1341 | 3.9467 | 0 | 178.8733 | 178.8733 | 178.4269 | 633.6838 | 5661 | 5661 | 6473.5571 | -2.8422e-13 | 63.4662 | 6473.5571 | 633.6838 | 178.8733 | 514.9933 | 5146.0067
| if those heat recovery options are to be considered in your design. | CD | 69.132 | 222 | 52 | 41.82 | 37.04% | 0.0058643 | 22.98 | 942.8919 | 57.4 | 126.8763 | 169.1684 | 19.96 | 49.42% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 3.4509 | 0.47914 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.96 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 69.132 | 73.1 | 52 | 4" MERV 8 | 4" MERV 8 | 49.42% | -1 | 168.5455 | 91.6165 | 52.8049 | 27.3691 | 48.5185 | 27.3691 | 4.2865 | 0 | 29395.9377 | 15978.7882 | 2.9554 | 1.4653 | 21.3567 | 5.7557 | 29213.3656 | 3926.3747 | 1.3836 | 0.032989 | 12.7183 | 0.040758 | 32.7727 | 6.51 | 5.6647 | 14.7847 | 1.1945 | 1.0351 | 145.6 | 31.2 | 72.8 | 15.6 | 0 | 218.4 | 46.8 | 9.8117 | 2.8687 | 0 | 0 | 0 | 376.4233 | 0 | 0 | 168.5455 | 91.8 | 52.7818 | 27.4216 | 48.4834 | 27.4216 | 4.2984 | 0 | 29339.2726 | 15979.9339 | 2.947 | 1.4655 | 21.2555 | 5.7569 | 29156.0382 | 3936.1935 | 1.3788 | 0.033143 | 12.6498 | 0.04105 | 32.6364 | 6.51 | 5.6868 | 14.8176 | 1.1936 | 1.0351 | 145.4 | 31.3 | 72.7 | 15.65 | 0 | 218.1 | 46.95 | 9.7961 | 2.8745 | 0 | 11561.76 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 69.132 | 75 | 52 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8525 | 18.946 | 14.1507 | 18.946 | 19.7018 | 0 | 18044.9953 | 10424.0507 | 2.1898 | 1.146 | 9.7138 | 2.9367 | 18747.7842 | 6585.6749 | 0.80802 | 0.10988 | 4.7667 | 0.22771 | 23.6 | 3.6 | 5.049 | 18.6269 | 1.2119 | 1.0321 | 79.7 | 27.3 | 39.85 | 13.65 | 0 | 119.55 | 40.95 | 8.1341 | 4.1815 | 0 | 376.4233 | 376.4233 | 313.3752 | 946.6906 | 12360.96 | 12360.96 | 13684.0739 | -6.8212e-13 | 61.64 | 13684.0739 | 946.6906 | 376.4233 | 1120.8678 | 11240.0922
|  | CE | 71.0419 | 332 | 54 | 47.12 | 42.47% | 0.0071914 | 24.89 | 948.6461 | 58 | 126.7233 | 168.9644 | 19.9611 | 49.42% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 1.3836 | 0 | 0 | 0 | 46.9 | 1259.52 | 1854 | 78 | 78 | 19.9611 | 46.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 71.0419 | 73.1 | 54 | 4" MERV 8 | 4" MERV 8 | 49.42% | -1 | 168.5455 | 91.6216 | 52.8036 | 27.3705 | 48.517 | 27.3705 | 4.2866 | 0 | 29392.6747 | 15977.9125 | 2.9549 | 1.4652 | 21.3509 | 5.7551 | 29199.1484 | 4180.2361 | 1.3824 | 0.037032 | 12.7013 | 0.04871 | 32.7545 | 6.51 | 5.668 | 14.7713 | 1.1943 | 1.0351 | 145.6 | 31.8 | 72.8 | 15.9 | 0 | 218.4 | 47.7 | 9.8083 | 2.9217 | 0 | 0 | 0 | 541.8033 | 0 | 0 | 168.5455 | 91.8 | 52.7812 | 27.4215 | 48.4829 | 27.4215 | 4.2982 | 0 | 29337.6056 | 15979.026 | 2.9468 | 1.4654 | 21.2525 | 5.7562 | 29143.4746 | 4190.5448 | 1.3778 | 0.037201 | 12.6348 | 0.049054 | 32.6182 | 6.51 | 5.6895 | 14.8031 | 1.1935 | 1.0351 | 145.3 | 31.9 | 72.65 | 15.95 | 0 | 217.95 | 47.85 | 9.7933 | 2.9274 | 0 | 17290.56 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 71.0419 | 75 | 54 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8523 | 18.9459 | 14.1505 | 18.9459 | 19.7018 | 0 | 18043.9701 | 10423.4584 | 2.1896 | 1.1459 | 9.7125 | 2.9364 | 18739.8446 | 7795.6326 | 0.80745 | 0.1516 | 4.7613 | 0.37187 | 23.6 | 3.7 | 5.0502 | 17.9973 | 1.2119 | 1.0333 | 79.6 | 29.5 | 39.8 | 14.75 | 0 | 119.4 | 44.25 | 8.1312 | 4.5164 | 0 | 541.8033 | 541.8033 | 349.6891 | 729.4374 | 18518.96 | 18518.96 | 19790.2008 | 1.0232e-12 | 59.609 | 19790.2008 | 729.4374 | 541.8033 | 1676.6519 | 16842.3081
12. | Commence itterations, using manufacturer's tool. I automated | CF | 73.161 | 351 | 56 | 49.75 | 43.62% | 0.0079457 | 26.23 | 932.4474 | 58.7 | 123.4961 | 164.6615 | 19.9632 | 49.42% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 48.9 | 1259.52 | 1854 | 78 | 78 | 19.9632 | 48.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 73.161 | 73.1 | 56 | 4" MERV 8 | 4" MERV 8 | 49.42% | -1 | 168.5455 | 91.6312 | 52.8008 | 27.3729 | 48.5139 | 27.3729 | 4.2869 | 0 | 29385.8185 | 15975.8553 | 2.9539 | 1.465 | 21.3386 | 5.7537 | 29166.7803 | 4492.322 | 1.3797 | 0.042277 | 12.6626 | 0.059762 | 32.7091 | 6.52 | 5.6753 | 14.7544 | 1.1941 | 1.0352 | 145.5 | 32.6 | 72.75 | 16.3 | 0 | 218.25 | 48.9 | 9.8006 | 2.9918 | 0 | 0 | 0 | 548.0167 | 0 | 0 | 168.5455 | 91.8 | 52.7796 | 27.4211 | 48.4818 | 27.4211 | 4.2978 | 0 | 29333.7186 | 15976.9089 | 2.9462 | 1.4652 | 21.2456 | 5.7548 | 29114.1565 | 4502.945 | 1.3754 | 0.042463 | 12.5999 | 0.060166 | 32.5818 | 6.52 | 5.6957 | 14.7842 | 1.1933 | 1.0352 | 145.2 | 32.6 | 72.6 | 16.3 | 0 | 217.8 | 48.9 | 9.7865 | 2.9974 | 0 | 18308.16 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 48.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 73.161 | 75 | 56 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8516 | 18.9457 | 14.15 | 18.9457 | 19.7016 | 0 | 18041.5794 | 10422.0774 | 2.1892 | 1.1458 | 9.7096 | 2.9356 | 18721.3225 | 9507.825 | 0.80613 | 0.22159 | 4.7489 | 0.66295 | 23.6 | 4 | 5.053 | 16.8478 | 1.2117 | 1.0355 | 79.6 | 32.7 | 39.8 | 16.35 | 0 | 119.4 | 49.05 | 8.1242 | 5.0147 | 0 | 548.0167 | 548.0167 | 285.5221 | 285.5221 | 19712.16 | 19712.16 | 20545.6988 | 0 | 58.5348 | 20545.6988 | 285.5221 | 548.0167 | 1773.5888 | 17938.5712
| that process to make this example happen. This calculation | CG | 74.8974 | 418 | 58 | 52.59 | 45.72% | 0.00884 | 27.64 | 979.0112 | 59.3 | 128.7063 | 171.6084 | 19.9626 | 49.42% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 53.1 | 1259.52 | 1854 | 78 | 78 | 19.9626 | 53.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 74.8974 | 73.1 | 58 | 4" MERV 8 | 4" MERV 8 | 49.42% | -1 | 168.5455 | 91.6282 | 52.7975 | 27.3712 | 48.5118 | 27.3712 | 4.2857 | 0 | 29377.7038 | 15970.9133 | 2.9527 | 1.4646 | 21.3241 | 5.7503 | 29099.4231 | 4881.9741 | 1.3742 | 0.049184 | 12.5824 | 0.075555 | 32.6273 | 6.53 | 5.6894 | 14.7299 | 1.1936 | 1.0352 | 145.2 | 33.3 | 72.6 | 16.65 | 0 | 217.8 | 49.95 | 9.7851 | 3.0552 | 0 | 0 | 0 | 628.43 | 0 | 0 | 168.5455 | 91.8 | 52.7759 | 27.4204 | 48.479 | 27.4204 | 4.2969 | 0 | 29324.6793 | 15971.9855 | 2.9449 | 1.4648 | 21.2295 | 5.7514 | 29045.9682 | 4893.8273 | 1.3697 | 0.049406 | 12.519 | 0.076081 | 32.5 | 6.53 | 5.7102 | 14.7601 | 1.1928 | 1.0352 | 145 | 33.3 | 72.5 | 16.65 | 0 | 217.5 | 49.95 | 9.7707 | 3.061 | 0 | 21836.32 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 53.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 74.8974 | 75 | 58 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.85 | 18.9454 | 14.1488 | 18.1608 | 19.7012 | 0.78465 | 18036.0198 | 10418.8658 | 2.1884 | 1.1456 | 9.7027 | 2.9343 | 18678.2567 | 10145.8553 | 0.80307 | 0.25028 | 4.7199 | 0.79902 | 23.5 | 4.5 | 5.0595 | 14.8597 | 1.2115 | 1.0403 | 79.4 | 33 | 39.7 | 16.5 | 0 | 119.1 | 49.5 | 8.1082 | 5.0564 | 0 | 628.43 | 628.43 | 340.0235 | 340.0235 | 23717.32 | 23717.32 | 24685.7735 | 0 | 59.0569 | 24685.7735 | 340.0235 | 628.43 | 2114.8601 | 21602.4599
| does not reflect any actual data center. I completed this for | CH | 78.9962 | 338 | 60 | 53.8 | 41.73% | 0.0092486 | 29.09 | 1027.5426 | 60 | 133.9147 | 178.553 | 19.9631 | 49.42% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 53.1 | 1259.52 | 1854 | 78 | 78 | 19.9631 | 53.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 78.9962 | 73.1 | 60 | 4" MERV 8 | 4" MERV 8 | 49.42% | -1 | 168.5455 | 91.6305 | 52.7972 | 27.3719 | 48.5113 | 27.3719 | 4.2859 | 0 | 29376.9857 | 15970.9278 | 2.9526 | 1.4646 | 21.3228 | 5.7503 | 29098.7088 | 5381.5338 | 1.3741 | 0.05899 | 12.5816 | 0.099892 | 32.6273 | 6.55 | 5.6897 | 14.6828 | 1.1936 | 1.0354 | 145.2 | 35.5 | 72.6 | 17.75 | 0 | 217.8 | 53.25 | 9.785 | 3.26 | 0 | 0 | 0 | 461.9767 | 0 | 0 | 168.5455 | 91.8 | 52.7759 | 27.4204 | 48.479 | 27.4204 | 4.2969 | 0 | 29324.6793 | 15971.9855 | 2.9449 | 1.4648 | 21.2295 | 5.7514 | 29045.9682 | 5394.6287 | 1.3697 | 0.059258 | 12.519 | 0.10059 | 32.5 | 6.55 | 5.7102 | 14.7121 | 1.1928 | 1.0353 | 145 | 35.6 | 72.5 | 17.8 | 0 | 217.5 | 53.4 | 9.7707 | 3.2663 | 0 | 17711.2 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 53.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 78.9962 | 75 | 60 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.85 | 18.9455 | 14.1488 | 17.003 | 19.7012 | 1.9425 | 18036.0198 | 10418.8658 | 2.1884 | 1.1458 | 9.7027 | 2.9347 | 18678.2567 | 10213.4535 | 0.80307 | 0.25377 | 4.7199 | 0.81556 | 23.5 | 5.1 | 5.0595 | 13.0475 | 1.2115 | 1.0459 | 79.4 | 34.6 | 39.7 | 17.3 | 0 | 119.1 | 51.9 | 8.1082 | 5.3048 | 0 | 461.9767 | 461.9767 | 274.9472 | 274.9472 | 19435 | 19435 | 20171.9239 | 0 | 59.6802 | 20171.9239 | 274.9472 | 461.9767 | 1710.1022 | 17724.8978
| example purposes only. | CI | 83.3602 | 241 | 62 | 54.97 | 37.78% | 0.0096571 | 30.62 | 1127.972 | 60.7 | 145.7169 | 194.2892 | 19.9619 | 49.42% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 55 | 1259.52 | 1854 | 78 | 78 | 19.9619 | 55 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 83.3602 | 73.1 | 62 | 4" MERV 8 | 4" MERV 8 | 49.42% | -1 | 168.5455 | 91.6252 | 52.796 | 27.37 | 48.5109 | 27.37 | 4.2851 | 0 | 29374.1012 | 15968.4388 | 2.9522 | 1.4644 | 21.3177 | 5.7486 | 29066.277 | 6042.066 | 1.3714 | 0.073165 | 12.5431 | 0.1391 | 32.5909 | 6.59 | 5.6963 | 14.6093 | 1.1933 | 1.0355 | 145.1 | 38.4 | 72.55 | 19.2 | 0 | 217.65 | 57.6 | 9.7775 | 3.5325 | 0 | 0 | 0 | 294.34 | 0 | 0 | 168.5455 | 91.8 | 52.7741 | 27.42 | 48.4776 | 27.42 | 4.2965 | 0 | 29320.1699 | 15969.5294 | 2.9442 | 1.4646 | 21.2214 | 5.7497 | 29011.9565 | 6057.4243 | 1.3669 | 0.073513 | 12.4788 | 0.14012 | 32.4545 | 6.59 | 5.7174 | 14.6388 | 1.1926 | 1.0355 | 144.9 | 38.5 | 72.45 | 19.25 | 0 | 217.35 | 57.75 | 9.7628 | 3.5398 | 0 | 12705.52 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 55 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 83.3602 | 75 | 62 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8493 | 18.9454 | 14.1482 | 15.8174 | 19.701 | 3.1281 | 18033.2463 | 10417.2636 | 2.1879 | 1.1458 | 9.6993 | 2.9343 | 18656.771 | 10270.9494 | 0.80154 | 0.25701 | 4.7055 | 0.83062 | 23.5 | 5.7 | 5.0627 | 11.6041 | 1.2113 | 1.0516 | 79.3 | 36.5 | 39.65 | 18.25 | 0 | 118.95 | 54.75 | 8.1001 | 5.5862 | 0 | 294.34 | 294.34 | 196.0423 | 196.0423 | 14079.22 | 14079.22 | 14569.6023 | 0 | 60.4548 | 14569.6023 | 196.0423 | 294.34 | 1220.1159 | 12859.1041
|  | CJ | 87.0126 | 190 | 64 | 56.69 | 35.78% | 0.010289 | 32.19 | 1146.6932 | 61.3 | 147.0146 | 196.0195 | 19.9632 | 49.42% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 55.9 | 1259.52 | 1854 | 78 | 78 | 19.9632 | 55.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 87.0126 | 73.1 | 64 | 4" MERV 8 | 4" MERV 8 | 49.42% | -1 | 168.5455 | 91.631 | 52.7944 | 27.3715 | 48.5091 | 27.3715 | 4.2852 | 0 | 29370.0568 | 15967.2589 | 2.9516 | 1.4643 | 21.3105 | 5.7478 | 29047.5715 | 6959.7292 | 1.3699 | 0.094886 | 12.5209 | 0.2078 | 32.5636 | 6.65 | 5.7006 | 14.4807 | 1.1932 | 1.0358 | 145 | 41.8 | 72.5 | 20.9 | 0 | 217.5 | 62.7 | 9.7731 | 3.8432 | 0 | 0 | 0 | 208.92 | 0 | 0 | 168.5455 | 91.8 | 52.7732 | 27.4198 | 48.4769 | 27.4198 | 4.2962 | 0 | 29317.9365 | 15968.313 | 2.9439 | 1.4645 | 21.2174 | 5.7489 | 28995.1191 | 6976.8645 | 1.3656 | 0.095327 | 12.4589 | 0.20928 | 32.4364 | 6.65 | 5.721 | 14.508 | 1.1924 | 1.0358 | 144.8 | 41.9 | 72.4 | 20.95 | 0 | 217.2 | 62.85 | 9.759 | 3.851 | 0 | 10108 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 55.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 87.0126 | 75 | 64 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8489 | 18.9454 | 14.1479 | 14.6257 | 19.7009 | 4.3197 | 18031.8726 | 10416.4701 | 2.1877 | 1.1459 | 9.6977 | 2.9344 | 18646.1277 | 10336.1824 | 0.80078 | 0.26013 | 4.6984 | 0.84606 | 23.5 | 6.4 | 5.0643 | 10.4417 | 1.2113 | 1.0573 | 79.3 | 37.5 | 39.65 | 18.75 | 0 | 118.95 | 56.25 | 8.0961 | 5.7378 | 0 | 208.92 | 208.92 | 154.5561 | 154.5561 | 11324 | 11324 | 11687.4761 | 0 | 61.513 | 11687.4761 | 154.5561 | 208.92 | 962.2226 | 10361.7774
|  | CK | 91.5062 | 97 | 68 | 57.99 | 32.54% | 0.010791 | 33.84 | 1168.0979 | 62.6 | 147.2851 | 196.3801 | 19.9649 | 49.43% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 0.11859 | 0.094871 | 57.9 | 1259.52 | 1854 | 78 | 78 | 19.9649 | 57.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 91.5062 | 73.1 | 68 | 4" MERV 8 | 4" MERV 8 | 49.43% | -1 | 168.5455 | 91.639 | 52.7912 | 27.3733 | 48.506 | 27.3733 | 4.2852 | 0 | 29362.3785 | 15964.4785 | 2.9504 | 1.4641 | 21.2967 | 5.7459 | 29005.816 | 10093.8422 | 1.3664 | 0.1871 | 12.4716 | 0.59425 | 32.5091 | 6.98 | 5.7098 | 13.7884 | 1.1929 | 1.0376 | 144.9 | 50 | 72.45 | 25 | 0 | 217.35 | 75 | 9.7633 | 4.5906 | 0 | 0 | 0 | 92.13 | 0 | 0 | 168.5455 | 91.8 | 52.7711 | 27.4193 | 48.4753 | 27.4193 | 4.2957 | 0 | 29312.7395 | 15965.4824 | 2.9431 | 1.4643 | 21.2082 | 5.7469 | 28955.9208 | 10116.1839 | 1.3623 | 0.1879 | 12.4127 | 0.59812 | 32.3818 | 6.98 | 5.7293 | 13.8088 | 1.1921 | 1.0377 | 144.7 | 50.1 | 72.35 | 25.05 | 0 | 217.05 | 75.15 | 9.7499 | 4.5995 | 0 | 5416.48 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 57.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 91.5062 | 75 | 68 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.848 | 18.9454 | 14.1473 | 12.2413 | 19.7007 | 6.7041 | 18028.6763 | 10414.6237 | 2.1872 | 1.1461 | 9.6937 | 2.9343 | 18621.3689 | 10470.0431 | 0.79903 | 0.26484 | 4.6819 | 0.87251 | 23.5 | 7.7 | 5.0681 | 8.7028 | 1.2111 | 1.0688 | 79.2 | 36.1 | 39.6 | 18.05 | 0 | 118.8 | 54.15 | 8.0869 | 5.5307 | 0 | 92.13 | 92.13 | 88.1074 | 88.1074 | 6163.38 | 6163.38 | 6343.6174 | 0 | 65.3981 | 6343.6174 | 88.1074 | 92.13 | 491.6027 | 5671.7773
|  | CL | 95.7912 | 34 | 70 | 59.52 | 30.12% | 0.011411 | 35.58 | 1208.1574 | 63.3 | 150.9584 | 201.2779 | 19.9657 | 49.43% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 0.65422 | 0.52338 | 59 | 1259.52 | 1854 | 78 | 78 | 19.9657 | 59 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 95.7912 | 73.1 | 70 | 4" MERV 8 | 4" MERV 8 | 49.43% | -1 | 168.5455 | 91.6424 | 52.7896 | 27.374 | 48.5044 | 27.374 | 4.2852 | 0 | 29358.3332 | 15962.8652 | 2.9498 | 1.4639 | 21.2895 | 5.7448 | 28982.108 | 13050.9081 | 1.3645 | 0.30235 | 12.4436 | 1.2416 | 32.4727 | 7.54 | 5.7151 | 12.7611 | 1.1927 | 1.0407 | 144.8 | 60.4 | 72.4 | 30.2 | 0 | 217.2 | 90.6 | 9.7578 | 5.5497 | 0 | 0 | 0 | 27.4367 | 0 | 0 | 168.5455 | 91.8 | 52.7698 | 27.4191 | 48.4744 | 27.4191 | 4.2954 | 0 | 29309.7388 | 15963.848 | 2.9427 | 1.4641 | 21.2028 | 5.7458 | 28933.2873 | 13077.7135 | 1.3605 | 0.30358 | 12.3861 | 1.2493 | 32.3545 | 7.55 | 5.7341 | 12.7742 | 1.192 | 1.0407 | 144.6 | 60.5 | 72.3 | 30.25 | 0 | 216.9 | 90.75 | 9.7446 | 5.5601 | 0 | 2053.6 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 59 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 95.7912 | 75 | 70 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8475 | 18.9454 | 14.1469 | 10.9828 | 19.7006 | 7.9627 | 18026.8307 | 10413.5575 | 2.1869 | 1.1462 | 9.6915 | 2.9343 | 18607.0699 | 10538.9919 | 0.79801 | 0.26847 | 4.6723 | 0.89031 | 23.5 | 8.3 | 5.0702 | 7.9965 | 1.211 | 1.0749 | 79.2 | 37.7 | 39.6 | 18.85 | 0 | 118.8 | 56.55 | 8.0816 | 5.7662 | 0 | 27.4367 | 27.4367 | 45.4523 | 45.4523 | 2333.08 | 2335.8 | 2408.6889 | -1.7764e-13 | 70.8438 | 2408.6889 | 45.4523 | 27.4367 | 172.3877 | 2163.4123
|  | CM | 99.7083 | 24 | 72 | 61.34 | 28.52% | 0.012189 | 37.4 | 1229.5625 | 64 | 152.2309 | 202.9745 | 19.9667 | 49.43% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 1.2145 | 0.97159 | 61 | 1259.52 | 1854 | 78 | 78 | 19.9667 | 61 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 99.7083 | 73.1 | 72 | 4" MERV 8 | 4" MERV 8 | 49.43% | -1 | 168.5455 | 91.6473 | 52.7866 | 27.375 | 48.5018 | 26.6122 | 4.2849 | 0.76284 | 29351.0791 | 15959.7769 | 2.9488 | 1.4638 | 21.2766 | 5.7429 | 28937.3162 | 15650.0299 | 1.3608 | 0.42561 | 12.3908 | 2.0959 | 32.4182 | 8.68 | 5.7248 | 11.0838 | 1.1924 | 1.0468 | 144.7 | 69.8 | 72.35 | 34.9 | 0 | 217.05 | 104.7 | 9.7474 | 6.4173 | 0 | 0 | 0 | 16.2333 | 0 | 0 | 168.5455 | 91.8 | 52.7675 | 27.4186 | 48.4727 | 26.6451 | 4.2948 | 0.7735 | 29304.0121 | 15960.7289 | 2.9419 | 1.4639 | 21.1926 | 5.7439 | 28890.0932 | 15650.6034 | 1.3569 | 0.42573 | 12.3354 | 2.0966 | 32.3 | 8.69 | 5.7433 | 11.0959 | 1.1917 | 1.0469 | 144.5 | 69.9 | 72.25 | 34.95 | 0 | 216.75 | 104.85 | 9.7347 | 6.4203 | 0 | 1668.48 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 61 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 99.7083 | 75 | 72 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8465 | 18.9453 | 14.1461 | 9.7151 | 19.7003 | 9.2302 | 18023.3085 | 10411.5229 | 2.1864 | 1.1462 | 9.6871 | 2.9337 | 18579.7865 | 10602.4567 | 0.79608 | 0.27166 | 4.6542 | 0.90631 | 23.5 | 9 | 5.0743 | 7.394 | 1.2108 | 1.081 | 79.1 | 38.7 | 39.55 | 19.35 | 0 | 118.65 | 58.05 | 8.0714 | 5.9271 | 0 | 16.2333 | 16.2333 | 42.841 | 42.841 | 1882.56 | 1884.48 | 1943.5543 | 3.1974e-14 | 80.9814 | 1943.5543 | 42.841 | 16.2333 | 121.7843 | 1762.6957
|  | CN | 103.8875 | 8 | 74 | 63.09 | 26.77% | 0.012983 | 39.31 | 1246.7063 | 64.6 | 153.1348 | 204.1798 | 19.9679 | 49.44% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 1.8025 | 1.442 | 63 | 1259.52 | 1854 | 78 | 78 | 19.9679 | 63 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 103.8875 | 73.1 | 74 | 4" MERV 8 | 4" MERV 8 | 49.44% | -1 | 168.5455 | 91.6526 | 52.7835 | 27.3761 | 48.4989 | 24.7256 | 4.2846 | 2.6505 | 29343.3498 | 15956.4918 | 2.9476 | 1.4636 | 21.2628 | 5.7412 | 28889.659 | 15744.1983 | 1.3569 | 0.43095 | 12.3349 | 2.135 | 32.3545 | 9.71 | 5.7353 | 9.9159 | 1.192 | 1.0524 | 144.5 | 72 | 72.25 | 36 | 0 | 216.75 | 108 | 9.7363 | 6.6107 | 0 | 0 | 0 | 4.2967 | 0 | 0 | 168.5455 | 91.8 | 52.7651 | 27.4183 | 48.4708 | 24.7576 | 4.2942 | 2.6607 | 29297.92 | 15957.4108 | 2.941 | 1.4638 | 21.1818 | 5.7422 | 28844.1336 | 15744.7454 | 1.3532 | 0.43107 | 12.2816 | 2.1357 | 32.2455 | 9.71 | 5.7531 | 9.9269 | 1.1913 | 1.0524 | 144.3 | 72 | 72.15 | 36 | 0 | 216.45 | 108 | 9.7239 | 6.6136 | 0 | 621.44 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 63 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 103.8875 | 75 | 74 | 4" MERV 8 | 4" MERV 8 | 57.77% | 0 | 111.24 | 64.26 | 33.8454 | 18.9451 | 14.1454 | 8.4287 | 19.7001 | 10.5165 | 18019.5616 | 10409.3584 | 2.1858 | 1.1462 | 9.6826 | 2.9331 | 18550.7606 | 10666.8649 | 0.79403 | 0.27504 | 4.6349 | 0.92317 | 23.4 | 9.7 | 5.0787 | 6.8685 | 1.2106 | 1.0872 | 79 | 40 | 39.5 | 20 | 0 | 118.5 | 60 | 8.0606 | 6.1248 | 0 | 4.2967 | 4.2967 | 18.0433 | 18.0433 | 699.04 | 699.04 | 721.38 | -4.1744e-14 | 90.1725 | 721.38 | 18.0433 | 4.2967 | 40.6298 | 658.4102
|  | CO |  | 0
|  |  | total | 2395 | hours | [194 empty] | Ventilation MLC component | Generator MLC component | UPS room MLC component | ITE room MLC component
[200 empty] | 0.010123 | 0.009817 | 0.0056105 | 0.052932

## 75% Bins
[197 empty] | NO | selected | Resulting | Resulting | Ventilation | Gen | UPS | ITE
| Notes on this 90.4 MLC calculation: | 2°F dry bulb bins (for hours equal or below 65°F dry bulb) | [7 empty] | Annual HW demand of cafeteria: |  |  |  | ITE zone | ITE zone | Properties of IT equipment zone: | [6 empty] | Properties for generic ventilation air handlers. | [17 empty] | Information used for hourly inputs for ITE room IDEC units (shown with heat recovery input) | [27 empty] | Outputs for ITE room IDEC units with heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | HR export |  | Generator room | [19 empty] | Outputs for ITE room IDEC units without heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | Without HR | UPS room variables | [13 empty] | Information used for hourly inputs for UPS room IDEC units | [27 empty] | Outputs for UPS units. NOTE: most of the performance values are PER UNIT | [18 empty] | Generator Room |  | Ventilation system |  | ITE and UPS cooling |  | Recovery | recovery | Mechanical | Mechanical | system | room | room | room
1. | This tab shows performance when data center is 75% loaded. There are two | bin | Outdoor | bin | average |  |  |  | Psychrometry for averaged points: | café avg | entering | kw from | H2O heater | delta T | % desigm | Temp | AHU | Min | Max | min. | max. |  | control | heat | liquid | Cooling | DX split | room air | Project | Design | Design | Reset | Resulting | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | energy avoided | Room heat | engine block | Recovery | Recovery | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | error | ITE cooling | UPS room | Battery | Project | Design | Design | Design | Alternate | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | with | without | with | without | with | without | whatsoever | savings | Input | energy | HVAC | HVAC | cooling | cooling
| traditional modeling methods that I used here to determine the MLC. | name | dry bulb | hours | °F wb | dewpoint | %rh | moisture | enthalpy | 140 | temp | hot aisle | input energy | w/ HR | w/ HR | into ITE | SAT: | moisture | moisture | enthalpy | enthalpy |  | mode | power | added | needed | kW input: | dew point | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | elsewhere | need, kWh | heat, kWh | Potential | Savings | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | annual kWh | temp | temp | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | recovery | recovery | recovery | recovery | recovery | recovery | at all | kWh: | Power | incl. Recov | Component | component | component | component
|  | AB | 65 | 378 | 51.8048 | 40.53 | 40.64% | 0.0055757 | 21.66 | 1108.8069 | 61.7 | 106.0761 | 141.4348 | 19.9763 | 74.18% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Heat-Hum | 7.3194 | 0.91043 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9763 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 65 | 73.1 | 51.8048 | 4" MERV 8 | 4" MERV 8 | 74.18% | 1 | 168.5455 | 114.614 | 52.7955 | 34.4246 | 48.5042 | 34.4246 | 4.2913 | 0 | 29372.8365 | 19974.0684 | 2.952 | 1.632 | 21.3154 | 8.0134 | 29189.998 | 4954.6609 | 1.3816 | 0.048787 | 12.6903 | 0.076061 | 32.7182 | 8.1667 | 5.6737 | 14.8185 | 1.1941 | 1.0529 | 145.5 | 37.1 | 72.75 | 18.55 | 0 | 218.25 | 55.65 | 9.8054 | 4.093 | 0 | 0 | 0 | 1039.5 | 0 | 0 | 168.5455 | 114.75 | 52.7818 | 34.4636 | 48.4834 | 34.4636 | 4.2984 | 0 | 29339.2726 | 19974.9174 | 2.947 | 1.6322 | 21.2555 | 8.0147 | 29156.0382 | 4961.8733 | 1.3788 | 0.04892 | 12.6498 | 0.076379 | 32.6364 | 8.1667 | 5.6868 | 14.8358 | 1.1936 | 1.0529 | 145.4 | 37.2 | 72.7 | 18.6 | 0 | 218.1 | 55.8 | 9.7961 | 4.0978 | 0 | 15435 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 65 | 75 | 51.8048 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8525 | 33.4893 | 14.1507 | 33.4893 | 19.7018 | 0 | 18044.9953 | 17869.8012 | 2.1898 | 2.1552 | 9.7138 | 9.4679 | 18747.7842 | 11487.5975 | 0.80802 | 0.30822 | 4.7667 | 1.1141 | 23.6 | 9.8 | 5.049 | 11.9588 | 1.2119 | 1.0885 | 79.7 | 42.8 | 39.85 | 21.4 | 0 | 119.55 | 64.2 | 8.1341 | 6.5599 | 0 | 1039.5 | 1039.5 | 787.0431 | 3074.2236 | 34574.4 | 34574.4 | 38688.1236 | 0 | 102.3495 | 38688.1236 | 3074.2236 | 1039.5 | 1908.5046 | 32665.8954
2. | A 2°F bin hour-grouping method is shown on each of these 25%, 50%, 75% | AC | 63 | 251 | 50.3876 | 39.11 | 41.23% | 0.0052714 | 20.85 | 1070.6375 | 61 | 103.3402 | 137.7869 | 19.9762 | 74.18% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Heat-Hum | 8.6345 | 1.1126 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9762 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 63 | 73.1 | 50.3876 | 4" MERV 8 | 4" MERV 8 | 74.18% | 1 | 168.5455 | 114.6133 | 52.7956 | 34.4244 | 48.5043 | 34.4244 | 4.2913 | 0 | 29373.0091 | 19974.064 | 2.952 | 1.632 | 21.3157 | 8.0134 | 29190.1643 | 4771.2628 | 1.3816 | 0.045416 | 12.6905 | 0.068185 | 32.7182 | 8.1583 | 5.6736 | 14.8309 | 1.1941 | 1.0528 | 145.5 | 36.4 | 72.75 | 18.2 | 0 | 218.25 | 54.6 | 9.8053 | 4.0145 | 0 | 0 | 0 | 715.35 | 0 | 0 | 168.5455 | 114.75 | 52.7818 | 34.4636 | 48.4834 | 34.4636 | 4.2984 | 0 | 29339.2726 | 19974.9174 | 2.947 | 1.6322 | 21.2555 | 8.0147 | 29156.0382 | 4778.158 | 1.3788 | 0.045539 | 12.6498 | 0.068468 | 32.6364 | 8.1583 | 5.6868 | 14.8483 | 1.1936 | 1.0528 | 145.4 | 36.5 | 72.7 | 18.25 | 0 | 218.1 | 54.75 | 9.7961 | 4.0192 | 0 | 20477.4167 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 63 | 75 | 50.3876 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8525 | 33.4893 | 14.1507 | 33.4893 | 19.7018 | 0 | 18044.9953 | 17869.8012 | 2.1898 | 2.1552 | 9.7138 | 9.4679 | 18747.7842 | 10378.8303 | 0.80802 | 0.25277 | 4.7667 | 0.82549 | 23.6 | 9.6 | 5.049 | 12.2718 | 1.2119 | 1.0863 | 79.7 | 40.5 | 39.85 | 20.25 | 0 | 119.55 | 60.75 | 8.1341 | 6.205 | 0 | 715.35 | 715.35 | 579.8252 | 2371.4256 | 22887.0167 | 22887.0167 | 25973.7923 | -1.4779e-12 | 103.4812 | 25973.7923 | 2371.4256 | 715.35 | 1267.2874 | 21619.7292
| and 100% load scenario tabs. The bin-group calculation method was | AD | 61 | 308 | 49.6315 | 39.36 | 44.69% | 0.0053243 | 20.42 | 1114.2039 | 60.3 | 108.4983 | 144.6643 | 19.9742 | 74.18% | 77.9263 | 77.5263 | 0.006946 | 0.013892 | 26.1505 | 33.4369 | 0 | Heat-Hum | 9.3036 | 1.0775 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.9263 | 19.9742 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 61 | 73.1 | 49.6315 | 4" MERV 8 | 4" MERV 8 | 74.18% | 1 | 168.5455 | 114.6018 | 52.7967 | 34.4208 | 48.5061 | 34.4208 | 4.2907 | 0 | 29375.858 | 19971.3522 | 2.9524 | 1.6317 | 21.3208 | 8.0119 | 29193.0541 | 4705.0916 | 1.3819 | 0.044103 | 12.694 | 0.065295 | 32.7273 | 8.1583 | 5.6725 | 14.8375 | 1.1942 | 1.0528 | 145.5 | 35.6 | 72.75 | 17.8 | 0 | 218.25 | 53.4 | 9.8062 | 3.9224 | 0 | 0 | 0 | 908.6 | 0 | 0 | 168.5455 | 114.75 | 52.7818 | 34.4633 | 48.4834 | 34.4633 | 4.2984 | 0 | 29339.2726 | 19972.2775 | 2.947 | 1.6319 | 21.2555 | 8.0133 | 29156.0382 | 4712.4025 | 1.3788 | 0.044231 | 12.6498 | 0.065587 | 32.6364 | 8.1583 | 5.6868 | 14.8565 | 1.1936 | 1.0528 | 145.4 | 35.6 | 72.7 | 17.8 | 0 | 218.1 | 53.4 | 9.7961 | 3.9273 | 0 | 25127.6667 | 85.2261 | 64.2261 | 1259.52 | 111.24 | 65 | 64.2261 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 61 | 75 | 49.6315 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8525 | 33.4851 | 14.1507 | 33.4851 | 19.7018 | 0 | 18044.9953 | 17844.4584 | 2.1898 | 2.151 | 9.7138 | 9.4494 | 18747.7842 | 10505.7462 | 0.80802 | 0.2579 | 4.7667 | 0.85256 | 23.6 | 9.6 | 5.049 | 12.2744 | 1.2119 | 1.0862 | 79.7 | 39 | 39.85 | 19.5 | 0 | 119.55 | 58.5 | 8.1341 | 5.9704 | 0 | 908.6 | 908.6 | 747.2213 | 3116.053 | 28084.4667 | 28084.4667 | 32109.1197 | -1.3642e-12 | 104.2504 | 32109.1197 | 3116.053 | 908.6 | 1555.0778 | 26529.3889
| attractive to me because it required only 49 iterations of inputs & outputs per | AE | 59 | 266 | 47.9132 | 37.22 | 44.14% | 0.0048929 | 19.47 | 953.2519 | 59.7 | 93.524 | 124.6986 | 19.977 | 74.19% | 77.5826 | 77.1826 | 0.006946 | 0.013892 | 26.0673 | 33.3537 | 0 | Heat-Hum | 10.7109 | 1.3641 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.5826 | 19.977 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 59 | 73.1 | 47.9132 | 4" MERV 8 | 4" MERV 8 | 74.19% | 1 | 168.5455 | 114.6179 | 52.7951 | 34.4239 | 48.5036 | 34.4239 | 4.2915 | 0 | 29371.8731 | 19959.1432 | 2.9518 | 1.6304 | 21.3137 | 8.0056 | 29189.0139 | 4584.2718 | 1.3816 | 0.04195 | 12.6892 | 0.060514 | 32.7182 | 8.1417 | 5.6741 | 14.864 | 1.1941 | 1.0527 | 145.5 | 35 | 72.75 | 17.5 | 0 | 218.25 | 52.5 | 9.805 | 3.8629 | 0 | 0 | 215.9033 | 798 | 0 | 0 | 168.5455 | 114.75 | 52.7818 | 34.4618 | 48.4834 | 34.4618 | 4.2984 | 0 | 29339.2726 | 19959.9679 | 2.947 | 1.6306 | 21.2555 | 8.0068 | 29156.0382 | 4590.5402 | 1.3788 | 0.042058 | 12.6498 | 0.060752 | 32.6364 | 8.1417 | 5.6868 | 14.881 | 1.1936 | 1.0527 | 145.4 | 35.1 | 72.7 | 17.55 | 0 | 218.1 | 52.65 | 9.7961 | 3.8671 | 0 | 21656.8333 | 81.6176 | 60.6176 | 1259.52 | 111.24 | 65 | 60.6176 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 59 | 75 | 47.9132 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8525 | 33.4656 | 14.1507 | 33.4656 | 19.7018 | 0 | 18044.9953 | 17726.2858 | 2.1898 | 2.1315 | 9.7138 | 9.3637 | 18747.7842 | 12695.9269 | 0.80802 | 0.37159 | 4.7667 | 1.4845 | 23.6 | 10 | 5.049 | 11.7462 | 1.2119 | 1.0901 | 79.7 | 40.3 | 39.85 | 20.15 | 0 | 119.55 | 60.45 | 8.1341 | 6.1699 | 0 | 798 | 798 | 710.2106 | 3065.4704 | 24316.8333 | 24316.8333 | 28180.3038 | 0 | 105.941 | 28180.3038 | 3065.4704 | 798 | 1343.0217 | 22973.8116
| zone per scenario for the manufacturer's tool, as opposed to 8760 iterations | AF | 57 | 282 | 46.766 | 36.61 | 46.29% | 0.0047757 | 18.85 | 1021.5681 | 59 | 101.1002 | 134.8003 | 19.9742 | 74.18% | 77.3532 | 76.9532 | 0.006946 | 0.013892 | 26.0118 | 33.2982 | 0 | Heat-Hum | 11.6273 | 1.4419 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.3532 | 19.9742 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 57 | 73.1 | 46.766 | 4" MERV 8 | 4" MERV 8 | 74.18% | 1 | 168.5455 | 114.6022 | 52.7967 | 34.4185 | 48.506 | 34.4185 | 4.2907 | 0 | 29375.7556 | 19950.8269 | 2.9524 | 1.6295 | 21.3206 | 8.0012 | 29192.9503 | 4515.7587 | 1.3819 | 0.040673 | 12.6939 | 0.057794 | 32.7273 | 8.1333 | 5.6726 | 14.8776 | 1.1942 | 1.0526 | 145.5 | 34.3 | 72.75 | 17.15 | 0 | 218.25 | 51.45 | 9.8062 | 3.787 | 0 | 0 | 686.67 | 846 | 0 | 0 | 168.5455 | 114.75 | 52.7818 | 34.4608 | 48.4834 | 34.4608 | 4.2984 | 0 | 29339.2726 | 19951.7496 | 2.947 | 1.6297 | 21.2555 | 8.0025 | 29156.0382 | 4522.6035 | 1.3788 | 0.040788 | 12.6498 | 0.058046 | 32.6364 | 8.1333 | 5.6868 | 14.8966 | 1.1936 | 1.0526 | 145.4 | 34.4 | 72.7 | 17.2 | 0 | 218.1 | 51.6 | 9.7961 | 3.7917 | 0 | 22936 | 79.2085 | 58.2085 | 1259.52 | 111.24 | 65 | 58.2085 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 57 | 75 | 46.766 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8525 | 33.4526 | 14.1507 | 33.4526 | 19.7018 | 0 | 18044.9953 | 17647.391 | 2.1898 | 2.1185 | 9.7138 | 9.3067 | 18747.7842 | 14534.9907 | 0.80802 | 0.48199 | 4.7667 | 2.2044 | 23.6 | 10.6 | 5.049 | 11.1367 | 1.2119 | 1.0949 | 79.7 | 40.4 | 39.85 | 20.2 | 0 | 119.55 | 60.6 | 8.1341 | 6.1866 | 0 | 846 | 846 | 797.7229 | 3508.2855 | 25925.2 | 25925.2 | 30279.4855 | 0 | 107.3741 | 30279.4855 | 3508.2855 | 846 | 1423.805 | 24501.395
| per zone per scenario... even though that is possible. I did use the full 8760 | AG | 55 | 284 | 45.3053 | 35.21 | 47.08% | 0.0045143 | 18.09 | 1042.1465 | 58.4 | 103.9008 | 138.5343 | 19.9726 | 74.17% | 77.0611 | 76.6611 | 0.006946 | 0.013892 | 25.9411 | 33.2275 | 0 | Heat-Hum | 12.7463 | 1.6156 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.0611 | 19.9726 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 55 | 73.1 | 45.3053 | 4" MERV 8 | 4" MERV 8 | 74.17% | 1 | 168.5455 | 114.5926 | 52.7977 | 34.4145 | 48.5075 | 34.4145 | 4.2902 | 0 | 29378.1329 | 19940.303 | 2.9527 | 1.6284 | 21.3249 | 7.9956 | 29195.3547 | 4433.3173 | 1.3821 | 0.039206 | 12.6967 | 0.054692 | 32.7273 | 8.125 | 5.6716 | 14.8956 | 1.1942 | 1.0526 | 145.5 | 33.8 | 72.75 | 16.9 | 0 | 218.25 | 50.7 | 9.8068 | 3.7222 | 0 | 0 | 1152.5667 | 852 | 0 | 0 | 168.5455 | 114.75 | 52.7818 | 34.4596 | 48.4834 | 34.4596 | 4.2984 | 0 | 29339.2726 | 19941.2858 | 2.947 | 1.6286 | 21.2555 | 7.9971 | 29156.0382 | 4440.3976 | 1.3788 | 0.039323 | 12.6498 | 0.054943 | 32.6364 | 8.125 | 5.6868 | 14.9159 | 1.1936 | 1.0526 | 145.4 | 33.8 | 72.7 | 16.9 | 0 | 218.1 | 50.7 | 9.7961 | 3.7271 | 0 | 23075 | 76.1411 | 55.1411 | 1259.52 | 111.24 | 65 | 55.1411 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 55 | 75 | 45.3053 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8525 | 33.4387 | 14.1507 | 33.4387 | 19.7018 | 0 | 18044.9953 | 17556.3912 | 2.1898 | 2.1047 | 9.7138 | 9.2459 | 18747.7842 | 16966.7067 | 0.80802 | 0.65016 | 4.7667 | 3.4711 | 23.6 | 11.6 | 5.049 | 10.1589 | 1.2119 | 1.104 | 79.7 | 41.2 | 39.85 | 20.6 | 0 | 119.55 | 61.8 | 8.1341 | 6.3143 | 0 | 852 | 852 | 858.4667 | 3850.9787 | 26369.4 | 26369.4 | 31072.3787 | 0 | 109.4098 | 31072.3787 | 3850.9787 | 852 | 1433.9029 | 24935.4971
| annual hour calculation method to sychronize the data center operation with | AH | 53 | 273 | 44.43 | 35.38 | 51% | 0.0045457 | 17.64 | 1084.8425 | 57.7 | 109.0853 | 145.4471 | 19.9701 | 74.16% | 76.886 | 76.486 | 0.0066891 | 0.013378 | 25.6292 | 32.6461 | 0 | Heat-Hum | 12.9705 | 1.4241 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.886 | 19.9701 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 53 | 73.1 | 44.43 | 4" MERV 8 | 4" MERV 8 | 74.16% | 1 | 168.5455 | 114.5785 | 52.7998 | 34.4099 | 48.5102 | 34.4099 | 4.2897 | 0 | 29383.4138 | 19935.1642 | 2.9535 | 1.6278 | 21.3343 | 7.9933 | 29212.4266 | 4394.5788 | 1.3835 | 0.038429 | 12.7172 | 0.053141 | 32.7545 | 8.1167 | 5.6674 | 14.9031 | 1.1943 | 1.0525 | 145.6 | 33 | 72.8 | 16.5 | 0 | 218.4 | 49.5 | 9.8108 | 3.641 | 0 | 0 | 1551.095 | 819 | 0 | 0 | 168.5455 | 114.75 | 52.7826 | 34.4591 | 48.484 | 34.4591 | 4.2986 | 0 | 29341.0671 | 19936.2351 | 2.9473 | 1.628 | 21.2587 | 7.9949 | 29169.5822 | 4402.1671 | 1.3799 | 0.038554 | 12.6659 | 0.053405 | 32.6545 | 8.1167 | 5.6839 | 14.9252 | 1.1937 | 1.0525 | 145.4 | 33.1 | 72.7 | 16.55 | 0 | 218.1 | 49.65 | 9.7993 | 3.6462 | 0 | 22158.5 | 74.3031 | 53.3031 | 1259.52 | 111.24 | 65 | 53.3031 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 53 | 75 | 44.43 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8529 | 33.435 | 14.1509 | 33.435 | 19.7019 | 0 | 18046.099 | 17532.7827 | 2.1899 | 2.1009 | 9.7151 | 9.2295 | 18756.3342 | 16943.6102 | 0.80863 | 0.64633 | 4.7725 | 3.4459 | 23.6 | 11.5 | 5.0477 | 10.1983 | 1.212 | 1.1036 | 79.7 | 38.8 | 39.85 | 19.4 | 0 | 119.55 | 58.2 | 8.1373 | 5.9368 | 0 | 819 | 819 | 835.826 | 3763.0325 | 25298 | 25298 | 29880.0325 | 0 | 109.4507 | 29880.0325 | 3763.0325 | 819 | 1378.011 | 23919.989
| the cafeteria heat recovery input, and to create chronological tallies of water | AI | 51 | 156 | 42.7795 | 33.57 | 51.07% | 0.0042271 | 16.81 | 1146.7615 | 57 | 116.2923 | 155.0564 | 19.9669 | 74.15% | 76.5559 | 76.1559 | 0.0066891 | 0.013378 | 25.5493 | 32.5661 | 0 | Heat-Hum | 14.1883 | 1.6357 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.5559 | 19.9669 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 51 | 73.1 | 42.7795 | 4" MERV 8 | 4" MERV 8 | 74.15% | 1 | 168.5455 | 114.56 | 52.8017 | 34.4032 | 48.513 | 34.4032 | 4.2887 | 0 | 29387.9895 | 19923.224 | 2.9542 | 1.6265 | 21.3425 | 7.987 | 29217.0645 | 4314.0304 | 1.3839 | 0.037041 | 12.7227 | 0.050281 | 32.7636 | 8.1083 | 5.6656 | 14.9215 | 1.1944 | 1.0525 | 145.6 | 32.5 | 72.8 | 16.25 | 0 | 218.4 | 48.75 | 9.8121 | 3.5839 | 0 | 0 | 1139.58 | 468 | 0 | 0 | 168.5455 | 114.75 | 52.7826 | 34.4577 | 48.484 | 34.4577 | 4.2986 | 0 | 29341.0671 | 19924.4103 | 2.9473 | 1.6268 | 21.2587 | 7.9887 | 29169.5822 | 4322.192 | 1.3799 | 0.037172 | 12.6659 | 0.050555 | 32.6545 | 8.1083 | 5.6839 | 14.9461 | 1.1937 | 1.0525 | 145.4 | 32.6 | 72.7 | 16.3 | 0 | 218.1 | 48.9 | 9.7993 | 3.5896 | 0 | 12649 | 70.8369 | 49.8369 | 1259.52 | 111.24 | 65 | 49.8369 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 51 | 75 | 42.7795 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8529 | 33.4276 | 14.1509 | 33.4276 | 19.7019 | 0 | 18046.099 | 17486.9502 | 2.1899 | 2.0934 | 9.7151 | 9.1969 | 18756.3342 | 16885.4881 | 0.80863 | 0.64111 | 4.7725 | 3.4064 | 23.6 | 11.4 | 5.0477 | 10.2684 | 1.212 | 1.1029 | 79.7 | 37.6 | 39.85 | 18.8 | 0 | 119.55 | 56.4 | 8.1373 | 5.759 | 0 | 671.58 | 671.58 | 510.5428 | 2340.2774 | 14427.4 | 14427.4 | 17439.2574 | 3.638e-12 | 111.7901 | 17439.2574 | 2340.2774 | 671.58 | 787.4348 | 13639.9652
| & potential fuel oil use, in order to calculate the tank sizes you see at top of | AJ | 49 | 258 | 41.8876 | 33.83 | 55.6% | 0.0042714 | 16.37 | 1117.462 | 56.4 | 114.1402 | 152.187 | 19.9662 | 74.15% | 76.3775 | 75.9775 | 0.0066891 | 0.013378 | 25.5061 | 32.523 | 0 | Heat-Hum | 14.8326 | 1.6063 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.3775 | 19.9662 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 49 | 73.1 | 41.8876 | 4" MERV 8 | 4" MERV 8 | 74.15% | 1 | 168.5455 | 114.5559 | 52.8021 | 34.4013 | 48.5136 | 34.4013 | 4.2885 | 0 | 29389.0027 | 19916.8088 | 2.9543 | 1.6258 | 21.3443 | 7.9836 | 29218.09 | 4279.2623 | 1.384 | 0.036352 | 12.7239 | 0.048949 | 32.7727 | 8.1 | 5.6652 | 14.9319 | 1.1944 | 1.0524 | 145.6 | 31.8 | 72.8 | 15.9 | 0 | 218.4 | 47.7 | 9.8124 | 3.5056 | 0 | 0 | 2303.51 | 774 | 0 | 0 | 168.5455 | 114.75 | 52.7826 | 34.4569 | 48.484 | 34.4569 | 4.2986 | 0 | 29341.0671 | 19918.0207 | 2.9473 | 1.6261 | 21.2587 | 7.9854 | 29169.5822 | 4287.4734 | 1.3799 | 0.036483 | 12.6659 | 0.04922 | 32.6545 | 8.1 | 5.6839 | 14.9571 | 1.1937 | 1.0524 | 145.4 | 31.8 | 72.7 | 15.9 | 0 | 218.1 | 47.7 | 9.7993 | 3.5112 | 0 | 20898 | 68.964 | 47.964 | 1259.52 | 111.24 | 65 | 47.964 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 49 | 75 | 41.8876 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8529 | 33.4235 | 14.1509 | 33.4235 | 19.7019 | 0 | 18046.099 | 17462.113 | 2.1899 | 2.0894 | 9.7151 | 9.1792 | 18756.3342 | 16854.5337 | 0.80863 | 0.63685 | 4.7725 | 3.3775 | 23.6 | 11.4 | 5.0477 | 10.3126 | 1.212 | 1.1024 | 79.7 | 35.2 | 39.85 | 17.6 | 0 | 119.55 | 52.8 | 8.1373 | 5.3839 | 0 | 1529.51 | 1529.51 | 873.1691 | 4036.6727 | 23839.2 | 23839.2 | 29405.3827 | 0 | 113.9744 | 29405.3827 | 4036.6727 | 1529.51 | 1302.2961 | 22536.9039
| the Summary tab. | AK | 47 | 418 | 40.4057 | 32.57 | 56.99% | 0.00406 | 15.66 | 1084.2727 | 55.7 | 111.6775 | 148.9034 | 19.9655 | 74.14% | 76.0811 | 75.6811 | 0.0066891 | 0.013378 | 25.4344 | 32.4512 | 0 | Heat-Hum | 15.8688 | 1.7468 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.0811 | 19.9655 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 47 | 73.1 | 40.4057 | 4" MERV 8 | 4" MERV 8 | 74.14% | 1 | 168.5455 | 114.552 | 52.8025 | 34.3989 | 48.5142 | 34.3989 | 4.2883 | 0 | 29389.9659 | 19906.1682 | 2.9545 | 1.6247 | 21.3461 | 7.978 | 29219.0651 | 4219.1679 | 1.384 | 0.035307 | 12.7251 | 0.046874 | 32.7727 | 8.0917 | 5.6649 | 14.9493 | 1.1944 | 1.0524 | 145.6 | 31.3 | 72.8 | 15.65 | 0 | 218.4 | 46.95 | 9.8127 | 3.4456 | 0 | 0 | 4410.5967 | 1254 | 0 | 0 | 168.5455 | 114.75 | 52.7826 | 34.4556 | 48.484 | 34.4556 | 4.2986 | 0 | 29341.0671 | 19907.4045 | 2.9473 | 1.625 | 21.2587 | 7.9798 | 29169.5822 | 4227.3447 | 1.3799 | 0.035435 | 12.6659 | 0.047136 | 32.6545 | 8.0917 | 5.6839 | 14.9751 | 1.1937 | 1.0524 | 145.4 | 31.3 | 72.7 | 15.65 | 0 | 218.1 | 46.95 | 9.7993 | 3.4512 | 0 | 33823.1667 | 65.8521 | 44.8521 | 1259.52 | 111.24 | 65 | 44.8521 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 47 | 75 | 40.4057 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8529 | 33.4169 | 14.1509 | 33.4169 | 19.7019 | 0 | 18046.099 | 17421.2318 | 2.1899 | 2.0828 | 9.7151 | 9.1502 | 18756.3342 | 16803.3227 | 0.80863 | 0.63193 | 4.7725 | 3.3413 | 23.6 | 11.3 | 5.0477 | 10.3771 | 1.212 | 1.1018 | 79.7 | 33.7 | 39.85 | 16.85 | 0 | 119.55 | 50.55 | 8.1373 | 5.1611 | 0 | 3156.5967 | 3156.5967 | 1489.7449 | 6973.1734 | 38546.5667 | 38546.5667 | 48676.3368 | 0 | 116.4506 | 48676.3368 | 6973.1734 | 3156.5967 | 2109.9215 | 36436.6451
|  | AL | 45 | 287 | 39.3812 | 32.57 | 61.48% | 0.00406 | 15.18 | 1099.57 | 55.1 | 114.0592 | 152.0789 | 19.9632 | 74.14% | 75.8762 | 75.4762 | 0.006485 | 0.01297 | 25.1706 | 31.9734 | 0 | Heat-Hum | 16.2199 | 1.6111 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.8762 | 19.9632 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 45 | 73.1 | 39.3812 | 4" MERV 8 | 4" MERV 8 | 74.14% | 1 | 168.5455 | 114.5388 | 52.8045 | 34.3945 | 48.5167 | 34.3945 | 4.2877 | 0 | 29394.8016 | 19899.8067 | 2.9552 | 1.624 | 21.3547 | 7.975 | 29234.1856 | 4184.6299 | 1.3853 | 0.034642 | 12.7432 | 0.045615 | 32.8 | 8.0833 | 5.6611 | 14.9582 | 1.1946 | 1.0523 | 145.7 | 30.6 | 72.85 | 15.3 | 0 | 218.55 | 45.9 | 9.8162 | 3.3723 | 0 | 0 | 3494.225 | 861 | 0 | 0 | 168.5455 | 114.75 | 52.7832 | 34.455 | 48.4845 | 34.455 | 4.2987 | 0 | 29342.6315 | 19901.1255 | 2.9475 | 1.6243 | 21.2615 | 7.9769 | 29181.3729 | 4193.2204 | 1.3809 | 0.034776 | 12.68 | 0.045886 | 32.6636 | 8.0833 | 5.6814 | 14.9857 | 1.1938 | 1.0523 | 145.5 | 30.6 | 72.75 | 15.3 | 0 | 218.25 | 45.9 | 9.802 | 3.3782 | 0 | 23199.1667 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 45 | 75 | 39.3812 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8531 | 33.4359 | 14.1512 | 33.4359 | 19.702 | 0 | 18047.0612 | 17544.3259 | 2.1901 | 2.1017 | 9.7163 | 9.2335 | 18763.7881 | 11260.5025 | 0.80916 | 0.28922 | 4.7775 | 1.0248 | 23.6 | 9.4 | 5.0465 | 12.4684 | 1.212 | 1.0848 | 79.7 | 29.5 | 39.85 | 14.75 | 0 | 119.55 | 44.25 | 8.1401 | 4.5208 | 0 | 2633.225 | 2633.225 | 1040.3292 | 4888.569 | 25896.9667 | 25896.9667 | 33418.7607 | 0 | 116.4417 | 33418.7607 | 4888.569 | 2633.225 | 1448.3542 | 24448.6125
3. | At least one manufacturer of IDEC cooling equipment maintains a | AM | 43 | 392 | 37.6204 | 30.82 | 61.46% | 0.0037586 | 14.37 | 1084.4031 | 54.4 | 113.4134 | 151.2178 | 19.9617 | 74.13% | 75.5241 | 75.1241 | 0.006485 | 0.01297 | 25.0854 | 31.8881 | 0 | Heat-Hum | 17.3965 | 1.8114 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.5241 | 19.9617 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 43 | 73.1 | 37.6204 | 4" MERV 8 | 4" MERV 8 | 74.13% | 1 | 168.5455 | 114.5302 | 52.8053 | 34.3905 | 48.518 | 34.3905 | 4.2873 | 0 | 29396.9231 | 19887.138 | 2.9555 | 1.6227 | 21.3585 | 7.9683 | 29236.3325 | 4122.3256 | 1.3855 | 0.033599 | 12.7458 | 0.043583 | 32.8 | 8.075 | 5.6603 | 14.9778 | 1.1946 | 1.0523 | 145.7 | 30.1 | 72.85 | 15.05 | 0 | 218.55 | 45.15 | 9.8168 | 3.3212 | 0 | 0 | 5408.9467 | 1176 | 0 | 0 | 168.5455 | 114.75 | 52.7832 | 34.4535 | 48.4845 | 34.4535 | 4.2987 | 0 | 29342.6315 | 19888.5103 | 2.9475 | 1.623 | 21.2615 | 7.9703 | 29181.3729 | 4131.0367 | 1.3809 | 0.033733 | 12.68 | 0.043849 | 32.6636 | 8.075 | 5.6814 | 15.0065 | 1.1938 | 1.0522 | 145.5 | 30.2 | 72.75 | 15.1 | 0 | 218.25 | 45.3 | 9.802 | 3.3272 | 0 | 31654 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 43 | 75 | 37.6204 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8531 | 33.4359 | 14.1512 | 33.4359 | 19.702 | 0 | 18047.0612 | 17544.3259 | 2.1901 | 2.1017 | 9.7163 | 9.2335 | 18763.7881 | 10166.2527 | 0.80916 | 0.23682 | 4.7775 | 0.75758 | 23.6 | 9.2 | 5.0465 | 12.7835 | 1.212 | 1.0827 | 79.7 | 28.5 | 39.85 | 14.25 | 0 | 119.55 | 42.75 | 8.1401 | 4.3584 | 0 | 4232.9467 | 4232.9467 | 1500.8847 | 7138.3136 | 35260.4 | 35260.4 | 46631.6603 | 0 | 118.9583 | 46631.6603 | 7138.3136 | 4232.9467 | 1978.2398 | 33282.1602
| spreadsheet-based performance tool. That expert tool is what I used to | AN | 41 | 329 | 36.0012 | 29.5 | 62.46% | 0.0035343 | 13.64 | 965.2833 | 53.7 | 101.7807 | 135.7076 | 19.9639 | 74.14% | 75.2002 | 74.8002 | 0.006485 | 0.01297 | 25.007 | 31.8097 | 0 | Heat-Hum | 18.4544 | 1.9604 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.2002 | 19.9639 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 41 | 73.1 | 36.0012 | 4" MERV 8 | 4" MERV 8 | 74.14% | 1 | 168.5455 | 114.5431 | 52.804 | 34.3928 | 48.516 | 34.3928 | 4.288 | 0 | 29393.7254 | 19875.618 | 2.955 | 1.6214 | 21.3528 | 7.9624 | 29233.1046 | 4072.1103 | 1.3852 | 0.032744 | 12.7419 | 0.041957 | 32.7909 | 8.0667 | 5.6615 | 14.9982 | 1.1946 | 1.0522 | 145.7 | 29.6 | 72.85 | 14.8 | 0 | 218.55 | 44.4 | 9.816 | 3.2667 | 0 | 0 | 5073.7283 | 987 | 0 | 0 | 168.5455 | 114.75 | 52.7832 | 34.4521 | 48.4845 | 34.4521 | 4.2987 | 0 | 29342.6315 | 19876.9096 | 2.9475 | 1.6217 | 21.2615 | 7.9643 | 29181.3729 | 4080.1289 | 1.3809 | 0.032866 | 12.68 | 0.042195 | 32.6636 | 8.0583 | 5.6814 | 15.0253 | 1.1938 | 1.0522 | 145.5 | 29.7 | 72.75 | 14.85 | 0 | 218.25 | 44.55 | 9.802 | 3.2722 | 0 | 26511.9167 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 41 | 75 | 36.0012 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8531 | 33.4359 | 14.1512 | 33.4359 | 19.702 | 0 | 18047.0612 | 17544.3259 | 2.1901 | 2.1017 | 9.7163 | 9.2335 | 18763.7881 | 9347.5462 | 0.80916 | 0.20085 | 4.7775 | 0.59075 | 23.6 | 9.1 | 5.0465 | 12.9885 | 1.212 | 1.0814 | 79.7 | 27.4 | 39.85 | 13.7 | 0 | 119.55 | 41.1 | 8.1401 | 4.2026 | 0 | 4086.7283 | 4086.7283 | 1319.9977 | 6339.1305 | 29533.2333 | 29505.8167 | 39931.6755 | -4.5475e-12 | 121.3729 | 39931.6755 | 6339.1305 | 4086.7283 | 1660.3084 | 27845.5082
| transform each unique bin's "Input" row of data to the horizontally-adjacent | AO | 39 | 281 | 34.1466 | 27.62 | 61.86% | 0.0032371 | 12.84 | 1097.1609 | 53.1 | 116.4903 | 155.3204 | 19.9566 | 74.11% | 74.8293 | 74.4293 | 0.0062436 | 0.012487 | 24.664 | 31.2135 | 0 | Heat-Hum | 19.1964 | 1.9975 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.8293 | 19.9566 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 39 | 73.1 | 34.1466 | 4" MERV 8 | 4" MERV 8 | 74.11% | 1 | 168.5455 | 114.5011 | 52.809 | 34.3795 | 48.5231 | 34.3795 | 4.286 | 0 | 29405.9839 | 19863.3197 | 2.9568 | 1.6201 | 21.3747 | 7.9562 | 29257.6146 | 4019.3409 | 1.3872 | 0.031868 | 12.7713 | 0.040305 | 32.8364 | 8.05 | 5.6545 | 15.0119 | 1.1948 | 1.0521 | 145.8 | 29.2 | 72.9 | 14.6 | 0 | 218.7 | 43.8 | 9.8221 | 3.217 | 0 | 0 | 4789.645 | 843 | 0 | 0 | 168.5455 | 114.75 | 52.784 | 34.4508 | 48.485 | 34.4508 | 4.2989 | 0 | 29344.4804 | 19864.8739 | 2.9478 | 1.6204 | 21.2648 | 7.9585 | 29195.3278 | 4028.7636 | 1.3821 | 0.032009 | 12.6967 | 0.040578 | 32.6818 | 8.05 | 5.6785 | 15.0445 | 1.1939 | 1.0521 | 145.5 | 29.2 | 72.75 | 14.6 | 0 | 218.25 | 43.8 | 9.8053 | 3.2235 | 0 | 22620.5 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 39 | 75 | 34.1466 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8534 | 33.4362 | 14.1514 | 33.4362 | 19.7021 | 0 | 18048.1984 | 17545.4314 | 2.1903 | 2.1018 | 9.7177 | 9.2348 | 18772.5974 | 8579.5237 | 0.80979 | 0.16977 | 4.7835 | 0.45832 | 23.6 | 8.9 | 5.0452 | 13.1544 | 1.2121 | 1.0803 | 79.8 | 26.7 | 39.9 | 13.35 | 0 | 119.7 | 40.05 | 8.1434 | 4.0914 | 0 | 3946.645 | 3946.645 | 1163.5522 | 5622.7637 | 25121.4 | 25121.4 | 34690.8087 | 0 | 123.4548 | 34690.8087 | 5622.7637 | 3946.645 | 1417.7 | 23703.7
| "output" line of data that you see here. They are recorded like a series of | AP | 37 | 392 | 33.0765 | 27.79 | 67.47% | 0.0032643 | 12.39 | 1036.3485 | 52.4 | 110.92 | 147.8933 | 19.9565 | 74.11% | 74.6153 | 74.2153 | 0.0062436 | 0.012487 | 24.6122 | 31.1617 | 0 | Heat-Hum | 19.8429 | 1.9794 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.6153 | 19.9565 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 37 | 73.1 | 33.0765 | 4" MERV 8 | 4" MERV 8 | 74.11% | 1 | 168.5455 | 114.5002 | 52.8091 | 34.3783 | 48.5232 | 34.3783 | 4.2859 | 0 | 29406.2089 | 19855.6469 | 2.9569 | 1.6193 | 21.3751 | 7.9522 | 29257.8341 | 9804.6653 | 1.3873 | 0.1366 | 12.7716 | 0.42142 | 32.8364 | 7.025 | 5.6544 | 17.2158 | 1.1948 | 1.0454 | 145.8 | 0 | 72.9 | 0 | 0 | 218.7 | 0 | 9.8221 | 0 | 0 | 0 | 7317.9867 | 1176 | 0 | 0 | 168.5455 | 114.75 | 52.784 | 34.4499 | 48.485 | 34.4499 | 4.2989 | 0 | 29344.4804 | 19857.2068 | 2.9478 | 1.6196 | 21.2648 | 7.9545 | 29195.3278 | 9820.4432 | 1.3821 | 0.13705 | 12.6967 | 0.4235 | 32.6818 | 7.025 | 5.6785 | 17.2425 | 1.1939 | 1.0455 | 145.5 | 0 | 72.75 | 0 | 0 | 218.25 | 0 | 9.8053 | 0 | 0 | 27538 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 37 | 75 | 33.0765 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8534 | 33.4451 | 14.1514 | 33.4451 | 19.7021 | 0 | 18048.1984 | 17581.3226 | 2.1903 | 2.1107 | 9.7177 | 9.274 | 18772.5974 | 16928.4712 | 0.80979 | 0.56519 | 4.7835 | 3.0106 | 23.6 | 10.3 | 5.0452 | 11.4171 | 1.2121 | 1.0926 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1434 | 0 | 0 | 6141.9867 | 6141.9867 | 1667.1004 | 8097.2709 | 31575.6 | 31575.6 | 45814.8576 | 0 | 116.8746 | 45814.8576 | 8097.2709 | 6141.9867 | 1977.7167 | 29597.8833
| snapshots, and there are several scenes occuring in each bin. | AQ | 35 | 453 | 31.6302 | 27 | 70.36% | 0.0031443 | 11.77 | 1108.0419 | 51.8 | 119.4056 | 159.2074 | 19.9504 | 74.09% | 74.326 | 73.926 | 0.0062436 | 0.012487 | 24.5422 | 31.0917 | 0 | Heat-Hum | 20.7357 | 2.0592 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.326 | 19.9504 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 35 | 73.1 | 31.6302 | 4" MERV 8 | 4" MERV 8 | 74.09% | 1 | 168.5455 | 114.4657 | 52.8126 | 34.3672 | 48.5285 | 34.3672 | 4.2841 | 0 | 29414.7496 | 19845.069 | 2.9581 | 1.6181 | 21.3904 | 7.9465 | 29266.4838 | 9406.2139 | 1.388 | 0.12604 | 12.782 | 0.37306 | 32.8545 | 6.9667 | 5.6511 | 17.3345 | 1.195 | 1.0451 | 145.8 | 0 | 72.9 | 0 | 0 | 218.7 | 0 | 9.8244 | 0 | 0 | 0 | 9192.125 | 1359 | 0 | 0 | 168.5455 | 114.75 | 52.784 | 34.4486 | 48.485 | 34.4486 | 4.2989 | 0 | 29344.4804 | 19846.8441 | 2.9478 | 1.6185 | 21.2648 | 7.9491 | 29195.3278 | 9423.3707 | 1.3821 | 0.12651 | 12.6967 | 0.37514 | 32.6818 | 6.975 | 5.6785 | 17.3657 | 1.1939 | 1.0451 | 145.5 | 0 | 72.75 | 0 | 0 | 218.25 | 0 | 9.8053 | 0 | 0 | 31596.75 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 35 | 75 | 31.6302 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8534 | 33.4362 | 14.1514 | 33.4362 | 19.7021 | 0 | 18048.1984 | 17545.4314 | 2.1903 | 2.1018 | 9.7177 | 9.2348 | 18772.5974 | 16218.8765 | 0.80979 | 0.51895 | 4.7835 | 2.6484 | 23.6 | 9.9 | 5.0452 | 11.8312 | 1.2121 | 1.0893 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1434 | 0 | 0 | 7833.125 | 7833.125 | 1996.6302 | 9761.7867 | 36043.7 | 36081.45 | 53676.3617 | 7.276e-12 | 118.4909 | 53676.3617 | 9761.7867 | 7833.125 | 2285.4736 | 33795.9764
|  | AR | 33 | 264 | 30.7235 | 27.56 | 78.25% | 0.0032286 | 11.38 | 964.9864 | 51.1 | 104.8148 | 139.7531 | 19.9539 | 74.1% | 74.1447 | 73.7447 | 0.0062436 | 0.012487 | 24.4983 | 31.0478 | 0 | Heat-Hum | 21.2976 | 2.0032 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.1447 | 19.9539 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 33 | 73.1 | 30.7235 | 4" MERV 8 | 4" MERV 8 | 74.1% | 1 | 168.5455 | 114.4853 | 52.8106 | 34.372 | 48.5255 | 34.372 | 4.2852 | 0 | 29409.8902 | 19838.6945 | 2.9574 | 1.6175 | 21.3817 | 7.9433 | 29261.5707 | 9031.696 | 1.3876 | 0.1165 | 12.7761 | 0.33108 | 32.8455 | 6.9333 | 5.653 | 17.4405 | 1.1949 | 1.0449 | 145.8 | 0 | 72.9 | 0 | 0 | 218.7 | 0 | 9.8232 | 0 | 0 | 0 | 5785.56 | 792 | 0 | 0 | 168.5455 | 114.75 | 52.784 | 34.4479 | 48.485 | 34.4479 | 4.2989 | 0 | 29344.4804 | 19840.3472 | 2.9478 | 1.6178 | 21.2648 | 7.9457 | 29195.3278 | 9046.9594 | 1.3821 | 0.1169 | 12.6967 | 0.33278 | 32.6818 | 6.9333 | 5.6785 | 17.4701 | 1.1939 | 1.0449 | 145.5 | 0 | 72.75 | 0 | 0 | 218.25 | 0 | 9.8053 | 0 | 0 | 18304 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 33 | 75 | 30.7235 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8534 | 33.4362 | 14.1514 | 33.4362 | 19.7021 | 0 | 18048.1984 | 17545.4314 | 2.1903 | 2.1018 | 9.7177 | 9.2348 | 18772.5974 | 14881.4178 | 0.80979 | 0.43708 | 4.7835 | 2.0467 | 23.6 | 9.4 | 5.0452 | 12.4892 | 1.2121 | 1.0846 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1434 | 0 | 0 | 4993.56 | 4993.56 | 1189.3109 | 5837.3288 | 20785.6 | 20785.6 | 31616.4888 | 0 | 119.7594 | 31616.4888 | 5837.3288 | 4993.56 | 1331.9317 | 19453.6683
4. | Knowing this, it should be possible to review my calculation (for any given | AS | 31 | 424 | 29.216 | 26.62 | 81.64% | 0.00309 | 10.75 | 1022.3825 | 50.4 | 111.9235 | 149.2313 | 19.9476 | 74.08% | 73.8432 | 73.4432 | 0.0060517 | 0.012103 | 24.224 | 30.5723 | 0 | Heat-Hum | 21.8752 | 1.9678 | 0 | 0 | 42.1 | 1259.52 | 1854 | 78 | 73.8432 | 19.9476 | 42.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 31 | 73.1 | 29.216 | 4" MERV 8 | 4" MERV 8 | 74.08% | 1 | 168.5455 | 114.4491 | 52.8149 | 34.3606 | 48.5315 | 34.3606 | 4.2834 | 0 | 29420.3222 | 19828.6559 | 2.959 | 1.6164 | 21.4004 | 7.9382 | 29281.7024 | 8710.8549 | 1.3892 | 0.10859 | 12.8003 | 0.29765 | 32.8818 | 6.8917 | 5.6472 | 17.5281 | 1.1951 | 1.0446 | 145.9 | 0 | 72.95 | 0 | 0 | 218.85 | 0 | 9.8281 | 0 | 0 | 0 | 9980.2533 | 1272 | 0 | 0 | 168.5455 | 114.75 | 52.7846 | 34.4468 | 48.4855 | 34.4468 | 4.2991 | 0 | 29345.9429 | 19830.5347 | 2.948 | 1.6168 | 21.2674 | 7.941 | 29206.3583 | 8727.5175 | 1.383 | 0.10901 | 12.7099 | 0.29938 | 32.7 | 6.9 | 5.6761 | 17.5624 | 1.194 | 1.0446 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8078 | 0 | 0 | 29256 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 42.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 31 | 75 | 29.216 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8537 | 33.4365 | 14.1516 | 33.4365 | 19.7021 | 0 | 18049.0979 | 17546.3058 | 2.1904 | 2.102 | 9.7188 | 9.2359 | 18779.5653 | 13738.6048 | 0.81029 | 0.37257 | 4.7882 | 1.6106 | 23.6 | 9 | 5.0441 | 13.0125 | 1.2121 | 1.0812 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.146 | 0 | 0 | 8708.2533 | 8708.2533 | 1952.5507 | 9619.9863 | 33036.6667 | 33072 | 51400.2397 | 0 | 121.227 | 51400.2397 | 9619.9863 | 8708.2533 | 2138.7153 | 30933.2847
| snapshot) using your own manufacturers' tool. Punch in my input shown for | AT | 29 | 342 | 26.8234 | 23.22 | 76.28% | 0.00263 | 9.78 | 896.2018 | 49.8 | 98.7671 | 131.6894 | 19.9505 | 74.09% | 73.3647 | 72.9647 | 0.0060517 | 0.012103 | 24.1082 | 30.4564 | 0 | Heat-Hum | 23.2619 | 2.2734 | 0 | 0 | 42.1 | 1259.52 | 1854 | 78 | 73.3647 | 19.9505 | 42.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 29 | 73.1 | 26.8234 | 4" MERV 8 | 4" MERV 8 | 74.09% | 1 | 168.5455 | 114.4662 | 52.8132 | 34.3634 | 48.5289 | 34.3634 | 4.2843 | 0 | 29416.0952 | 19811.6183 | 2.9583 | 1.6146 | 21.3928 | 7.9295 | 29277.4198 | 8440.4502 | 1.3889 | 0.10214 | 12.7951 | 0.27128 | 32.8727 | 6.8583 | 5.6488 | 17.6215 | 1.195 | 1.0444 | 145.8 | 0 | 72.9 | 0 | 0 | 218.7 | 0 | 9.827 | 0 | 0 | 0 | 8605.29 | 1026 | 0 | 0 | 168.5455 | 114.75 | 52.7846 | 34.4447 | 48.4855 | 34.4447 | 4.2991 | 0 | 29345.9429 | 19813.3906 | 2.948 | 1.615 | 21.2674 | 7.932 | 29206.3583 | 8455.6155 | 1.383 | 0.10252 | 12.7099 | 0.27276 | 32.7 | 6.8583 | 5.6761 | 17.6544 | 1.194 | 1.0444 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8078 | 0 | 0 | 23455.5 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 42.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 29 | 75 | 26.8234 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8537 | 33.4365 | 14.1516 | 33.4365 | 19.7021 | 0 | 18049.0979 | 17546.3058 | 2.1904 | 2.102 | 9.7188 | 9.2359 | 18779.5653 | 12742.1866 | 0.81029 | 0.32052 | 4.7882 | 1.2851 | 23.6 | 8.8 | 5.0441 | 13.4336 | 1.2121 | 1.0787 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.146 | 0 | 0 | 7579.29 | 7579.29 | 1657.1388 | 8233.7814 | 26465.1 | 26465.1 | 42278.1714 | 0 | 123.6204 | 42278.1714 | 8233.7814 | 7579.29 | 1725.0959 | 24740.0041
| any line of input, you should get close to my output. | AU | 27 | 116 | 24.4672 | 19.74 | 70.89% | 0.0022257 | 8.86 | 844.1155 | 49.1 | 93.7488 | 124.9983 | 19.9496 | 74.08% | 72.8934 | 72.4934 | 0.0058452 | 0.01169 | 23.7775 | 29.9091 | 0 | Heat-Hum | 24.2187 | 2.4048 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72.8934 | 19.9496 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 27 | 73.1 | 24.4672 | 4" MERV 8 | 4" MERV 8 | 74.08% | 1 | 168.5455 | 114.4607 | 52.8144 | 34.3601 | 48.5302 | 34.3601 | 4.2842 | 0 | 29419.1987 | 19795.8666 | 2.9588 | 1.6129 | 21.3984 | 7.9217 | 29291.8728 | 8193.7097 | 1.3901 | 0.096411 | 12.8125 | 0.24857 | 32.8909 | 6.825 | 5.6456 | 17.7022 | 1.1952 | 1.0442 | 145.9 | 0 | 72.95 | 0 | 0 | 218.85 | 0 | 9.8303 | 0 | 0 | 0 | 3107.06 | 348 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.443 | 48.486 | 34.443 | 4.2992 | 0 | 29347.6707 | 19797.6735 | 2.9483 | 1.6133 | 21.2705 | 7.9243 | 29219.3903 | 8208.654 | 1.3841 | 0.096767 | 12.7255 | 0.24995 | 32.7091 | 6.825 | 5.6734 | 17.7361 | 1.1941 | 1.0442 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 7917 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 27 | 75 | 24.4672 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 11883.7429 | 0.81088 | 0.27871 | 4.7938 | 1.0422 | 23.6 | 8.5 | 5.0429 | 13.7645 | 1.2122 | 1.0768 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 2759.06 | 2759.06 | 581.3076 | 2903.7301 | 8903 | 8903 | 14565.7901 | 0 | 125.5672 | 14565.7901 | 2903.7301 | 2759.06 | 584.9755 | 8318.0245
|  | AV | 25 | 42 | 22.5357 | 17.51 | 69.9% | 0.0019971 | 8.13 | 1002.7905 | 48.5 | 112.1066 | 149.4754 | 19.9349 | 74.03% | 72.5071 | 72.1071 | 0.0058452 | 0.01169 | 23.684 | 29.8156 | 0 | Heat-Hum | 25.252 | 2.5567 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72.5071 | 19.9349 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 25 | 73.1 | 22.5357 | 4" MERV 8 | 4" MERV 8 | 74.03% | 1 | 168.5455 | 114.3763 | 52.823 | 34.3343 | 48.5432 | 34.3343 | 4.2798 | 0 | 29440.1162 | 19781.4991 | 2.9619 | 1.6113 | 21.4359 | 7.9137 | 29313.0815 | 7951.3537 | 1.3918 | 0.090939 | 12.8381 | 0.22753 | 32.9455 | 6.7917 | 5.6375 | 17.7658 | 1.1955 | 1.044 | 146 | 0 | 73 | 0 | 0 | 219 | 0 | 9.8361 | 0 | 0 | 0 | 1193.15 | 126 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4413 | 48.486 | 34.4413 | 4.2992 | 0 | 29347.6707 | 19783.8326 | 2.9483 | 1.6118 | 21.2705 | 7.9171 | 29219.3903 | 7970.0044 | 1.3841 | 0.091371 | 12.7255 | 0.22915 | 32.7091 | 6.8 | 5.6734 | 17.8101 | 1.1941 | 1.044 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 2856 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 25 | 75 | 22.5357 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 11132.5103 | 0.81088 | 0.24451 | 4.7938 | 0.85653 | 23.6 | 8.4 | 5.0429 | 14.0298 | 1.2122 | 1.0753 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 1067.15 | 1067.15 | 217.996 | 1094.7508 | 3205.3 | 3208.8 | 5370.7008 | 0 | 127.8738 | 5370.7008 | 1094.7508 | 1067.15 | 211.8015 | 2996.9985
5. | I did use generic performance data (excel formulas) for the ventilation units. | AW | 23 | 25 | 19.956 | 12.66 | 60.54% | 0.0015729 | 7.2 | 887.4 | 47.8 | 99.9655 | 133.2873 | 19.9369 | 74.04% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 26.5626 | 2.8385 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.9369 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 23 | 73.1 | 19.956 | 4" MERV 8 | 4" MERV 8 | 74.04% | 1 | 168.5455 | 114.3878 | 52.8218 | 34.3354 | 48.5414 | 34.3354 | 4.2804 | 0 | 29437.2635 | 19763.4005 | 2.9615 | 1.6094 | 21.4308 | 7.9044 | 29310.1903 | 7745.4334 | 1.3916 | 0.086411 | 12.8346 | 0.2106 | 32.9364 | 6.7667 | 5.6386 | 17.8414 | 1.1954 | 1.0438 | 146 | 0 | 73 | 0 | 0 | 219 | 0 | 9.8354 | 0 | 0 | 0 | 750.7917 | 75 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 7762.9585 | 1.3841 | 0.086806 | 12.7255 | 0.21204 | 32.7091 | 6.7667 | 5.6734 | 17.8848 | 1.1941 | 1.0438 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 1691.6667 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 23 | 75 | 19.956 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 10470.7476 | 0.81088 | 0.21621 | 4.7938 | 0.71235 | 23.6 | 8.3 | 5.0429 | 14.243 | 1.2122 | 1.0742 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 675.7917 | 675.7917 | 135.4384 | 684.4012 | 1899.1667 | 1899.1667 | 3259.3595 | 0 | 130.3744 | 3259.3595 | 684.4012 | 675.7917 | 126.0723 | 1773.0944
|  | AX | 21 | 23 | 18.4913 | 12.19 | 65.07% | 0.0015371 | 6.68 | 558.6 | 47.1 | 63.404 | 84.5386 | 19.9561 | 74.11% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 27.4068 | 2.8623 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.9561 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 21 | 73.1 | 18.4913 | 4" MERV 8 | 4" MERV 8 | 74.11% | 1 | 168.5455 | 114.4984 | 52.8106 | 34.3671 | 48.5244 | 34.3671 | 4.2862 | 0 | 29409.8475 | 19764.0912 | 2.9574 | 1.6096 | 21.3817 | 7.9054 | 29282.3964 | 7514.6288 | 1.3893 | 0.081468 | 12.8011 | 0.19264 | 32.8727 | 6.75 | 5.6492 | 17.897 | 1.195 | 1.0437 | 145.9 | 0 | 72.95 | 0 | 0 | 218.85 | 0 | 9.8278 | 0 | 0 | 0 | 728.065 | 69 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 7526.3495 | 1.3841 | 0.081724 | 12.7255 | 0.19354 | 32.7091 | 6.7583 | 5.6734 | 17.9274 | 1.1941 | 1.0437 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 1554.4167 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 21 | 75 | 18.4913 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 9892.8534 | 0.81088 | 0.19288 | 4.7938 | 0.60041 | 23.6 | 8.2 | 5.0429 | 14.4131 | 1.2122 | 1.0733 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 659.065 | 659.065 | 127.9689 | 649.0663 | 1741.1 | 1743.0167 | 3051.1479 | 0 | 132.6586 | 3051.1479 | 649.0663 | 659.065 | 115.9865 | 1627.0301
6. | The most difficult task was calculating accurate wet bulb values for TMY data. | AY | 19 | 10 | 16.38 | 8.98 | 61.02% | 0.0013086 | 5.95 | 1368.42 | 46.5 | 156.3258 | 208.4345 | 19.8805 | 73.83% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 28.592 | 3.0141 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8805 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 19 | 73.1 | 16.38 | 4" MERV 8 | 4" MERV 8 | 73.83% | 1 | 168.5455 | 114.0644 | 52.8713 | 34.2477 | 48.6037 | 34.2477 | 4.2676 | 0 | 29517.7526 | 19761.3807 | 2.9833 | 1.6134 | 21.6481 | 7.9233 | 29391.9751 | 7283.539 | 1.3984 | 0.076637 | 12.9332 | 0.17564 | 33.2 | 6.75 | 5.5986 | 17.8345 | 1.197 | 1.0437 | 146.3 | 0 | 73.15 | 0 | 0 | 219.45 | 0 | 9.8581 | 0 | 0 | 0 | 332.7833 | 30 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 7313.5784 | 1.3841 | 0.077275 | 12.7255 | 0.17783 | 32.7091 | 6.7417 | 5.6734 | 17.9638 | 1.1941 | 1.0436 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 674.1667 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 19 | 75 | 16.38 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 9379.1696 | 0.81088 | 0.17323 | 4.7938 | 0.51124 | 23.6 | 8.1 | 5.0429 | 14.5515 | 1.2122 | 1.0726 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 302.7833 | 302.7833 | 57.6929 | 294.0544 | 756 | 755.1667 | 1352.0044 | 0 | 135.2004 | 1352.0044 | 294.0544 | 302.7833 | 50.4289 | 704.7377
|  | AZ | 17 | 16 | 13.6313 | 1.78 | 46.49% | 0.00090429 | 5.04 | 1406.6875 | 45.8 | 161.9005 | 215.8674 | 19.8617 | 73.76% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 30.0694 | 3.2827 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8617 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 17 | 73.1 | 13.6313 | 4" MERV 8 | 4" MERV 8 | 73.76% | 1 | 168.5455 | 113.9564 | 52.8825 | 34.2168 | 48.6205 | 34.2168 | 4.262 | 0 | 29544.7276 | 19760.7064 | 2.9873 | 1.6133 | 21.6969 | 7.9223 | 29419.3234 | 7089.0959 | 1.4007 | 0.072688 | 12.9664 | 0.16214 | 33.2727 | 6.7417 | 5.5883 | 17.8516 | 1.1974 | 1.0436 | 146.4 | 0 | 73.2 | 0 | 0 | 219.6 | 0 | 9.8656 | 0 | 0 | 0 | 558.4267 | 48 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 7122.8049 | 1.3841 | 0.073384 | 12.7255 | 0.16447 | 32.7091 | 6.725 | 5.6734 | 17.9948 | 1.1941 | 1.0436 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 1076 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 17 | 75 | 13.6313 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 8921.1247 | 0.81088 | 0.15657 | 4.7938 | 0.43951 | 23.6 | 8 | 5.0429 | 14.6647 | 1.2122 | 1.0721 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 510.4267 | 510.4267 | 96.4059 | 494.1253 | 1206.6667 | 1204 | 2208.552 | 0 | 138.0345 | 2208.552 | 494.1253 | 510.4267 | 80.6863 | 1123.3137
7. | Because this is a model for an indirect evaporative cooling system, I decided | BA | 15 | 8 | 12.8625 | 5.83 | 63.19% | 0.0011143 | 4.79 | 1195.375 | 45.2 | 138.4562 | 184.6082 | 19.8659 | 73.77% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 30.4753 | 3.1432 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8659 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 15 | 73.1 | 12.8625 | 4" MERV 8 | 4" MERV 8 | 73.77% | 1 | 168.5455 | 113.9808 | 52.8799 | 34.2238 | 48.6167 | 34.2238 | 4.2632 | 0 | 29538.6209 | 19760.8589 | 2.9864 | 1.6133 | 21.6858 | 7.9225 | 29413.1268 | 6927.806 | 1.4002 | 0.06949 | 12.9589 | 0.15148 | 33.2545 | 6.7333 | 5.5906 | 17.8794 | 1.1973 | 1.0436 | 146.4 | 0 | 73.2 | 0 | 0 | 219.6 | 0 | 9.8639 | 0 | 0 | 0 | 292.2 | 24 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 6959.4128 | 1.3841 | 0.070127 | 12.7255 | 0.15357 | 32.7091 | 6.7167 | 5.6734 | 18.0202 | 1.1941 | 1.0435 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 537.3333 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 15 | 75 | 12.8625 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 8520.3536 | 0.81088 | 0.14266 | 4.7938 | 0.38248 | 23.6 | 8 | 5.0429 | 14.7561 | 1.2122 | 1.0716 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 268.2 | 268.2 | 48.7657 | 250.3097 | 602.6667 | 601.3333 | 1119.843 | 0 | 139.9804 | 1119.843 | 250.3097 | 268.2 | 40.3431 | 560.9902
| to "split" the 2°F bin hours into two groupings, to more closely represent the | BB | 13 | 14 | 10.8643 | 3.02 | 60.35% | 0.00096429 | 4.15 | 878.5143 | 44.5 | 102.5066 | 136.6755 | 19.8855 | 73.85% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 31.5143 | 3.2429 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8855 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 13 | 73.1 | 10.8643 | 4" MERV 8 | 4" MERV 8 | 73.85% | 1 | 168.5455 | 114.0929 | 52.8684 | 34.2559 | 48.5993 | 34.2559 | 4.2691 | 0 | 29510.6306 | 19761.559 | 2.9823 | 1.6135 | 21.6353 | 7.9236 | 29384.7566 | 6786.8595 | 1.3978 | 0.066749 | 12.9245 | 0.14255 | 33.1818 | 6.725 | 5.6013 | 17.9145 | 1.1969 | 1.0435 | 146.3 | 0 | 73.15 | 0 | 0 | 219.45 | 0 | 9.8562 | 0 | 0 | 0 | 534.0767 | 42 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 6812.9129 | 1.3841 | 0.067264 | 12.7255 | 0.1442 | 32.7091 | 6.7083 | 5.6734 | 18.0421 | 1.1941 | 1.0434 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 939.1667 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 13 | 75 | 10.8643 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 8158.9903 | 0.81088 | 0.13065 | 4.7938 | 0.33543 | 23.6 | 7.9 | 5.0429 | 14.8323 | 1.2122 | 1.0713 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 492.0767 | 492.0767 | 87.8614 | 452.5886 | 1052.1 | 1049.7667 | 1994.4319 | 0 | 142.4594 | 1994.4319 | 452.5886 | 492.0767 | 70.6005 | 979.1662
| two phases if an indirect evaporative unit's intended sequence of operation, | BC | 11 | 19 | 8.1211 | -5.46 | 42.65% | 0.00061714 | 3.29 | 1240.4842 | 43.8 | 145.8029 | 194.4038 | 19.8075 | 73.56% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 32.9105 | 3.4735 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8075 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 11 | 73.1 | 8.1211 | 4" MERV 8 | 4" MERV 8 | 73.56% | 1 | 168.5455 | 113.6454 | 52.9147 | 34.1277 | 48.669 | 34.1277 | 4.2456 | 0 | 29622.6831 | 19758.7647 | 2.9989 | 1.6129 | 21.8382 | 7.9194 | 29498.3353 | 6640.6589 | 1.4073 | 0.063954 | 13.0625 | 0.13364 | 33.4727 | 6.7083 | 5.5586 | 17.8774 | 1.1986 | 1.0434 | 146.7 | 0 | 73.35 | 0 | 0 | 220.05 | 0 | 9.8869 | 0 | 0 | 0 | 755.6617 | 57 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 6683.7081 | 1.3841 | 0.064783 | 12.7255 | 0.13625 | 32.7091 | 6.7083 | 5.6734 | 18.0607 | 1.1941 | 1.0434 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 1274.5833 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 11 | 75 | 8.1211 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 7834.0375 | 0.81088 | 0.12029 | 4.7938 | 0.29652 | 23.6 | 7.9 | 5.0429 | 14.8959 | 1.2122 | 1.0709 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 698.6617 | 698.6617 | 123.8386 | 640.7556 | 1424.6833 | 1424.6833 | 2764.1006 | 0 | 145.479 | 2764.1006 | 640.7556 | 698.6617 | 95.815 | 1328.8684
| according to this design. See this distinction represented graphically on each | BD | 9 | 25 | 5.576 | -15.93 | 26.54% | 0.00034714 | 2.53 | 1260.92 | 43.2 | 149.1292 | 198.8389 | 19.7593 | 73.38% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 34.1444 | 3.6529 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.7593 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 9 | 73.1 | 5.576 | 4" MERV 8 | 4" MERV 8 | 73.38% | 1 | 168.5455 | 113.3692 | 52.9435 | 34.0485 | 48.7124 | 34.0485 | 4.2311 | 0 | 29692.303 | 19757.0395 | 3.0092 | 1.6125 | 21.9649 | 7.9168 | 29568.8993 | 6520.7317 | 1.4132 | 0.061704 | 13.1488 | 0.12661 | 33.6455 | 6.7 | 5.5322 | 17.858 | 1.1996 | 1.0434 | 147 | 0 | 73.5 | 0 | 0 | 220.5 | 0 | 9.906 | 0 | 0 | 0 | 1034.875 | 75 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 6573.2568 | 1.3841 | 0.062697 | 12.7255 | 0.12968 | 32.7091 | 6.7 | 5.6734 | 18.0761 | 1.1941 | 1.0434 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 1675 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 9 | 75 | 5.576 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 7544.0841 | 0.81088 | 0.11139 | 4.7938 | 0.26441 | 23.6 | 7.9 | 5.0429 | 14.9488 | 1.2122 | 1.0707 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 959.875 | 959.875 | 168.2922 | 873.9461 | 1872.5 | 1872.5 | 3706.3211 | 0 | 148.2528 | 3706.3211 | 873.9461 | 959.875 | 126.0723 | 1746.4277
| IDEC units' submittal tab. | BE | 7 | 16 | 3.9125 | -16.83 | 27.91% | 0.00033 | 2.03 | 3.9125 | 42.5 | 0.46608 | 0.62144 | 19.999 | 74.27% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 34.9561 | 3.6643 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.999 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 7 | 73.1 | 3.9125 | 4" MERV 8 | 4" MERV 8 | 74.27% | 1 | 168.5455 | 114.7445 | 52.7858 | 34.4376 | 48.4869 | 34.4376 | 4.299 | 0 | 29349.0389 | 19765.6277 | 2.9485 | 1.6099 | 21.2729 | 7.9076 | 29220.7765 | 6482.0577 | 1.3842 | 0.060998 | 12.7271 | 0.12442 | 32.7182 | 6.6917 | 5.6728 | 18.0877 | 1.1941 | 1.0433 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8112 | 0 | 0 | 0 | 688.2933 | 48 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 6482.2655 | 1.3841 | 0.061002 | 12.7255 | 0.12443 | 32.7091 | 6.6917 | 5.6734 | 18.0884 | 1.1941 | 1.0433 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 1070.6667 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 7 | 75 | 3.9125 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 7287.0122 | 0.81088 | 0.10377 | 4.7938 | 0.23793 | 23.6 | 7.8 | 5.0429 | 14.9927 | 1.2122 | 1.0705 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 640.2933 | 640.2933 | 109.9582 | 572.3136 | 1195.4667 | 1195.4667 | 2408.0736 | 0 | 150.5046 | 2408.0736 | 572.3136 | 640.2933 | 80.6863 | 1114.7804
|  | BF | 5 | 4 | 1.575 | -31.11 | 13.44% | 0.00014286 | 1.35 | 684.25 | 41.9 | 82.0132 | 109.3509 | 19.7618 | 73.39% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 36.0601 | 3.7886 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.7618 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 5 | 73.1 | 1.575 | 4" MERV 8 | 4" MERV 8 | 73.39% | 1 | 168.5455 | 113.3831 | 52.9421 | 34.0525 | 48.7102 | 34.0525 | 4.2319 | 0 | 29688.782 | 19757.1266 | 3.0087 | 1.6125 | 21.9585 | 7.9169 | 29565.3308 | 6357.3668 | 1.4129 | 0.058702 | 13.1444 | 0.11743 | 33.6364 | 6.7 | 5.5335 | 17.8811 | 1.1996 | 1.0433 | 147 | 0 | 73.5 | 0 | 0 | 220.5 | 0 | 9.905 | 0 | 0 | 0 | 178.5667 | 12 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 6406.668 | 1.3841 | 0.059609 | 12.7255 | 0.12017 | 32.7091 | 6.6917 | 5.6734 | 18.0985 | 1.1941 | 1.0433 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 267.6667 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 5 | 75 | 1.575 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 7055.5259 | 0.81088 | 0.097125 | 4.7938 | 0.21563 | 23.6 | 7.8 | 5.0429 | 15.0299 | 1.2122 | 1.0703 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 166.5667 | 166.5667 | 28.255 | 147.4944 | 299.2 | 298.8667 | 612.9277 | 0 | 153.2319 | 612.9277 | 147.4944 | 166.5667 | 20.1716 | 278.6951
8. | There is a "dry" group of hours sorted by dry bulb containing hours below 65°F | BG | 3 | 0
| dry bulb outdoors. Below those a moist group containing the rest of the hours, | BH | 1 | 0
| during which the evaporative process takes place. | BI | -1 | 2 | -3.8 | -44.97 | 7.74% | 6e-05 | -0.18 | 772.8 | 39.9 | 94.515 | 126.0201 | 20 | 79.37% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 38.5441 | 3.8437 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -1 | 73.1 | -3.8 | 4" MERV 8 | 4" MERV 8 | 79.37% | 1 | 168.5455 | 122.6263 | 52.7853 | 36.9802 | 48.486 | 36.9802 | 4.2992 | 0 | 29347.6707 | 21122.3453 | 2.9483 | 1.758 | 21.2705 | 9.2277 | 29219.3903 | 6740.7525 | 1.3841 | 0.064919 | 12.7255 | 0.1377 | 32.7091 | 7.8083 | 5.6734 | 16.6585 | 1.1941 | 1.0505 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 99.0233 | 6 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 6283.5365 | 1.3841 | 0.057373 | 12.7255 | 0.11344 | 32.7091 | 6.6833 | 5.6734 | 18.1143 | 1.1941 | 1.0433 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 133.6667 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -1 | 75 | -3.8 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 6504.6875 | 0.81088 | 0.082155 | 4.7938 | 0.16815 | 23.6 | 7.8 | 5.0429 | 15.1097 | 1.2122 | 1.0699 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 93.0233 | 93.0233 | 14.9886 | 78.7151 | 171.7667 | 149.2667 | 321.0051 | 0 | 160.5026 | 321.0051 | 78.7151 | 93.0233 | 10.0858 | 139.1809
|  | BJ | -3 | 0
| Here is the sequence for repeating / reviewing my calculation. | BK | -5 | 1 | -6.7 | -25.11 | 32.42% | 0.00020429 | -0.98 | 0 | 38.6 | 0 | 0 | 20 | 74.27% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 39.8429 | 3.7478 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -5 | 73.1 | -6.7 | 4" MERV 8 | 4" MERV 8 | 74.27% | 1 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 6289.5495 | 1.3841 | 0.057482 | 12.7255 | 0.11376 | 32.7091 | 6.6833 | 5.6734 | 18.1135 | 1.1941 | 1.0433 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 52.7583 | 3 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 6289.5495 | 1.3841 | 0.057482 | 12.7255 | 0.11376 | 32.7091 | 6.6833 | 5.6734 | 18.1135 | 1.1941 | 1.0433 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 66.8333 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -5 | 75 | -6.7 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 6237.2575 | 0.81088 | 0.075313 | 4.7938 | 0.14781 | 23.6 | 7.8 | 5.0429 | 15.1441 | 1.2122 | 1.0698 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 49.7583 | 49.7583 | 7.7194 | 40.6564 | 74.6333 | 74.6333 | 165.048 | 0 | 165.048 | 165.048 | 40.6564 | 49.7583 | 5.0429 | 69.5904
|  | BL | -7 | 4 | -8.125 | -19.29 | 50.54% | 0.00028714 | -1.37 | 1014.3 | 37.9 | 126.5295 | 168.7061 | 20 | 75.25% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 40.4761 | 3.6928 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -7 | 73.1 | -8.125 | 4" MERV 8 | 4" MERV 8 | 75.25% | 1 | 168.5455 | 116.2563 | 52.7853 | 34.9226 | 48.486 | 34.9226 | 4.2992 | 0 | 29347.6707 | 20025.1229 | 2.9483 | 1.6375 | 21.2705 | 8.1489 | 29219.3903 | 6408.9691 | 1.3841 | 0.059478 | 12.7255 | 0.11995 | 32.7091 | 6.8917 | 5.6734 | 17.8179 | 1.1941 | 1.0446 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 217.5267 | 12 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 6321.3078 | 1.3841 | 0.058055 | 12.7255 | 0.11548 | 32.7091 | 6.6833 | 5.6734 | 18.1095 | 1.1941 | 1.0433 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 267.3333 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -7 | 75 | -8.125 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 6129.2845 | 0.81088 | 0.072629 | 4.7938 | 0.14008 | 23.6 | 7.8 | 5.0429 | 15.1573 | 1.2122 | 1.0697 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 205.5267 | 205.5267 | 31.3166 | 165.1582 | 306.8667 | 298.5333 | 669.2182 | 0 | 167.3045 | 669.2182 | 165.1582 | 205.5267 | 20.1716 | 278.3618
9. | Maintain coordination with electrical design. Keep input values in rows 44-46 | BM | -9 | 2 | -10.95 | -54.68 | 6.27% | 3.1429e-05 | -2.12 | 563.5 | 37.2 | 70.7761 | 94.3682 | 20 | 74.7% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | 0 | Heat-Hum | 41.6937 | 3.8627 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -9 | 73.1 | -10.95 | 4" MERV 8 | 4" MERV 8 | 74.7% | 1 | 168.5455 | 115.4053 | 52.7853 | 34.6494 | 48.486 | 34.6494 | 4.2992 | 0 | 29347.6707 | 19878.5436 | 2.9483 | 1.6219 | 21.2705 | 8.012 | 29219.3903 | 6410.037 | 1.3841 | 0.059595 | 12.7255 | 0.1202 | 32.7091 | 6.775 | 5.6734 | 17.9754 | 1.1941 | 1.0439 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 0 | 112.01 | 6 | 0 | 0 | 168.5455 | 114.75 | 52.7853 | 34.4392 | 48.486 | 34.4392 | 4.2992 | 0 | 29347.6707 | 19765.6623 | 2.9483 | 1.6099 | 21.2705 | 7.9077 | 29219.3903 | 6371.6086 | 1.3841 | 0.058968 | 12.7255 | 0.11823 | 32.7091 | 6.6917 | 5.6734 | 18.103 | 1.1941 | 1.0433 | 145.6 | 0 | 72.8 | 0 | 0 | 218.4 | 0 | 9.8109 | 0 | 0 | 133.8333 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -9 | 75 | -10.95 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.854 | 33.4367 | 14.1518 | 33.4367 | 19.7022 | 0 | 18050.1605 | 17547.3389 | 2.1906 | 2.1021 | 9.7201 | 9.2371 | 18787.7997 | 6034.745 | 0.81088 | 0.070315 | 4.7938 | 0.13352 | 23.6 | 7.8 | 5.0429 | 15.1684 | 1.2122 | 1.0697 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 106.01 | 106.01 | 16.0804 | 85.0143 | 151.1 | 149.4333 | 340.4577 | 0 | 170.2288 | 340.4577 | 85.0143 | 106.01 | 10.0858 | 139.3475
| of the Summary tab that are consistant with the electrical design. | BN | -11 | 0
|  |  | total | 6365 | hours
10. | Manual psychrometric solutions appear to the left here, in column 15 (or
| column "O" if you prefer). There are 98 such manual selections in this bin tab; | [195 empty] | NO | selected | Resulting | Resulting | Ventilation | Gen | UPS | ITE
| common psychrometric results may be copied to other scenario tabs | 2°F wet bulb bins (for hours above 65°F dry bulb) | [7 empty] | Annual HW demand of cafeteria: |  |  |  | recovery | zone | temp | [6 empty] | Properties for generic ventilation air handlers. | [17 empty] | Information used for hourly inputs for ITE room IDEC units (shown with heat recovery input) | [27 empty] | Outputs for ITE room IDEC units with heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | HR export |  | Generator room | [19 empty] | Outputs for ITE room IDEC units without heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | Without HR | UPS room variables | [13 empty] | Information used for hourly inputs for UPS room IDEC units | [27 empty] | Outputs for UPS units. NOTE: most of the performance values are PER UNIT | [18 empty] | Generator Room |  | Ventilation system |  | ITE and UPS cooling |  | Recovery | recovery | Mechanical | Mechanical | system | room | room | room
|  | bin | Average | bin | Outdoor |  |  |  | Psychrometric values for averaged points: | café avg | entering | kwh from | H2O heater | delta T | % desigm | Temp | AHU | Min | Max | min. | max. |  | control | heat | liquid | Cooling | DX split | room air | Project | Design | Design | Reset | Resulting | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | energy avoided | Room heat | engine block | Recovery | Recovery | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | error | ITE cooling | UPS room | Battery | Project | Design | Design | Design | Alternate | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | with | without | with | without | with | without | whatsoever | savings | Input | energy | HVAC | HVAC | cooling | cooling
11. | Review equipment selections, ensure they are consistent with your design | name | dry bulb | hours | wet bulb | dewpoint | %rh | moisture | enthalpy | 140 | temp | hot aisle | input energy | w/ HR | w/ HR | into ITE | SAT: | moisture | moisture | enthalpy | enthalpy |  | mode | power | added | needed | kW input: | dew point | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | elsewhere | need, kWh | heat, kWh | Potential | Savings | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | annual kWh | temp | temp | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | recovery | recovery | recovery | recovery | recovery | recovery | at all | kWh: | Power | incl. Recov | Component | component | component | component
| especially during the extreme climate data. Fill out the remaining user input | CA | 66 | 4 | 46 | 25 | 20.24% | 0.0028629 | 18.95 | 1706.6 | 55.4 | 176.4013 | 235.2018 | 19.9612 | 74.13% | 77.2 | 76.8 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Heat-Hum | 11.7191 | 2.7128 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.2 | 19.9612 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 66 | 73.1 | 46 | 4" MERV 8 | 4" MERV 8 | 74.13% | 1 | 168.5455 | 114.5273 | 52.8043 | 34.3963 | 48.5174 | 34.3963 | 4.2868 | 0 | 29394.2844 | 19944.8721 | 2.9551 | 1.6288 | 21.3538 | 7.9976 | 29211.6852 | 4398.4447 | 1.3834 | 0.039667 | 12.7163 | 0.0549 | 32.7727 | 8.125 | 5.6653 | 14.8798 | 1.1944 | 1.0526 | 145.6 | 38.8 | 72.8 | 19.4 | 0 | 218.4 | 58.2 | 9.8112 | 4.2818 | 0 | 0 | 0 | 10.8 | 0 | 0 | 168.5455 | 114.75 | 52.7818 | 34.4602 | 48.4834 | 34.4602 | 4.2984 | 0 | 29339.2726 | 19946.2626 | 2.947 | 1.6291 | 21.2555 | 7.9997 | 29156.0382 | 4408.6932 | 1.3788 | 0.03984 | 12.6498 | 0.055268 | 32.6364 | 8.125 | 5.6868 | 14.9085 | 1.1936 | 1.0526 | 145.4 | 38.9 | 72.7 | 19.45 | 0 | 218.1 | 58.35 | 9.7961 | 4.29 | 0 | 162.5 | 77.6 | 56.6 | 1259.52 | 111.24 | 65 | 56.6 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 66 | 75 | 46 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8525 | 33.4439 | 14.1507 | 33.4439 | 19.7018 | 0 | 18044.9953 | 17594.7149 | 2.1898 | 2.1099 | 9.7138 | 9.2687 | 18747.7842 | 16327.9718 | 0.80802 | 0.61902 | 4.7667 | 3.1804 | 23.6 | 11.4 | 5.049 | 10.3548 | 1.2119 | 1.1021 | 79.7 | 60.3 | 39.85 | 30.15 | 0 | 119.55 | 90.45 | 8.1341 | 9.239 | 0 | 10.8 | 10.8 | 11.3789 | 50.1303 | 370.6 | 370.6 | 431.5303 | 0 | 107.8826 | 431.5303 | 50.1303 | 10.8 | 20.1958 | 350.4042
| (yellow cells in boxes), including how much cooling equipment to install, | CB | 67.7765 | 34 | 48 | 29.1 | 23.04% | 0.0034686 | 20.04 | 1611.8235 | 56 | 165.4232 | 220.5643 | 19.9646 | 74.14% | 77.6 | 77.2 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Heat-Hum | 9.9495 | 2.3104 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.6 | 19.9646 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 67.7765 | 73.1 | 48 | 4" MERV 8 | 4" MERV 8 | 74.14% | 1 | 168.5455 | 114.5466 | 52.8023 | 34.4036 | 48.5145 | 34.4036 | 4.2878 | 0 | 29389.5001 | 19959.3202 | 2.9544 | 1.6304 | 21.3452 | 8.0053 | 29206.8533 | 4520.041 | 1.383 | 0.041765 | 12.7105 | 0.059402 | 32.7636 | 8.1417 | 5.6672 | 14.8556 | 1.1944 | 1.0527 | 145.6 | 39.3 | 72.8 | 19.65 | 0 | 218.4 | 58.95 | 9.8099 | 4.3326 | 0 | 0 | 0 | 88.78 | 0 | 0 | 168.5455 | 114.75 | 52.7818 | 34.4619 | 48.4834 | 34.4619 | 4.2984 | 0 | 29339.2726 | 19960.59 | 2.947 | 1.6306 | 21.2555 | 8.0072 | 29156.0382 | 4529.805 | 1.3788 | 0.041933 | 12.6498 | 0.05977 | 32.6364 | 8.1417 | 5.6868 | 14.8817 | 1.1936 | 1.0527 | 145.4 | 39.4 | 72.7 | 19.7 | 0 | 218.1 | 59.1 | 9.7961 | 4.3402 | 0 | 2768.1667 | 81.8 | 60.8 | 1259.52 | 111.24 | 65 | 60.8 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 67.7765 | 75 | 48 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8525 | 33.4666 | 14.1507 | 33.4666 | 19.7018 | 0 | 18044.9953 | 17732.2581 | 2.1898 | 2.1325 | 9.7138 | 9.368 | 18747.7842 | 12745.7215 | 0.80802 | 0.38247 | 4.7667 | 1.5339 | 23.6 | 10.1 | 5.049 | 11.6891 | 1.2119 | 1.0905 | 79.7 | 53.1 | 39.85 | 26.55 | 0 | 119.55 | 79.65 | 8.1341 | 8.1242 | 0 | 88.78 | 88.78 | 86.2919 | 365.9405 | 3111.5667 | 3111.5667 | 3566.2871 | 1.5632e-13 | 104.8908 | 3566.2871 | 365.9405 | 88.78 | 171.6644 | 2939.9022
| when. Review accuracy of generator room heating load, HW export schedule | CC | 67.3902 | 102 | 50 | 35.69 | 30.93% | 0.0046029 | 21.18 | 1429.3569 | 56.7 | 145.474 | 193.9654 | 19.9686 | 74.16% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Heat-Hum | 8.0987 | 1.5568 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9686 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 67.3902 | 73.1 | 50 | 4" MERV 8 | 4" MERV 8 | 74.16% | 1 | 168.5455 | 114.5701 | 52.7999 | 34.412 | 48.5109 | 34.412 | 4.289 | 0 | 29383.687 | 19973.7943 | 2.9536 | 1.6319 | 21.3348 | 8.013 | 29200.9731 | 4681.9874 | 1.3825 | 0.044374 | 12.7035 | 0.065373 | 32.7455 | 8.1583 | 5.6695 | 14.8296 | 1.1943 | 1.0528 | 145.6 | 38.7 | 72.8 | 19.35 | 0 | 218.4 | 58.05 | 9.8083 | 4.2679 | 0 | 0 | 0 | 268.31 | 0 | 0 | 168.5455 | 114.75 | 52.7818 | 34.4636 | 48.4834 | 34.4636 | 4.2984 | 0 | 29339.2726 | 19974.9174 | 2.947 | 1.6322 | 21.2555 | 8.0147 | 29156.0382 | 4690.997 | 1.3788 | 0.044533 | 12.6498 | 0.065735 | 32.6364 | 8.1583 | 5.6868 | 14.8526 | 1.1936 | 1.0528 | 145.4 | 38.8 | 72.7 | 19.4 | 0 | 218.1 | 58.2 | 9.7961 | 4.2745 | 0 | 8321.5 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 67.3902 | 75 | 50 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8525 | 33.4893 | 14.1507 | 33.4893 | 19.7018 | 0 | 18044.9953 | 17869.8012 | 2.1898 | 2.1552 | 9.7138 | 9.4679 | 18747.7842 | 10159.3329 | 0.80802 | 0.2453 | 4.7667 | 0.78418 | 23.6 | 9.6 | 5.049 | 12.3179 | 1.2119 | 1.0859 | 79.7 | 45.7 | 39.85 | 22.85 | 0 | 119.55 | 68.55 | 8.1341 | 6.9973 | 0 | 268.31 | 268.31 | 226.1542 | 909.0395 | 9300.7 | 9300.7 | 10478.0495 | 0 | 102.726 | 10478.0495 | 909.0395 | 268.31 | 514.9933 | 8785.7067
| if those heat recovery options are to be considered in your design. | CD | 69.132 | 222 | 52 | 41.82 | 37.04% | 0.0058643 | 22.98 | 1257.1892 | 57.4 | 126.8763 | 169.1684 | 19.9733 | 74.17% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Heat-Hum | 5.1764 | 0.7187 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9733 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 69.132 | 73.1 | 52 | 4" MERV 8 | 4" MERV 8 | 74.17% | 1 | 168.5455 | 114.5971 | 52.7972 | 34.4198 | 48.5068 | 34.4198 | 4.2904 | 0 | 29377.0241 | 19973.9626 | 2.9526 | 1.632 | 21.3229 | 8.0133 | 29194.2255 | 4946.9844 | 1.382 | 0.049126 | 12.6954 | 0.076472 | 32.7273 | 8.1667 | 5.6721 | 14.8156 | 1.1942 | 1.0529 | 145.5 | 39.3 | 72.75 | 19.65 | 0 | 218.25 | 58.95 | 9.8064 | 4.3304 | 0 | 0 | 0 | 564.635 | 0 | 0 | 168.5455 | 114.75 | 52.7818 | 34.4636 | 48.4834 | 34.4636 | 4.2984 | 0 | 29339.2726 | 19974.9174 | 2.947 | 1.6322 | 21.2555 | 8.0147 | 29156.0382 | 4955.2035 | 1.3788 | 0.049279 | 12.6498 | 0.076837 | 32.6364 | 8.1667 | 5.6868 | 14.8351 | 1.1936 | 1.0529 | 145.4 | 39.3 | 72.7 | 19.65 | 0 | 218.1 | 58.95 | 9.7961 | 4.3362 | 0 | 18130 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 69.132 | 75 | 52 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8525 | 33.4893 | 14.1507 | 33.4893 | 19.7018 | 0 | 18044.9953 | 17869.8012 | 2.1898 | 2.1552 | 9.7138 | 9.4679 | 18747.7842 | 11727.2673 | 0.80802 | 0.32388 | 4.7667 | 1.1952 | 23.6 | 9.9 | 5.049 | 11.8738 | 1.2119 | 1.0891 | 79.7 | 48.4 | 39.85 | 24.2 | 0 | 119.55 | 72.6 | 8.1341 | 7.4131 | 0 | 564.635 | 564.635 | 379.7694 | 1329.7426 | 20327.8 | 20327.8 | 22222.1776 | -1.0232e-12 | 100.0999 | 22222.1776 | 1329.7426 | 564.635 | 1120.8678 | 19206.9322
|  | CE | 71.0419 | 332 | 54 | 47.12 | 42.47% | 0.0071914 | 24.89 | 1264.8614 | 58 | 126.7233 | 168.9644 | 19.9741 | 74.18% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Heat-Hum | 2.0755 | 0 | 0 | 0 | 46.9 | 1259.52 | 1854 | 78 | 78 | 19.9741 | 46.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 71.0419 | 73.1 | 54 | 4" MERV 8 | 4" MERV 8 | 74.18% | 1 | 168.5455 | 114.6014 | 52.7961 | 34.4208 | 48.5056 | 34.4208 | 4.2905 | 0 | 29374.2945 | 19972.8545 | 2.9522 | 1.6319 | 21.318 | 8.0123 | 29180.5637 | 5267.3098 | 1.3809 | 0.055161 | 12.6791 | 0.091426 | 32.7091 | 8.1833 | 5.6751 | 14.7942 | 1.1941 | 1.0529 | 145.5 | 40 | 72.75 | 20 | 0 | 218.25 | 60 | 9.8032 | 4.4104 | 0 | 0 | 0 | 812.705 | 0 | 0 | 168.5455 | 114.75 | 52.7812 | 34.4633 | 48.4829 | 34.4633 | 4.2982 | 0 | 29337.6056 | 19973.7825 | 2.9468 | 1.6321 | 21.2525 | 8.0137 | 29143.4746 | 5275.9361 | 1.3778 | 0.05533 | 12.6348 | 0.091857 | 32.6182 | 8.1833 | 5.6895 | 14.813 | 1.1935 | 1.0529 | 145.3 | 40.1 | 72.65 | 20.05 | 0 | 217.95 | 60.15 | 9.7933 | 4.4161 | 0 | 27168.6667 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 71.0419 | 75 | 54 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8523 | 33.4891 | 14.1505 | 33.4891 | 19.7018 | 0 | 18043.9701 | 17868.7859 | 2.1896 | 2.1551 | 9.7125 | 9.4667 | 18739.8446 | 13860.8168 | 0.80745 | 0.44806 | 4.7613 | 1.9542 | 23.6 | 10.6 | 5.0502 | 11.1335 | 1.2119 | 1.0951 | 79.6 | 52.3 | 39.8 | 26.15 | 0 | 119.4 | 78.45 | 8.1312 | 8.0041 | 0 | 812.705 | 812.705 | 389.5004 | 959.1229 | 30687.8667 | 30687.8667 | 32459.6946 | 0 | 97.7702 | 32459.6946 | 959.1229 | 812.705 | 1676.6519 | 29011.2148
12. | Commence itterations, using manufacturer's tool. I automated | CF | 73.161 | 351 | 56 | 49.75 | 43.62% | 0.0079457 | 26.23 | 1243.2632 | 58.7 | 123.4961 | 164.6615 | 19.9755 | 74.18% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Vent-only | 0 | 0 | 0 | 0 | 48.9 | 1259.52 | 1854 | 78 | 78 | 19.9755 | 48.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 73.161 | 73.1 | 56 | 4" MERV 8 | 4" MERV 8 | 74.18% | 1 | 168.5455 | 114.6093 | 52.7937 | 34.4225 | 48.5032 | 34.4225 | 4.2905 | 0 | 29368.4305 | 19970.2581 | 2.9513 | 1.6316 | 21.3075 | 8.01 | 29149.2144 | 5660.8754 | 1.3783 | 0.063014 | 12.6417 | 0.11225 | 32.6636 | 8.2 | 5.6821 | 14.7663 | 1.1938 | 1.0531 | 145.4 | 41 | 72.7 | 20.5 | 0 | 218.1 | 61.5 | 9.7959 | 4.5165 | 0 | 0 | 0 | 822.025 | 0 | 0 | 168.5455 | 114.75 | 52.7796 | 34.4628 | 48.4818 | 34.4628 | 4.2978 | 0 | 29333.7186 | 19971.1361 | 2.9462 | 1.6318 | 21.2456 | 8.0113 | 29114.1565 | 5669.7649 | 1.3754 | 0.0632 | 12.5999 | 0.11275 | 32.5818 | 8.2 | 5.6957 | 14.7839 | 1.1933 | 1.053 | 145.2 | 41 | 72.6 | 20.5 | 0 | 217.8 | 61.5 | 9.7865 | 4.5221 | 0 | 28782 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 48.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 73.161 | 75 | 56 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8516 | 33.4884 | 14.15 | 33.4884 | 19.7016 | 0 | 18041.5794 | 17866.4184 | 2.1892 | 2.1547 | 9.7096 | 9.4638 | 18721.3225 | 16865.9889 | 0.80613 | 0.65679 | 4.7489 | 3.4857 | 23.6 | 11.9 | 5.053 | 9.8898 | 1.2117 | 1.107 | 79.6 | 58 | 39.8 | 29 | 0 | 119.4 | 87 | 8.1242 | 8.8797 | 0 | 822.025 | 822.025 | 285.5221 | 285.5221 | 32958.9 | 32958.9 | 34066.4471 | 9.0949e-13 | 97.0554 | 34066.4471 | 285.5221 | 822.025 | 1773.5888 | 31185.3112
| that process to make this example happen. This calculation | CG | 74.8974 | 418 | 58 | 52.59 | 45.72% | 0.00884 | 27.64 | 1305.3483 | 59.3 | 128.7063 | 171.6084 | 19.975 | 74.18% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Vent-only | 0 | 0 | 0 | 0 | 53.1 | 1259.52 | 1854 | 78 | 78 | 19.975 | 53.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 74.8974 | 73.1 | 58 | 4" MERV 8 | 4" MERV 8 | 74.18% | 1 | 168.5455 | 114.6068 | 52.7903 | 34.4205 | 48.5008 | 34.4205 | 4.2895 | 0 | 29360.0069 | 19964.0884 | 2.9501 | 1.631 | 21.2925 | 8.0044 | 29081.5914 | 6152.3221 | 1.3727 | 0.073395 | 12.5612 | 0.14209 | 32.5818 | 8.2167 | 5.6963 | 14.728 | 1.1933 | 1.0532 | 145.2 | 41.8 | 72.6 | 20.9 | 0 | 217.8 | 62.7 | 9.7803 | 4.6123 | 0 | 0 | 0 | 942.645 | 0 | 0 | 168.5455 | 114.75 | 52.7759 | 34.4615 | 48.479 | 34.4615 | 4.2969 | 0 | 29324.6793 | 19964.9819 | 2.9449 | 1.6311 | 21.2295 | 8.0057 | 29045.9682 | 6162.2384 | 1.3697 | 0.073618 | 12.519 | 0.14275 | 32.5 | 8.2167 | 5.7102 | 14.7456 | 1.1928 | 1.0532 | 145 | 41.9 | 72.5 | 20.95 | 0 | 217.5 | 62.85 | 9.7707 | 4.6182 | 0 | 34345.6667 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 53.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 74.8974 | 75 | 58 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.85 | 33.4874 | 14.1488 | 31.865 | 19.7012 | 1.6224 | 18036.0198 | 17860.9128 | 2.1884 | 2.1543 | 9.7027 | 9.4592 | 18678.2567 | 17407.7104 | 0.80307 | 0.69647 | 4.7199 | 3.8149 | 23.5 | 13 | 5.0595 | 9.0294 | 1.2115 | 1.1172 | 79.4 | 57.3 | 39.7 | 28.65 | 0 | 119.1 | 85.95 | 8.1082 | 8.7681 | 0 | 942.645 | 942.645 | 340.0235 | 340.0235 | 39779.6667 | 39779.6667 | 41062.3352 | -2.5011e-12 | 98.2353 | 41062.3352 | 340.0235 | 942.645 | 2114.8601 | 37664.8066
| does not reflect any actual data center. I completed this for | CH | 78.9962 | 338 | 60 | 53.8 | 41.73% | 0.0092486 | 29.09 | 1370.0568 | 60 | 133.9147 | 178.553 | 19.9754 | 74.18% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Vent-only | 0 | 0 | 0 | 0 | 53.1 | 1259.52 | 1854 | 78 | 78 | 19.9754 | 53.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 78.9962 | 73.1 | 60 | 4" MERV 8 | 4" MERV 8 | 74.18% | 1 | 168.5455 | 114.6087 | 52.7901 | 34.4211 | 48.5005 | 34.4211 | 4.2896 | 0 | 29359.5287 | 19964.1005 | 2.95 | 1.631 | 21.2916 | 8.0044 | 29081.1102 | 6782.6591 | 1.3726 | 0.088195 | 12.5607 | 0.18823 | 32.5818 | 8.2583 | 5.6965 | 14.6566 | 1.1933 | 1.0534 | 145.2 | 44.6 | 72.6 | 22.3 | 0 | 217.8 | 66.9 | 9.7802 | 4.9222 | 0 | 0 | 0 | 692.965 | 0 | 0 | 168.5455 | 114.75 | 52.7759 | 34.4615 | 48.479 | 34.4615 | 4.2969 | 0 | 29324.6793 | 19964.9819 | 2.9449 | 1.6311 | 21.2295 | 8.0057 | 29045.9682 | 6793.612 | 1.3697 | 0.088464 | 12.519 | 0.18911 | 32.5 | 8.2583 | 5.7102 | 14.6735 | 1.1928 | 1.0534 | 145 | 44.7 | 72.5 | 22.35 | 0 | 217.5 | 67.05 | 9.7707 | 4.9286 | 0 | 27913.1667 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 53.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 78.9962 | 75 | 60 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.85 | 33.4879 | 14.1488 | 29.885 | 19.7012 | 3.6028 | 18036.0198 | 17860.9128 | 2.1884 | 2.1549 | 9.7027 | 9.4615 | 18678.2567 | 17523.4014 | 0.80307 | 0.70632 | 4.7199 | 3.8946 | 23.5 | 14.2 | 5.0595 | 8.3206 | 1.2115 | 1.1272 | 79.4 | 60.1 | 39.7 | 30.05 | 0 | 119.1 | 90.15 | 8.1082 | 9.1959 | 0 | 692.965 | 692.965 | 274.9472 | 274.9472 | 32712.7667 | 32712.7667 | 33680.6789 | 2.3874e-12 | 99.647 | 33680.6789 | 274.9472 | 692.965 | 1710.1022 | 31002.6645
| example purposes only. | CI | 83.3602 | 241 | 62 | 54.97 | 37.78% | 0.0096571 | 30.62 | 1503.9627 | 60.7 | 145.7169 | 194.2892 | 19.9746 | 74.18% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Vent-only | 0 | 0 | 0 | 0 | 55 | 1259.52 | 1854 | 78 | 78 | 19.9746 | 55 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 83.3602 | 73.1 | 62 | 4" MERV 8 | 4" MERV 8 | 74.18% | 1 | 168.5455 | 114.6043 | 52.7887 | 34.4192 | 48.4998 | 34.4192 | 4.2889 | 0 | 29356.1013 | 19961.0029 | 2.9495 | 1.6306 | 21.2855 | 8.0016 | 29048.1497 | 7616.1324 | 1.3699 | 0.10969 | 12.5216 | 0.26287 | 32.5455 | 8.3167 | 5.7033 | 14.5459 | 1.1931 | 1.0538 | 145 | 48.4 | 72.5 | 24.2 | 0 | 217.5 | 72.6 | 9.7726 | 5.3347 | 0 | 0 | 0 | 441.51 | 0 | 0 | 168.5455 | 114.75 | 52.7741 | 34.4609 | 48.4776 | 34.4609 | 4.2965 | 0 | 29320.1699 | 19961.9118 | 2.9442 | 1.6308 | 21.2214 | 8.0029 | 29011.9565 | 7628.9789 | 1.3669 | 0.11004 | 12.4788 | 0.26416 | 32.4545 | 8.3167 | 5.7174 | 14.5626 | 1.1926 | 1.0539 | 144.9 | 48.5 | 72.45 | 24.25 | 0 | 217.35 | 72.75 | 9.7628 | 5.342 | 0 | 20043.1667 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 55 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 83.3602 | 75 | 62 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8493 | 33.4877 | 14.1482 | 27.8564 | 19.701 | 5.6312 | 18033.2463 | 17858.1662 | 2.1879 | 2.155 | 9.6993 | 9.4605 | 18656.771 | 17621.7768 | 0.80154 | 0.71547 | 4.7055 | 3.9673 | 23.5 | 15.3 | 5.0627 | 7.7067 | 1.2113 | 1.1373 | 79.3 | 63.2 | 39.65 | 31.6 | 0 | 118.95 | 94.8 | 8.1001 | 9.6801 | 0 | 441.51 | 441.51 | 196.0423 | 196.0423 | 23730.4667 | 23730.4667 | 24368.0189 | -1.5348e-12 | 101.1121 | 24368.0189 | 196.0423 | 441.51 | 1220.1159 | 22510.3508
|  | CJ | 87.0126 | 190 | 64 | 56.69 | 35.78% | 0.010289 | 32.19 | 1528.9242 | 61.3 | 147.0146 | 196.0195 | 19.9755 | 74.18% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Vent-only | 0 | 0 | 0 | 0 | 55.9 | 1259.52 | 1854 | 78 | 78 | 19.9755 | 55.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 87.0126 | 73.1 | 64 | 4" MERV 8 | 4" MERV 8 | 74.18% | 1 | 168.5455 | 114.6092 | 52.7873 | 34.4202 | 48.4984 | 34.4202 | 4.2889 | 0 | 29352.662 | 19959.5129 | 2.949 | 1.6305 | 21.2794 | 8.0003 | 29030.0624 | 8772.7355 | 1.3684 | 0.14276 | 12.5002 | 0.39407 | 32.5182 | 8.4333 | 5.7074 | 14.3517 | 1.1929 | 1.0546 | 145 | 52.6 | 72.5 | 26.3 | 0 | 217.5 | 78.9 | 9.7683 | 5.8046 | 0 | 0 | 0 | 313.38 | 0 | 0 | 168.5455 | 114.75 | 52.7732 | 34.4606 | 48.4769 | 34.4606 | 4.2962 | 0 | 29317.9365 | 19960.3912 | 2.9439 | 1.6307 | 21.2174 | 8.0015 | 28995.1191 | 8787.0601 | 1.3656 | 0.1432 | 12.4589 | 0.39595 | 32.4364 | 8.4333 | 5.721 | 14.3667 | 1.1924 | 1.0546 | 144.8 | 52.7 | 72.4 | 26.35 | 0 | 217.2 | 79.05 | 9.759 | 5.8124 | 0 | 16023.3333 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 55.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 87.0126 | 75 | 64 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8489 | 33.4878 | 14.1479 | 25.8181 | 19.7009 | 7.6697 | 18031.8726 | 17856.8059 | 2.1877 | 2.1553 | 9.6977 | 9.4613 | 18646.1277 | 17733.41 | 0.80078 | 0.72431 | 4.6984 | 4.0417 | 23.5 | 16.4 | 5.0643 | 7.1736 | 1.2113 | 1.1475 | 79.3 | 64.9 | 39.65 | 32.45 | 0 | 118.95 | 97.35 | 8.0961 | 9.9419 | 0 | 313.38 | 313.38 | 154.5561 | 154.5561 | 19139.3333 | 19139.3333 | 19607.2695 | 1.08e-12 | 103.1962 | 19607.2695 | 154.5561 | 313.38 | 962.2226 | 18177.1107
|  | CK | 91.5062 | 97 | 68 | 57.99 | 32.54% | 0.010791 | 33.84 | 1557.4639 | 62.6 | 147.2851 | 196.3801 | 19.9766 | 74.19% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Dehum | 0 | 0 | 0.17788 | 0.14231 | 57.9 | 1259.52 | 1854 | 78 | 78 | 19.9766 | 57.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 91.5062 | 73.1 | 68 | 4" MERV 8 | 4" MERV 8 | 74.19% | 1 | 168.5455 | 114.6159 | 52.7845 | 34.4214 | 48.4958 | 34.4214 | 4.2887 | 0 | 29345.8128 | 19956.0164 | 2.948 | 1.6301 | 21.2672 | 7.9971 | 28989.1708 | 12716.719 | 1.3651 | 0.28414 | 12.4519 | 1.137 | 32.4636 | 9.075 | 5.7163 | 13.3348 | 1.1926 | 1.0587 | 144.8 | 62.9 | 72.4 | 31.45 | 0 | 217.2 | 94.35 | 9.7589 | 6.9333 | 0 | 0 | 0 | 138.195 | 0 | 0 | 168.5455 | 114.75 | 52.7711 | 34.4599 | 48.4753 | 34.4599 | 4.2957 | 0 | 29312.7395 | 19956.853 | 2.9431 | 1.6303 | 21.2082 | 7.9983 | 28955.9208 | 12735.3722 | 1.3623 | 0.28496 | 12.4127 | 1.142 | 32.3818 | 9.0833 | 5.7293 | 13.3441 | 1.1921 | 1.0588 | 144.7 | 63 | 72.35 | 31.5 | 0 | 217.05 | 94.5 | 9.7499 | 6.9422 | 0 | 8810.8333 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 57.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 91.5062 | 75 | 68 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.848 | 33.488 | 14.1473 | 21.7421 | 19.7007 | 11.7459 | 18028.6763 | 17853.6406 | 2.1872 | 2.1559 | 9.6937 | 9.4622 | 18621.3689 | 17962.4377 | 0.79903 | 0.73763 | 4.6819 | 4.1692 | 23.5 | 18.7 | 5.0681 | 6.3083 | 1.2111 | 1.1678 | 79.2 | 62.6 | 39.6 | 31.3 | 0 | 118.8 | 93.9 | 8.0869 | 9.5913 | 0 | 138.195 | 138.195 | 92.7086 | 92.7086 | 10616.65 | 10624.7333 | 10855.637 | -5.1159e-13 | 111.9138 | 10855.637 | 92.7086 | 138.195 | 491.6027 | 10133.1306
|  | CL | 95.7912 | 34 | 70 | 59.52 | 30.12% | 0.011411 | 35.58 | 1610.8765 | 63.3 | 150.9584 | 201.2779 | 19.9771 | 74.19% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Dehum | 0 | 0 | 0.98133 | 0.78507 | 59 | 1259.52 | 1854 | 78 | 78 | 19.9771 | 59 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 95.7912 | 73.1 | 70 | 4" MERV 8 | 4" MERV 8 | 74.19% | 1 | 168.5455 | 114.6187 | 52.783 | 34.4218 | 48.4944 | 34.4218 | 4.2886 | 0 | 29342.1165 | 19953.991 | 2.9475 | 1.6299 | 21.2606 | 7.9953 | 28965.8151 | 16435.1197 | 1.3631 | 0.46209 | 12.4244 | 2.3897 | 32.4364 | 10.1667 | 5.7214 | 11.9073 | 1.1925 | 1.0658 | 144.8 | 76 | 72.4 | 38 | 0 | 217.2 | 114 | 9.7534 | 8.3812 | 0 | 0 | 0 | 41.155 | 0 | 0 | 168.5455 | 114.75 | 52.7698 | 34.4594 | 48.4744 | 34.4594 | 4.2954 | 0 | 29309.7388 | 19954.81 | 2.9427 | 1.6301 | 21.2028 | 7.9965 | 28933.2873 | 16457.4814 | 1.3605 | 0.46335 | 12.3861 | 2.3995 | 32.3545 | 10.175 | 5.7341 | 11.911 | 1.192 | 1.0658 | 144.6 | 76.1 | 72.3 | 38.05 | 0 | 216.9 | 114.15 | 9.7446 | 8.3916 | 0 | 3459.5 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 59 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 95.7912 | 75 | 70 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8475 | 33.4881 | 14.1469 | 19.5879 | 19.7006 | 13.9002 | 18026.8307 | 17851.8129 | 2.1869 | 2.1562 | 9.6915 | 9.4625 | 18607.0699 | 18080.4592 | 0.79801 | 0.74791 | 4.6723 | 4.255 | 23.5 | 19.9 | 5.0702 | 5.9255 | 1.211 | 1.1786 | 79.2 | 65.3 | 39.6 | 32.65 | 0 | 118.8 | 97.95 | 8.0816 | 9.9966 | 0 | 41.155 | 41.155 | 54.3497 | 54.3497 | 4133.2667 | 4136.1 | 4231.6047 | -2.7001e-13 | 124.459 | 4231.6047 | 54.3497 | 41.155 | 172.3877 | 3963.7123
|  | CM | 99.7083 | 24 | 72 | 61.34 | 28.52% | 0.012189 | 37.4 | 1639.4167 | 64 | 152.2309 | 202.9745 | 19.9778 | 74.19% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Dehum | 0 | 0 | 1.8217 | 1.4574 | 61 | 1259.52 | 1854 | 78 | 78 | 19.9778 | 61 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 99.7083 | 73.1 | 72 | 4" MERV 8 | 4" MERV 8 | 74.19% | 1 | 168.5455 | 114.6228 | 52.7803 | 34.4223 | 48.4921 | 33.4191 | 4.2882 | 1.0033 | 29335.3727 | 19950.1178 | 2.9465 | 1.6297 | 21.2485 | 7.9924 | 28921.5575 | 19565.2124 | 1.3595 | 0.64448 | 12.3723 | 3.9677 | 32.3818 | 12.0583 | 5.731 | 10.0348 | 1.1921 | 1.0781 | 144.6 | 87.5 | 72.3 | 43.75 | 0 | 216.9 | 131.25 | 9.7432 | 9.6427 | 0 | 0 | 0 | 24.35 | 0 | 0 | 168.5455 | 114.75 | 52.7675 | 34.4588 | 48.4727 | 33.4466 | 4.2948 | 1.0122 | 29304.0121 | 19950.9111 | 2.9419 | 1.6298 | 21.1926 | 7.9936 | 28890.0932 | 19565.6914 | 1.3569 | 0.64462 | 12.3354 | 3.9686 | 32.3 | 12.0667 | 5.7433 | 10.0413 | 1.1917 | 1.0781 | 144.5 | 87.5 | 72.25 | 43.75 | 0 | 216.75 | 131.25 | 9.7347 | 9.6457 | 0 | 2896 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 61 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 99.7083 | 75 | 72 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8465 | 33.4877 | 14.1461 | 17.418 | 19.7003 | 16.0698 | 18023.3085 | 17848.3249 | 2.1864 | 2.1562 | 9.6871 | 9.4608 | 18579.7865 | 18189.075 | 0.79608 | 0.75694 | 4.6542 | 4.3323 | 23.5 | 21.1 | 5.0743 | 5.5867 | 1.2108 | 1.1895 | 79.1 | 67.1 | 39.55 | 33.55 | 0 | 118.65 | 100.65 | 8.0714 | 10.2743 | 0 | 24.35 | 24.35 | 54.5 | 54.5 | 3400.4 | 3402.4 | 3481.25 | -6.3949e-14 | 145.0521 | 3481.25 | 54.5 | 24.35 | 121.7843 | 3280.6157
|  | CN | 103.8875 | 8 | 74 | 63.09 | 26.77% | 0.012983 | 39.31 | 1662.275 | 64.6 | 153.1348 | 204.1798 | 19.9786 | 74.19% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | 0 | Dehum | 0 | 0 | 2.7037 | 2.1629 | 63 | 1259.52 | 1854 | 78 | 78 | 19.9786 | 63 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 103.8875 | 73.1 | 74 | 4" MERV 8 | 4" MERV 8 | 74.19% | 1 | 168.5455 | 114.6272 | 52.7773 | 34.423 | 48.4895 | 31.0608 | 4.2878 | 3.3621 | 29328.1903 | 19945.9977 | 2.9454 | 1.6295 | 21.2357 | 7.9898 | 28874.4702 | 19682.8812 | 1.3557 | 0.65266 | 12.3171 | 4.0423 | 32.3182 | 13.3583 | 5.7412 | 9.0581 | 1.1918 | 1.0865 | 144.4 | 90.1 | 72.2 | 45.05 | 0 | 216.6 | 135.15 | 9.7322 | 9.933 | 0 | 0 | 0 | 6.445 | 0 | 0 | 168.5455 | 114.75 | 52.7651 | 34.4582 | 48.4708 | 31.0875 | 4.2942 | 3.3706 | 29297.92 | 19946.7635 | 2.941 | 1.6296 | 21.1818 | 7.9909 | 28844.1336 | 19683.3386 | 1.3532 | 0.65279 | 12.2816 | 4.0432 | 32.2455 | 13.3667 | 5.7531 | 9.0642 | 1.1913 | 1.0865 | 144.3 | 90.1 | 72.15 | 45.05 | 0 | 216.45 | 135.15 | 9.7239 | 9.9359 | 0 | 1069.3333 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 63 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 103.8875 | 75 | 74 | 4" MERV 8 | 4" MERV 8 | 99.03% | 0 | 111.24 | 110.16 | 33.8454 | 33.4873 | 14.1454 | 15.2152 | 19.7001 | 18.2721 | 18019.5616 | 17844.6144 | 2.1858 | 2.1563 | 9.6826 | 9.4589 | 18550.7606 | 18299.3171 | 0.79403 | 0.76652 | 4.6349 | 4.4137 | 23.4 | 22.3 | 5.0787 | 5.2797 | 1.2106 | 1.2005 | 79 | 69.3 | 39.5 | 34.65 | 0 | 118.5 | 103.95 | 8.0606 | 10.6148 | 0 | 6.445 | 6.445 | 23.8111 | 23.8111 | 1247.0667 | 1247.7333 | 1277.9895 | -6.2172e-14 | 159.7487 | 1277.9895 | 23.8111 | 6.445 | 40.6298 | 1207.1036
|  | CO |  | 0
|  |  | total | 2395 | hours | [195 empty] | Ventilation MLC component | Generator MLC component | UPS room MLC component | ITE room MLC component
[201 empty] | 0.0098221 | 0.0064531 | 0.0037404 | 0.062587

## 100% Bins
[196 empty] | NO | selected | Resulting | Resulting | Ventilation | Gen | UPS | ITE
| Notes on this 90.4 MLC calculation: | 2°F dry bulb bins (for hours equal or below 65°F dry bulb) | [7 empty] | Annual HW demand of cafeteria: |  |  |  | ITE zone | ITE zone | Properties of IT equipment zone: | [5 empty] | Properties for generic ventilation air handlers. | [17 empty] | Information used for hourly inputs for ITE room IDEC units (shown with heat recovery input) | [27 empty] | Outputs for ITE room IDEC units with heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | HR export |  | Generator room | [19 empty] | Outputs for ITE room IDEC units without heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | Without HR | UPS room variables | [13 empty] | Information used for hourly inputs for UPS room IDEC units | [27 empty] | Outputs for UPS units. NOTE: most of the performance values are PER UNIT | [18 empty] | Generator Room |  | Ventilation system |  | ITE and UPS cooling |  | Recovery | recovery | Mechanical | Mechanical | system | room | room | room
1. | This tab shows performance when data center is 100% loaded. There are two | bin | Outdoor | bin | average |  |  |  | Psychrometry for averaged points: | café avg | entering | kw from | H2O heater | delta T | % desigm | Temp | AHU | Min | Max | min. | max. | control | heat | liquid | Cooling | DX split | room air | Project | Design | Design | Reset | Resulting | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | energy avoided | Room heat | engine block | Recovery | Recovery | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | error | ITE cooling | UPS room | Battery | Project | Design | Design | Design | Alternate | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | with | without | with | without | with | without | whatsoever | savings | Input | energy | HVAC | HVAC | cooling | cooling
| traditional modeling methods that I used here to determine the MLC. | name | dry bulb | hours | °F wb | dewpoint | %rh | moisture | enthalpy | 140 | temp | hot aisle | input energy | w/ HR | w/ HR | into ITE | SAT: | moisture | moisture | enthalpy | enthalpy | mode | power | added | needed | kW input: | dew point | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | elsewhere | need, kWh | heat, kWh | Potential | Savings | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | annual kWh | temp | temp | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | recovery | recovery | recovery | recovery | recovery | recovery | at all | kWh: | Power | incl. Recov | Component | component | component | component
|  | AB | 65 | 378 | 51.8048 | 40.53 | 40.64% | 0.0055757 | 21.66 | 2217.6138 | 61.7 | 106.0761 | 141.4348 | 19.9822 | 98.94% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 9.7592 | 1.2139 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9822 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 65 | 75 | 51.8048 | 4" MERV 8 | 4" MERV 8 | 98.94% | 3 | 168.5455 | 131.0263 | 52.7921 | 39.5976 | 45.5715 | 39.5976 | 7.2206 | 0 | 29364.4381 | 22827.7493 | 2.9507 | 1.8229 | 21.3004 | 10.2295 | 29389.6599 | 5709.7628 | 1.3872 | 0.062301 | 12.8283 | 0.11193 | 34.3636 | 9.8714 | 5.4018 | 14.1045 | 1.2039 | 1.0745 | 137.1 | 42.7 | 68.55 | 21.35 | 0 | 205.65 | 64.05 | 9.2393 | 5.4937 | 0 | 0 | 0 | 1039.5 | 0 | 0 | 168.5455 | 131.1429 | 52.7818 | 39.6311 | 45.5588 | 39.6311 | 7.223 | 0 | 29339.2726 | 22828.477 | 2.947 | 1.823 | 21.2555 | 10.2308 | 29364.0101 | 5715.9713 | 1.3851 | 0.062428 | 12.7976 | 0.11228 | 34.3 | 9.8714 | 5.4109 | 14.1159 | 1.2035 | 1.0745 | 137 | 42.7 | 68.5 | 21.35 | 0 | 205.5 | 64.05 | 9.233 | 5.4984 | 0 | 18657 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 65 | 75 | 51.8048 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8525 | 34.7094 | 14.1507 | 34.7094 | 19.7018 | 0 | 18044.9953 | 18465.4612 | 2.1898 | 2.2555 | 9.7138 | 10.2385 | 18747.7842 | 11914.0359 | 0.80802 | 0.33021 | 4.7667 | 1.2379 | 23.6 | 10.6 | 5.049 | 11.5101 | 1.2119 | 1.0953 | 79.7 | 44.4 | 39.85 | 22.2 | 0 | 119.55 | 66.6 | 8.1341 | 6.8003 | 0 | 1039.5 | 1039.5 | 946.8956 | 3996.4697 | 48783.6 | 48783.6 | 53819.5697 | 0 | 142.3798 | 53819.5697 | 3996.4697 | 1039.5 | 1908.5046 | 46875.0954
2. | A 2°F bin hour-grouping method is shown on each of these 25%, 50%, 75% | AC | 63 | 251 | 50.3876 | 39.11 | 41.23% | 0.0052714 | 20.85 | 3339.6733 | 61 | 103.3402 | 137.7869 | 19.9821 | 98.94% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 11.5126 | 1.4835 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9821 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 63 | 75 | 50.3876 | 4" MERV 8 | 4" MERV 8 | 98.94% | 3 | 168.5455 | 131.0257 | 52.7921 | 39.5975 | 45.5715 | 39.5975 | 7.2206 | 0 | 29364.5674 | 22827.7455 | 2.9508 | 1.8229 | 21.3006 | 10.2295 | 29389.791 | 5497.8647 | 1.3872 | 0.057971 | 12.8285 | 0.10029 | 34.3636 | 9.8643 | 5.4017 | 14.119 | 1.2039 | 1.0745 | 137.1 | 41.9 | 68.55 | 20.95 | 0 | 205.65 | 62.85 | 9.2394 | 5.388 | 0 | 0 | 0 | 715.35 | 0 | 0 | 168.5455 | 131.1429 | 52.7818 | 39.6311 | 45.5588 | 39.6311 | 7.223 | 0 | 29339.2726 | 22828.477 | 2.947 | 1.823 | 21.2555 | 10.2308 | 29364.0101 | 5503.8005 | 1.3851 | 0.058089 | 12.7976 | 0.1006 | 34.3 | 9.8643 | 5.4109 | 14.1304 | 1.2035 | 1.0745 | 137 | 41.9 | 68.5 | 20.95 | 0 | 205.5 | 62.85 | 9.233 | 5.3927 | 0 | 12379.6786 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 63 | 75 | 50.3876 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8525 | 34.7094 | 14.1507 | 34.7094 | 19.7018 | 0 | 18044.9953 | 18465.4612 | 2.1898 | 2.2555 | 9.7138 | 10.2385 | 18747.7842 | 10764.7892 | 0.80802 | 0.27076 | 4.7667 | 0.91715 | 23.6 | 10.3 | 5.049 | 11.8213 | 1.2119 | 1.0928 | 79.7 | 42 | 39.85 | 21 | 0 | 119.55 | 63 | 8.1341 | 6.4324 | 0 | 715.35 | 715.35 | 705.0414 | 3093.8419 | 32296.5286 | 32296.5286 | 36105.7205 | -5.1159e-12 | 143.8475 | 36105.7205 | 3093.8419 | 715.35 | 1267.2874 | 31029.2411
| and 100% load scenario tabs. The bin-group calculation method was | AD | 61 | 308 | 49.6315 | 39.36 | 44.69% | 0.0053243 | 20.42 | 2721.6169 | 60.3 | 108.4983 | 144.6643 | 19.9806 | 98.93% | 77.9263 | 77.5263 | 0.006946 | 0.013892 | 26.1505 | 33.4369 | Heat-Hum | 12.4048 | 1.4366 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.9263 | 19.9806 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 61 | 75 | 49.6315 | 4" MERV 8 | 4" MERV 8 | 98.93% | 3 | 168.5455 | 131.0158 | 52.793 | 39.5942 | 45.5726 | 39.5942 | 7.2204 | 0 | 29366.7028 | 22824.6669 | 2.9511 | 1.8225 | 21.3045 | 10.2273 | 29391.9671 | 5421.3797 | 1.3874 | 0.056287 | 12.8311 | 0.09602 | 34.3727 | 9.8571 | 5.4009 | 14.1272 | 1.2039 | 1.0744 | 137.1 | 40.9 | 68.55 | 20.45 | 0 | 205.65 | 61.35 | 9.2399 | 5.2644 | 0 | 0 | 0 | 908.6 | 0 | 0 | 168.5455 | 131.1429 | 52.7818 | 39.6306 | 45.5588 | 39.6306 | 7.223 | 0 | 29339.2726 | 22825.46 | 2.947 | 1.8227 | 21.2555 | 10.2288 | 29364.0101 | 5427.6708 | 1.3851 | 0.05641 | 12.7976 | 0.096342 | 34.3 | 9.8571 | 5.4109 | 14.1397 | 1.2035 | 1.0744 | 137 | 41 | 68.5 | 20.5 | 0 | 205.5 | 61.5 | 9.233 | 5.2693 | 0 | 15180 | 85.2261 | 64.2261 | 1259.52 | 111.24 | 65 | 64.2261 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 61 | 75 | 49.6315 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8525 | 34.7047 | 14.1507 | 34.7047 | 19.7018 | 0 | 18044.9953 | 18439.2737 | 2.1898 | 2.251 | 9.7138 | 10.2182 | 18747.7842 | 10896.0952 | 0.80802 | 0.27626 | 4.7667 | 0.94717 | 23.6 | 10.3 | 5.049 | 11.8233 | 1.2119 | 1.0928 | 79.7 | 40.4 | 39.85 | 20.2 | 0 | 119.55 | 60.6 | 8.1341 | 6.1889 | 0 | 908.6 | 908.6 | 912.7805 | 4071.2228 | 39604.4 | 39604.4 | 44584.2228 | -1.3642e-12 | 144.754 | 44584.2228 | 4071.2228 | 908.6 | 1555.0778 | 38049.3222
| attractive to me because it required only 49 iterations of inputs & outputs per | AE | 59 | 266 | 47.9132 | 37.22 | 44.14% | 0.0048929 | 19.47 | 3151.3459 | 59.7 | 93.524 | 124.6986 | 19.9827 | 98.94% | 77.5826 | 77.1826 | 0.006946 | 0.013892 | 26.0673 | 33.3537 | Heat-Hum | 14.2812 | 1.8188 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.5826 | 19.9827 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 59 | 75 | 47.9132 | 4" MERV 8 | 4" MERV 8 | 98.94% | 3 | 168.5455 | 131.0296 | 52.7918 | 39.596 | 45.5711 | 39.596 | 7.2207 | 0 | 29363.716 | 22810.685 | 2.9506 | 1.8208 | 21.2991 | 10.218 | 29388.9239 | 5281.3379 | 1.3871 | 0.053518 | 12.8275 | 0.088939 | 34.3636 | 9.8357 | 5.402 | 14.1558 | 1.2039 | 1.0743 | 137.1 | 40.3 | 68.55 | 20.15 | 0 | 205.65 | 60.45 | 9.2392 | 5.184 | 0 | 0 | 215.9033 | 798 | 0 | 0 | 168.5455 | 131.1429 | 52.7818 | 39.6285 | 45.5588 | 39.6285 | 7.223 | 0 | 29339.2726 | 22811.3918 | 2.947 | 1.821 | 21.2555 | 10.2192 | 29364.0101 | 5286.7354 | 1.3851 | 0.053621 | 12.7976 | 0.089201 | 34.3 | 9.8357 | 5.4109 | 14.167 | 1.2035 | 1.0743 | 137 | 40.3 | 68.5 | 20.15 | 0 | 205.5 | 60.45 | 9.233 | 5.1883 | 0 | 13081.5 | 81.6176 | 60.6176 | 1259.52 | 111.24 | 65 | 60.6176 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 59 | 75 | 47.9132 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8525 | 34.6832 | 14.1507 | 34.6832 | 19.7018 | 0 | 18044.9953 | 18317.162 | 2.1898 | 2.2302 | 9.7138 | 10.1239 | 18747.7842 | 13165.3267 | 0.80802 | 0.39809 | 4.7667 | 1.6491 | 23.6 | 10.8 | 5.049 | 11.296 | 1.2119 | 1.097 | 79.7 | 41.8 | 39.85 | 20.9 | 0 | 119.55 | 62.7 | 8.1341 | 6.3955 | 0 | 798 | 798 | 874.8213 | 4015.1677 | 34268.4 | 34268.4 | 39081.5677 | 0 | 146.9232 | 39081.5677 | 4015.1677 | 798 | 1343.0217 | 32925.3783
| zone per scenario for the manufacturer's tool, as opposed to 8760 iterations | AF | 57 | 282 | 46.766 | 36.61 | 46.29% | 0.0047757 | 18.85 | 2972.5461 | 59 | 101.1002 | 134.8003 | 19.9807 | 98.93% | 77.3532 | 76.9532 | 0.006946 | 0.013892 | 26.0118 | 33.2982 | Heat-Hum | 15.503 | 1.9226 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.3532 | 19.9807 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 57 | 75 | 46.766 | 4" MERV 8 | 4" MERV 8 | 98.93% | 3 | 168.5455 | 131.0162 | 52.793 | 39.5906 | 45.5726 | 39.5906 | 7.2204 | 0 | 29366.626 | 22801.2087 | 2.9511 | 1.8197 | 21.3043 | 10.2114 | 29391.8901 | 5202.1705 | 1.3874 | 0.051882 | 12.831 | 0.084927 | 34.3636 | 9.8214 | 5.401 | 14.1718 | 1.2039 | 1.0742 | 137.1 | 39.5 | 68.55 | 19.75 | 0 | 205.65 | 59.25 | 9.2399 | 5.0822 | 0 | 0 | 686.67 | 846 | 0 | 0 | 168.5455 | 131.1429 | 52.7818 | 39.627 | 45.5588 | 39.627 | 7.223 | 0 | 29339.2726 | 22801.9996 | 2.947 | 1.8198 | 21.2555 | 10.2129 | 29364.0101 | 5208.0632 | 1.3851 | 0.051992 | 12.7976 | 0.085204 | 34.3 | 9.8214 | 5.4109 | 14.1843 | 1.2035 | 1.0742 | 137 | 39.5 | 68.5 | 19.75 | 0 | 205.5 | 59.25 | 9.233 | 5.0869 | 0 | 13848.2143 | 79.2085 | 58.2085 | 1259.52 | 111.24 | 65 | 58.2085 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 57 | 75 | 46.766 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8525 | 34.669 | 14.1507 | 34.669 | 19.7018 | 0 | 18044.9953 | 18235.6374 | 2.1898 | 2.2164 | 9.7138 | 10.0613 | 18747.7842 | 15070.1717 | 0.80802 | 0.51637 | 4.7667 | 2.4486 | 23.6 | 11.4 | 5.049 | 10.6914 | 1.2119 | 1.1025 | 79.7 | 41.9 | 39.85 | 20.95 | 0 | 119.55 | 62.85 | 8.1341 | 6.4125 | 0 | 846 | 846 | 987.1659 | 4601.2494 | 36450.5143 | 36450.5143 | 41897.7637 | 0 | 148.5736 | 41897.7637 | 4601.2494 | 846 | 1423.805 | 35026.7093
| per zone per scenario... even though that is possible. I did use the full 8760 | AG | 55 | 284 | 45.3053 | 35.21 | 47.08% | 0.0045143 | 18.09 | 2951.6127 | 58.4 | 103.9008 | 138.5343 | 19.9794 | 98.93% | 77.0611 | 76.6611 | 0.006946 | 0.013892 | 25.9411 | 33.2275 | Heat-Hum | 16.9951 | 2.1542 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.0611 | 19.9794 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 55 | 75 | 45.3053 | 4" MERV 8 | 4" MERV 8 | 98.93% | 3 | 168.5455 | 131.0079 | 52.7937 | 39.5864 | 45.5735 | 39.5864 | 7.2202 | 0 | 29368.4078 | 22789.1985 | 2.9513 | 1.8182 | 21.3075 | 10.2033 | 29393.7053 | 5106.8197 | 1.3875 | 0.050001 | 12.8332 | 0.080348 | 34.3727 | 9.8071 | 5.4003 | 14.1924 | 1.2039 | 1.0741 | 137.1 | 38.8 | 68.55 | 19.4 | 0 | 205.65 | 58.2 | 9.2403 | 4.9952 | 0 | 0 | 1152.5667 | 852 | 0 | 0 | 168.5455 | 131.1429 | 52.7818 | 39.6252 | 45.5588 | 39.6252 | 7.223 | 0 | 29339.2726 | 22790.0409 | 2.947 | 1.8184 | 21.2555 | 10.2048 | 29364.0101 | 5112.9151 | 1.3851 | 0.050113 | 12.7976 | 0.080625 | 34.3 | 9.8071 | 5.4109 | 14.2058 | 1.2035 | 1.0741 | 137 | 38.9 | 68.5 | 19.45 | 0 | 205.5 | 58.35 | 9.233 | 5.0001 | 0 | 13926.1429 | 76.1411 | 55.1411 | 1259.52 | 111.24 | 65 | 55.1411 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 55 | 75 | 45.3053 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8525 | 34.6537 | 14.1507 | 34.6537 | 19.7018 | 0 | 18044.9953 | 18142.5996 | 2.1898 | 2.2017 | 9.7138 | 9.9945 | 18747.7842 | 17533.3885 | 0.80802 | 0.69231 | 4.7667 | 3.8196 | 23.6 | 12.5 | 5.049 | 9.7505 | 1.2119 | 1.1123 | 79.7 | 42.7 | 39.85 | 21.35 | 0 | 119.55 | 64.05 | 8.1341 | 6.537 | 0 | 852 | 852 | 1067.6153 | 5057.6313 | 36972.7429 | 36972.7429 | 42882.3742 | 0 | 150.9943 | 42882.3742 | 5057.6313 | 852 | 1433.9029 | 35538.8399
| annual hour calculation method to sychronize the data center operation with | AH | 53 | 273 | 44.43 | 35.38 | 51% | 0.0045457 | 17.64 | 3070.5421 | 57.7 | 109.0853 | 145.4471 | 19.9776 | 98.92% | 76.886 | 76.486 | 0.0066891 | 0.013378 | 25.6292 | 32.6461 | Heat-Hum | 17.2941 | 1.8987 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.886 | 19.9776 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 53 | 75 | 44.43 | 4" MERV 8 | 4" MERV 8 | 98.92% | 3 | 168.5455 | 130.9958 | 52.7955 | 39.5822 | 45.5753 | 39.5822 | 7.2202 | 0 | 29372.8153 | 22783.3508 | 2.952 | 1.8175 | 21.3154 | 10.1998 | 29409.992 | 5062.0424 | 1.3889 | 0.049008 | 12.8528 | 0.078062 | 34.4 | 9.8 | 5.3968 | 14.2016 | 1.2041 | 1.074 | 137.2 | 38 | 68.6 | 19 | 0 | 205.8 | 57 | 9.2439 | 4.8862 | 0 | 0 | 1551.095 | 819 | 0 | 0 | 168.5455 | 131.1429 | 52.7826 | 39.6244 | 45.5594 | 39.6244 | 7.2232 | 0 | 29341.0671 | 22784.2687 | 2.9473 | 1.8177 | 21.2587 | 10.2015 | 29377.6183 | 5068.5765 | 1.3862 | 0.049127 | 12.8139 | 0.078352 | 34.3182 | 9.8 | 5.4083 | 14.2162 | 1.2036 | 1.074 | 137.1 | 38 | 68.55 | 19 | 0 | 205.65 | 57 | 9.2359 | 4.8914 | 0 | 13377 | 74.3031 | 53.3031 | 1259.52 | 111.24 | 65 | 53.3031 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 53 | 75 | 44.43 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8529 | 34.6496 | 14.1509 | 34.6496 | 19.7019 | 0 | 18046.099 | 18118.2138 | 2.1899 | 2.1976 | 9.7151 | 9.9765 | 18756.3342 | 17509.5299 | 0.80863 | 0.68823 | 4.7725 | 3.7919 | 23.6 | 12.4 | 5.0477 | 9.7889 | 1.212 | 1.1119 | 79.7 | 40.1 | 39.85 | 20.05 | 0 | 119.55 | 60.15 | 8.1373 | 6.1467 | 0 | 819 | 819 | 1040.4104 | 4943.3524 | 35490 | 35490 | 41252.3524 | 0 | 151.1075 | 41252.3524 | 4943.3524 | 819 | 1378.011 | 34111.989
| the cafeteria heat recovery input, and to create chronological tallies of water | AI | 51 | 156 | 42.7795 | 33.57 | 51.07% | 0.0042271 | 16.81 | 5373.4487 | 57 | 116.2923 | 155.0564 | 19.9752 | 98.91% | 76.5559 | 76.1559 | 0.0066891 | 0.013378 | 25.5493 | 32.5661 | Heat-Hum | 18.9178 | 2.1809 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.5559 | 19.9752 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 51 | 75 | 42.7795 | 4" MERV 8 | 4" MERV 8 | 98.91% | 3 | 168.5455 | 130.98 | 52.7969 | 39.5756 | 45.5771 | 39.5756 | 7.2198 | 0 | 29376.2443 | 22769.7378 | 2.9525 | 1.8158 | 21.3215 | 10.1905 | 29413.4974 | 4968.9798 | 1.3891 | 0.047231 | 12.857 | 0.073849 | 34.4091 | 9.7857 | 5.3955 | 14.223 | 1.2041 | 1.0739 | 137.2 | 37.4 | 68.6 | 18.7 | 0 | 205.8 | 56.1 | 9.2449 | 4.8097 | 0 | 0 | 1139.58 | 468 | 0 | 0 | 168.5455 | 131.1429 | 52.7826 | 39.6223 | 45.5594 | 39.6223 | 7.2232 | 0 | 29341.0671 | 22770.7546 | 2.9473 | 1.8161 | 21.2587 | 10.1923 | 29377.6183 | 4976.0059 | 1.3862 | 0.047357 | 12.8139 | 0.07415 | 34.3182 | 9.7857 | 5.4083 | 14.2393 | 1.2036 | 1.0739 | 137.1 | 37.4 | 68.55 | 18.7 | 0 | 205.65 | 56.1 | 9.2359 | 4.8153 | 0 | 7632.8571 | 70.8369 | 49.8369 | 1259.52 | 111.24 | 65 | 49.8369 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 51 | 75 | 42.7795 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8529 | 34.6415 | 14.1509 | 34.6415 | 19.7019 | 0 | 18046.099 | 18070.8734 | 2.1899 | 2.1897 | 9.7151 | 9.9406 | 18756.3342 | 17449.4837 | 0.80863 | 0.68267 | 4.7725 | 3.7483 | 23.6 | 12.4 | 5.0477 | 9.8571 | 1.212 | 1.1111 | 79.7 | 38.9 | 39.85 | 19.45 | 0 | 119.55 | 58.35 | 8.1373 | 5.9627 | 0 | 671.58 | 671.58 | 638.4242 | 3078.0703 | 20253.2571 | 20253.2571 | 24002.9074 | 1.819e-12 | 153.8648 | 24002.9074 | 3078.0703 | 671.58 | 787.4348 | 19465.8223
| & potential fuel oil use, in order to calculate the tank sizes you see at top of | AJ | 49 | 258 | 41.8876 | 33.83 | 55.6% | 0.0042714 | 16.37 | 3249.062 | 56.4 | 114.1402 | 152.187 | 19.9746 | 98.9% | 76.3775 | 75.9775 | 0.0066891 | 0.013378 | 25.5061 | 32.523 | Heat-Hum | 19.7768 | 2.1417 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.3775 | 19.9746 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 49 | 75 | 41.8876 | 4" MERV 8 | 4" MERV 8 | 98.9% | 3 | 168.5455 | 130.9765 | 52.7972 | 39.5734 | 45.5774 | 39.5734 | 7.2198 | 0 | 29377.0036 | 22762.4134 | 2.9526 | 1.8149 | 21.3229 | 10.1855 | 29414.2619 | 4928.6739 | 1.3892 | 0.04635 | 12.8579 | 0.071883 | 34.4091 | 9.7714 | 5.3952 | 14.2348 | 1.2041 | 1.0738 | 137.2 | 36.6 | 68.6 | 18.3 | 0 | 205.8 | 54.9 | 9.245 | 4.7045 | 0 | 0 | 2303.51 | 774 | 0 | 0 | 168.5455 | 131.1429 | 52.7826 | 39.6212 | 45.5594 | 39.6212 | 7.2232 | 0 | 29341.0671 | 22763.4522 | 2.9473 | 1.8152 | 21.2587 | 10.1874 | 29377.6183 | 4935.7435 | 1.3862 | 0.046475 | 12.8139 | 0.07218 | 34.3182 | 9.7786 | 5.4083 | 14.2514 | 1.2036 | 1.0738 | 137.1 | 36.6 | 68.55 | 18.3 | 0 | 205.65 | 54.9 | 9.2359 | 4.7101 | 0 | 12614.3571 | 68.964 | 47.964 | 1259.52 | 111.24 | 65 | 47.964 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 49 | 75 | 41.8876 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8529 | 34.637 | 14.1509 | 34.637 | 19.7019 | 0 | 18046.099 | 18045.2186 | 2.1899 | 2.1855 | 9.7151 | 9.9212 | 18756.3342 | 17417.505 | 0.80863 | 0.67812 | 4.7725 | 3.7166 | 23.6 | 12.3 | 5.0477 | 9.9001 | 1.212 | 1.1106 | 79.7 | 36.4 | 39.85 | 18.2 | 0 | 119.55 | 54.6 | 8.1373 | 5.5749 | 0 | 1529.51 | 1529.51 | 1094.2684 | 5312.2732 | 33425.7429 | 33447.8571 | 40289.6404 | 2.2737e-12 | 156.1614 | 40289.6404 | 5312.2732 | 1529.51 | 1302.2961 | 32145.5611
| the Summary tab. | AK | 47 | 418 | 40.4057 | 32.57 | 56.99% | 0.00406 | 15.66 | 2005.4019 | 55.7 | 111.6775 | 148.9034 | 19.9741 | 98.9% | 76.0811 | 75.6811 | 0.0066891 | 0.013378 | 25.4344 | 32.4512 | Heat-Hum | 21.1584 | 2.329 | 0 | 0 | 45 | 1259.52 | 1854 | 78 | 76.0811 | 19.9741 | 45 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 47 | 75 | 40.4057 | 4" MERV 8 | 4" MERV 8 | 98.9% | 3 | 168.5455 | 130.9731 | 52.7975 | 39.5706 | 45.5778 | 39.5706 | 7.2197 | 0 | 29377.7253 | 22750.2598 | 2.9527 | 1.8135 | 21.3242 | 10.1773 | 29414.9985 | 4859.0733 | 1.3893 | 0.045011 | 12.8588 | 0.068821 | 34.4091 | 9.7571 | 5.395 | 14.2543 | 1.2042 | 1.0737 | 137.2 | 35.9 | 68.6 | 17.95 | 0 | 205.8 | 53.85 | 9.2452 | 4.6238 | 0 | 0 | 4410.5967 | 1254 | 0 | 0 | 168.5455 | 131.1429 | 52.7826 | 39.6193 | 45.5594 | 39.6193 | 7.2232 | 0 | 29341.0671 | 22751.3194 | 2.9473 | 1.8137 | 21.2587 | 10.1792 | 29377.6183 | 4866.1131 | 1.3862 | 0.045134 | 12.8139 | 0.069109 | 34.3182 | 9.7643 | 5.4083 | 14.2713 | 1.2036 | 1.0737 | 137.1 | 36 | 68.55 | 18 | 0 | 205.65 | 54 | 9.2359 | 4.6294 | 0 | 20407.3571 | 65.8521 | 44.8521 | 1259.52 | 111.24 | 65 | 44.8521 | 21 | 45 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 47 | 75 | 40.4057 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8529 | 34.6298 | 14.1509 | 34.6298 | 19.7019 | 0 | 18046.099 | 18002.9931 | 2.1899 | 2.1784 | 9.7151 | 9.8893 | 18756.3342 | 17364.5999 | 0.80863 | 0.67288 | 4.7725 | 3.6766 | 23.6 | 12.2 | 5.0477 | 9.9628 | 1.212 | 1.1099 | 79.7 | 34.9 | 39.85 | 17.45 | 0 | 119.55 | 52.35 | 8.1373 | 5.3445 | 0 | 3156.5967 | 3156.5967 | 1872.9853 | 9184.2234 | 54041.4286 | 54077.2571 | 66418.0772 | 5.457e-12 | 158.8949 | 66418.0772 | 9184.2234 | 3156.5967 | 2109.9215 | 51967.3356
|  | AL | 45 | 287 | 39.3812 | 32.57 | 61.48% | 0.00406 | 15.18 | 2920.7596 | 55.1 | 114.0592 | 152.0789 | 19.9724 | 98.89% | 75.8762 | 75.4762 | 0.006485 | 0.01297 | 25.1706 | 31.9734 | Heat-Hum | 21.6265 | 2.1482 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.8762 | 19.9724 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 45 | 75 | 39.3812 | 4" MERV 8 | 4" MERV 8 | 98.89% | 3 | 168.5455 | 130.9618 | 52.7991 | 39.5664 | 45.5795 | 39.5664 | 7.2196 | 0 | 29381.7411 | 22743.013 | 2.9533 | 1.8126 | 21.3313 | 10.1728 | 29429.3874 | 4819.1579 | 1.3905 | 0.044163 | 12.8761 | 0.066969 | 34.4273 | 9.75 | 5.3918 | 14.265 | 1.2043 | 1.0736 | 137.3 | 35.2 | 68.65 | 17.6 | 0 | 205.95 | 52.8 | 9.2484 | 4.5255 | 0 | 0 | 3494.225 | 861 | 0 | 0 | 168.5455 | 131.1429 | 52.7832 | 39.6183 | 45.5599 | 39.6183 | 7.2233 | 0 | 29342.6315 | 22744.1434 | 2.9475 | 1.8129 | 21.2615 | 10.1749 | 29389.4843 | 4826.5543 | 1.3872 | 0.044291 | 12.8281 | 0.067266 | 34.3273 | 9.75 | 5.406 | 14.2832 | 1.2037 | 1.0736 | 137.1 | 35.2 | 68.55 | 17.6 | 0 | 205.65 | 52.8 | 9.2385 | 4.5314 | 0 | 13991.25 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 45 | 75 | 39.3812 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8531 | 34.6506 | 14.1512 | 34.6506 | 19.702 | 0 | 18047.0612 | 18129.1368 | 2.1901 | 2.1985 | 9.7163 | 9.9809 | 18763.7881 | 11677.0975 | 0.80916 | 0.30976 | 4.7775 | 1.1382 | 23.6 | 10.1 | 5.0465 | 12.009 | 1.212 | 1.0912 | 79.7 | 30.6 | 39.85 | 15.3 | 0 | 119.55 | 45.9 | 8.1401 | 4.6854 | 0 | 2633.225 | 2633.225 | 1309.2852 | 6440.2717 | 36477.7 | 36477.7 | 45551.1967 | 0 | 158.715 | 45551.1967 | 6440.2717 | 2633.225 | 1448.3542 | 35029.3458
3. | At least one manufacturer of IDEC cooling equipment maintains a | AM | 43 | 392 | 37.6204 | 30.82 | 61.46% | 0.0037586 | 14.37 | 2138.4133 | 54.4 | 113.4134 | 151.2178 | 19.9713 | 98.89% | 75.5241 | 75.1241 | 0.006485 | 0.01297 | 25.0854 | 31.8881 | Heat-Hum | 23.1954 | 2.4152 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.5241 | 19.9713 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 43 | 75 | 37.6204 | 4" MERV 8 | 4" MERV 8 | 98.89% | 3 | 168.5455 | 130.9545 | 52.7998 | 39.5621 | 45.5803 | 39.5621 | 7.2195 | 0 | 29383.3306 | 22728.5498 | 2.9535 | 1.8108 | 21.3342 | 10.163 | 29430.9987 | 4747.0416 | 1.3906 | 0.042829 | 12.8781 | 0.063974 | 34.4364 | 9.7357 | 5.3912 | 14.2871 | 1.2043 | 1.0735 | 137.3 | 34.6 | 68.65 | 17.3 | 0 | 205.95 | 51.9 | 9.2488 | 4.4569 | 0 | 0 | 5408.9467 | 1176 | 0 | 0 | 168.5455 | 131.1429 | 52.7832 | 39.6161 | 45.5599 | 39.6161 | 7.2233 | 0 | 29342.6315 | 22729.7261 | 2.9475 | 1.8111 | 21.2615 | 10.1651 | 29389.4843 | 4754.5417 | 1.3872 | 0.042956 | 12.8281 | 0.064266 | 34.3273 | 9.7357 | 5.406 | 14.3061 | 1.2037 | 1.0735 | 137.1 | 34.7 | 68.55 | 17.35 | 0 | 205.65 | 52.05 | 9.2385 | 4.4629 | 0 | 19082 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 43 | 75 | 37.6204 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8531 | 34.6506 | 14.1512 | 34.6506 | 19.702 | 0 | 18047.0612 | 18129.1368 | 2.1901 | 2.1985 | 9.7163 | 9.9809 | 18763.7881 | 10542.8998 | 0.80916 | 0.25361 | 4.7775 | 0.84133 | 23.6 | 9.9 | 5.0465 | 12.3226 | 1.212 | 1.0889 | 79.7 | 29.5 | 39.85 | 14.75 | 0 | 119.55 | 44.25 | 8.1401 | 4.5169 | 0 | 4232.9467 | 4232.9467 | 1894.8883 | 9411.4602 | 49677.6 | 49677.6 | 63322.0069 | 0 | 161.5357 | 63322.0069 | 9411.4602 | 4232.9467 | 1978.2398 | 47699.3602
| spreadsheet-based performance tool. That expert tool is what I used to | AN | 41 | 329 | 36.0012 | 29.5 | 62.46% | 0.0035343 | 13.64 | 2547.8967 | 53.7 | 101.7807 | 135.7076 | 19.973 | 98.9% | 75.2002 | 74.8002 | 0.006485 | 0.01297 | 25.007 | 31.8097 | Heat-Hum | 24.6059 | 2.6139 | 0 | 0 | 44.1 | 1259.52 | 1854 | 78 | 75.2002 | 19.973 | 44.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 41 | 75 | 36.0012 | 4" MERV 8 | 4" MERV 8 | 98.9% | 3 | 168.5455 | 130.9655 | 52.7988 | 39.5632 | 45.5791 | 39.5632 | 7.2197 | 0 | 29380.9346 | 22715.361 | 2.9532 | 1.8093 | 21.3299 | 10.1542 | 29428.564 | 4688.6621 | 1.3904 | 0.041732 | 12.8751 | 0.06157 | 34.4273 | 9.7214 | 5.3921 | 14.3089 | 1.2043 | 1.0734 | 137.3 | 34.1 | 68.65 | 17.05 | 0 | 205.95 | 51.15 | 9.2482 | 4.3836 | 0 | 0 | 5073.7283 | 987 | 0 | 0 | 168.5455 | 131.1429 | 52.7832 | 39.6141 | 45.5599 | 39.6141 | 7.2233 | 0 | 29342.6315 | 22716.4681 | 2.9475 | 1.8095 | 21.2615 | 10.1562 | 29389.4843 | 4695.5653 | 1.3872 | 0.041848 | 12.8281 | 0.061832 | 34.3273 | 9.7214 | 5.406 | 14.3268 | 1.2037 | 1.0734 | 137.1 | 34.1 | 68.55 | 17.05 | 0 | 205.65 | 51.15 | 9.2385 | 4.3891 | 0 | 15991.75 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 44.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 41 | 75 | 36.0012 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8531 | 34.6506 | 14.1512 | 34.6506 | 19.702 | 0 | 18047.0612 | 18129.1368 | 2.1901 | 2.1985 | 9.7163 | 9.9809 | 18763.7881 | 9694.1382 | 0.80916 | 0.21505 | 4.7775 | 0.65599 | 23.6 | 9.7 | 5.0465 | 12.5269 | 1.212 | 1.0874 | 79.7 | 28.4 | 39.85 | 14.2 | 0 | 119.55 | 42.6 | 8.1401 | 4.3554 | 0 | 4086.7283 | 4086.7283 | 1670.7882 | 8362.9652 | 41571.5 | 41571.5 | 54021.1936 | 0 | 164.1982 | 54021.1936 | 8362.9652 | 4086.7283 | 1660.3084 | 39911.1916
| transform each unique bin's "Input" row of data to the horizontally-adjacent | AO | 39 | 281 | 34.1466 | 27.62 | 61.86% | 0.0032371 | 12.84 | 2983.1246 | 53.1 | 116.4903 | 155.3204 | 19.9675 | 98.87% | 74.8293 | 74.4293 | 0.0062436 | 0.012487 | 24.664 | 31.2135 | Heat-Hum | 25.5952 | 2.6633 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.8293 | 19.9675 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 39 | 75 | 34.1466 | 4" MERV 8 | 4" MERV 8 | 98.87% | 3 | 168.5455 | 130.9295 | 52.8192 | 39.5584 | 45.5961 | 39.5584 | 7.2231 | 0 | 29390.583 | 22701.3809 | 2.9646 | 1.8135 | 21.4194 | 10.1782 | 29450.7658 | 4628.9291 | 1.3922 | 0.040634 | 12.9017 | 0.059185 | 34.5273 | 9.7357 | 5.3784 | 14.2885 | 1.2049 | 1.0735 | 137.3 | 33.6 | 68.65 | 16.8 | 0 | 205.95 | 50.4 | 9.254 | 4.3179 | 0 | 0 | 4789.645 | 843 | 0 | 0 | 168.5455 | 131.1429 | 52.784 | 39.6121 | 45.5604 | 39.6121 | 7.2235 | 0 | 29344.4804 | 22702.713 | 2.9478 | 1.8079 | 21.2648 | 10.1475 | 29403.5071 | 4636.0429 | 1.3883 | 0.040753 | 12.845 | 0.05945 | 34.3455 | 9.7071 | 5.4033 | 14.3482 | 1.2038 | 1.0733 | 137.2 | 33.6 | 68.6 | 16.8 | 0 | 205.8 | 50.4 | 9.2415 | 4.3237 | 0 | 13638.5357 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 39 | 75 | 34.1466 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8534 | 34.651 | 14.1514 | 34.651 | 19.7021 | 0 | 18048.1984 | 18130.2791 | 2.1903 | 2.1987 | 9.7177 | 9.9823 | 18772.5974 | 8897.7936 | 0.80979 | 0.18175 | 4.7835 | 0.50888 | 23.6 | 9.6 | 5.0452 | 12.6924 | 1.2121 | 1.0863 | 79.8 | 27.7 | 39.9 | 13.85 | 0 | 119.7 | 41.55 | 8.1434 | 4.2401 | 0 | 3946.645 | 3946.645 | 1475.2094 | 7420.8249 | 35526.4286 | 35430.0857 | 46797.5556 | 0 | 166.5393 | 46797.5556 | 7420.8249 | 3946.645 | 1417.7 | 34012.3857
| "output" line of data that you see here. They are recorded like a series of | AP | 37 | 392 | 33.0765 | 27.79 | 67.47% | 0.0032643 | 12.39 | 2138.4133 | 52.4 | 110.92 | 147.8933 | 19.9673 | 98.87% | 74.6153 | 74.2153 | 0.0062436 | 0.012487 | 24.6122 | 31.1617 | Heat-Hum | 26.4571 | 2.6393 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.6153 | 19.9673 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 37 | 75 | 33.0765 | 4" MERV 8 | 4" MERV 8 | 98.87% | 3 | 168.5455 | 130.9287 | 52.8193 | 39.5568 | 45.5962 | 39.5568 | 7.2231 | 0 | 29390.7515 | 22692.6135 | 2.9646 | 1.8124 | 21.4197 | 10.1722 | 29450.9387 | 11257.3716 | 1.3922 | 0.17526 | 12.9019 | 0.62083 | 34.5273 | 9.05 | 5.3784 | 15.3642 | 1.2049 | 1.0684 | 137.3 | 0 | 68.65 | 0 | 0 | 205.95 | 0 | 9.2541 | 0 | 0 | 0 | 7317.9867 | 1176 | 0 | 0 | 168.5455 | 131.1429 | 52.784 | 39.6108 | 45.5604 | 39.6108 | 7.2235 | 0 | 29344.4804 | 22693.9506 | 2.9478 | 1.8068 | 21.2648 | 10.1416 | 29403.5071 | 11269.4465 | 1.3883 | 0.17566 | 12.845 | 0.62291 | 34.3455 | 9.0286 | 5.4033 | 15.4257 | 1.2038 | 1.0682 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2415 | 0 | 0 | 17696 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 37 | 75 | 33.0765 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8534 | 34.6608 | 14.1514 | 34.6608 | 19.7021 | 0 | 18048.1984 | 18169.2519 | 2.1903 | 2.2081 | 9.7177 | 10.0254 | 18772.5974 | 17494.9682 | 0.80979 | 0.60205 | 4.7835 | 3.3143 | 23.6 | 11.2 | 5.0452 | 10.8936 | 1.2121 | 1.1006 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1434 | 0 | 0 | 6141.9867 | 6141.9867 | 2116.5093 | 10690.07 | 46961.6 | 46860.8 | 63692.8567 | 0 | 162.4818 | 63692.8567 | 10690.07 | 6141.9867 | 1977.7167 | 44883.0833
| snapshots, and there are several scenes occuring in each bin. | AQ | 35 | 453 | 31.6302 | 27 | 70.36% | 0.0031443 | 11.77 | 1850.4592 | 51.8 | 119.4056 | 159.2074 | 19.9628 | 98.85% | 74.326 | 73.926 | 0.0062436 | 0.012487 | 24.5422 | 31.0917 | Heat-Hum | 27.6477 | 2.7456 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.326 | 19.9628 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 35 | 75 | 31.6302 | 4" MERV 8 | 4" MERV 8 | 98.85% | 3 | 168.5455 | 130.8992 | 52.8219 | 39.5465 | 45.5994 | 39.5465 | 7.2225 | 0 | 29397.1496 | 22680.586 | 2.9655 | 1.8109 | 21.4312 | 10.1639 | 29457.4679 | 10801.0401 | 1.3928 | 0.16165 | 12.9098 | 0.54938 | 34.5455 | 8.9786 | 5.3761 | 15.4861 | 1.205 | 1.0678 | 137.4 | 0 | 68.7 | 0 | 0 | 206.1 | 0 | 9.2557 | 0 | 0 | 0 | 9192.125 | 1359 | 0 | 0 | 168.5455 | 131.1429 | 52.784 | 39.6089 | 45.5604 | 39.6089 | 7.2235 | 0 | 29344.4804 | 22682.1076 | 2.9478 | 1.8054 | 21.2648 | 10.1336 | 29403.5071 | 10814.3335 | 1.3883 | 0.16206 | 12.845 | 0.55149 | 34.3455 | 8.9571 | 5.4033 | 15.5512 | 1.2038 | 1.0676 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2415 | 0 | 0 | 20287.9286 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 35 | 75 | 31.6302 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8534 | 34.651 | 14.1514 | 34.651 | 19.7021 | 0 | 18048.1984 | 18130.2791 | 2.1903 | 2.1987 | 9.7177 | 9.9823 | 18772.5974 | 16783.5587 | 0.80979 | 0.55419 | 4.7835 | 2.9267 | 23.6 | 10.8 | 5.0452 | 11.2845 | 1.2121 | 1.0971 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1434 | 0 | 0 | 7833.125 | 7833.125 | 2539.3421 | 12892.8842 | 53699.9143 | 53583.4286 | 74309.4378 | 0 | 164.0385 | 74309.4378 | 12892.8842 | 7833.125 | 2285.4736 | 51297.9549
|  | AR | 33 | 264 | 30.7235 | 27.56 | 78.25% | 0.0032286 | 11.38 | 3175.2197 | 51.1 | 104.8148 | 139.7531 | 19.9654 | 98.86% | 74.1447 | 73.7447 | 0.0062436 | 0.012487 | 24.4983 | 31.0478 | Heat-Hum | 28.3969 | 2.6709 | 0 | 0 | 43 | 1259.52 | 1854 | 78 | 74.1447 | 19.9654 | 43 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 33 | 75 | 30.7235 | 4" MERV 8 | 4" MERV 8 | 98.86% | 3 | 168.5455 | 130.916 | 52.8204 | 39.5502 | 45.5976 | 39.5502 | 7.2228 | 0 | 29393.5094 | 22673.266 | 2.965 | 1.81 | 21.4247 | 10.1591 | 29453.7618 | 10371.201 | 1.3925 | 0.14931 | 12.9053 | 0.48727 | 34.5364 | 8.9214 | 5.3774 | 15.5932 | 1.2049 | 1.0673 | 137.4 | 0 | 68.7 | 0 | 0 | 206.1 | 0 | 9.2548 | 0 | 0 | 0 | 5785.56 | 792 | 0 | 0 | 168.5455 | 131.1429 | 52.784 | 39.6078 | 45.5604 | 39.6078 | 7.2235 | 0 | 29344.4804 | 22674.6826 | 2.9478 | 1.8045 | 21.2648 | 10.1286 | 29403.5071 | 10382.9092 | 1.3883 | 0.14967 | 12.845 | 0.48897 | 34.3455 | 8.8929 | 5.4033 | 15.658 | 1.2038 | 1.0672 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2415 | 0 | 0 | 11738.5714 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 43 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 33 | 75 | 30.7235 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8534 | 34.651 | 14.1514 | 34.651 | 19.7021 | 0 | 18048.1984 | 18130.2791 | 2.1903 | 2.1987 | 9.7177 | 9.9823 | 18772.5974 | 15400.6395 | 0.80979 | 0.46674 | 4.7835 | 2.2619 | 23.6 | 10.2 | 5.0452 | 11.9233 | 1.2121 | 1.0919 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1434 | 0 | 0 | 4993.56 | 4993.56 | 1514.1639 | 7711.5211 | 30955.8857 | 30865.3714 | 43570.4525 | 0 | 165.0396 | 43570.4525 | 7711.5211 | 4993.56 | 1331.9317 | 29533.4398
4. | Knowing this, it should be possible to review my calculation (for any given | AS | 31 | 424 | 29.216 | 26.62 | 81.64% | 0.00309 | 10.75 | 1977.0236 | 50.4 | 111.9235 | 149.2313 | 19.9607 | 98.83% | 73.8432 | 73.4432 | 0.0060517 | 0.012103 | 24.224 | 30.5723 | Heat-Hum | 29.1669 | 2.6237 | 0 | 0 | 42.1 | 1259.52 | 1854 | 78 | 73.8432 | 19.9607 | 42.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 31 | 75 | 29.216 | 4" MERV 8 | 4" MERV 8 | 98.83% | 3 | 168.5455 | 130.885 | 52.8237 | 39.5397 | 45.6014 | 39.5397 | 7.2223 | 0 | 29401.6908 | 22661.8579 | 2.9662 | 1.8086 | 21.4393 | 10.1516 | 29471.7289 | 10003.7951 | 1.3939 | 0.13913 | 12.927 | 0.43794 | 34.5636 | 8.8643 | 5.3728 | 15.6836 | 1.2051 | 1.0669 | 137.4 | 0 | 68.7 | 0 | 0 | 206.1 | 0 | 9.2589 | 0 | 0 | 0 | 9980.2533 | 1272 | 0 | 0 | 168.5455 | 131.1429 | 52.7846 | 39.6062 | 45.5609 | 39.6062 | 7.2237 | 0 | 29345.9429 | 22663.4682 | 2.948 | 1.8032 | 21.2674 | 10.1216 | 29414.5986 | 10016.7332 | 1.3892 | 0.1395 | 12.8583 | 0.4397 | 34.3636 | 8.8429 | 5.4012 | 15.7519 | 1.2039 | 1.0668 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2439 | 0 | 0 | 18746.8571 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 42.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 31 | 75 | 29.216 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8537 | 34.6512 | 14.1516 | 34.6512 | 19.7021 | 0 | 18049.0979 | 18131.1827 | 2.1904 | 2.1988 | 9.7188 | 9.9835 | 18779.5653 | 14218.8889 | 0.81029 | 0.39784 | 4.7882 | 1.78 | 23.6 | 9.8 | 5.0441 | 12.4323 | 1.2121 | 1.0881 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.146 | 0 | 0 | 8708.2533 | 8708.2533 | 2488.4329 | 12711.6804 | 49256.6857 | 49147.6571 | 70567.5908 | 0 | 166.433 | 70567.5908 | 12711.6804 | 8708.2533 | 2138.7153 | 47008.9418
| snapshot) using your own manufacturers' tool. Punch in my input shown for | AT | 29 | 342 | 26.8234 | 23.22 | 76.28% | 0.00263 | 9.78 | 2451.0468 | 49.8 | 98.7671 | 131.6894 | 19.9629 | 98.85% | 73.3647 | 72.9647 | 0.0060517 | 0.012103 | 24.1082 | 30.4564 | Heat-Hum | 31.0159 | 3.0312 | 0 | 0 | 42.1 | 1259.52 | 1854 | 78 | 73.3647 | 19.9629 | 42.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 29 | 75 | 26.8234 | 4" MERV 8 | 4" MERV 8 | 98.85% | 3 | 168.5455 | 130.8996 | 52.8225 | 39.5409 | 45.5998 | 39.5409 | 7.2226 | 0 | 29398.5246 | 22642.3559 | 2.9657 | 1.8063 | 21.4336 | 10.1385 | 29468.4871 | 9693.2804 | 1.3937 | 0.1308 | 12.9231 | 0.39895 | 34.5636 | 8.8143 | 5.374 | 15.777 | 1.205 | 1.0665 | 137.4 | 0 | 68.7 | 0 | 0 | 206.1 | 0 | 9.258 | 0 | 0 | 0 | 8605.29 | 1026 | 0 | 0 | 168.5455 | 131.1429 | 52.7846 | 39.6032 | 45.5609 | 39.6032 | 7.2237 | 0 | 29345.9429 | 22643.8749 | 2.948 | 1.8008 | 21.2674 | 10.1084 | 29414.5986 | 9704.9656 | 1.3892 | 0.13113 | 12.8583 | 0.40044 | 34.3636 | 8.7857 | 5.4012 | 15.8448 | 1.2039 | 1.0664 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2439 | 0 | 0 | 15023.5714 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 42.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 29 | 75 | 26.8234 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8537 | 34.6512 | 14.1516 | 34.6512 | 19.7021 | 0 | 18049.0979 | 18131.1827 | 2.1904 | 2.1988 | 9.7188 | 9.9835 | 18779.5653 | 13188.4326 | 0.81029 | 0.34224 | 4.7882 | 1.4203 | 23.6 | 9.5 | 5.0441 | 12.8424 | 1.2121 | 1.0853 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.146 | 0 | 0 | 7579.29 | 7579.29 | 2116.7847 | 10885.6415 | 39422.8286 | 39305.5714 | 57770.5029 | 0 | 168.9196 | 57770.5029 | 10885.6415 | 7579.29 | 1725.0959 | 37580.4756
| any line of input, you should get close to my output. | AU | 27 | 116 | 24.4672 | 19.74 | 70.89% | 0.0022257 | 8.86 | 7226.3621 | 49.1 | 93.7488 | 124.9983 | 19.9622 | 98.84% | 72.8934 | 72.4934 | 0.0058452 | 0.01169 | 23.7775 | 29.9091 | Heat-Hum | 32.2916 | 3.2064 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72.8934 | 19.9622 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 27 | 75 | 24.4672 | 4" MERV 8 | 4" MERV 8 | 98.84% | 3 | 168.5455 | 130.8948 | 52.8236 | 39.5369 | 45.6009 | 39.5369 | 7.2227 | 0 | 29401.2828 | 22624.3638 | 2.9662 | 1.8041 | 21.4386 | 10.1269 | 29482.6645 | 9410.272 | 1.3949 | 0.12341 | 12.9402 | 0.36542 | 34.5818 | 8.7643 | 5.3711 | 15.8583 | 1.2052 | 1.0662 | 137.5 | 0 | 68.75 | 0 | 0 | 206.25 | 0 | 9.2611 | 0 | 0 | 0 | 3107.06 | 348 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.6006 | 45.5614 | 39.6006 | 7.2238 | 0 | 29347.6707 | 22625.9126 | 2.9483 | 1.7987 | 21.2705 | 10.0969 | 29427.7032 | 9421.7946 | 1.3903 | 0.12372 | 12.8741 | 0.3668 | 34.3818 | 8.7429 | 5.3986 | 15.9272 | 1.204 | 1.066 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 5070.8571 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 27 | 75 | 24.4672 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 12300.6112 | 0.81088 | 0.29758 | 4.7938 | 1.1518 | 23.6 | 9.3 | 5.0429 | 13.1651 | 1.2122 | 1.0832 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 2759.06 | 2759.06 | 743.6232 | 3840.1866 | 13278.6857 | 13248.8571 | 19848.1038 | 0 | 171.1043 | 19848.1038 | 3840.1866 | 2759.06 | 584.9755 | 12663.8816
|  | AV | 25 | 42 | 22.5357 | 17.51 | 69.9% | 0.0019971 | 8.13 | 19958.5238 | 48.5 | 112.1066 | 149.4754 | 19.9512 | 98.79% | 72.5071 | 72.1071 | 0.0058452 | 0.01169 | 23.684 | 29.8156 | Heat-Hum | 33.6694 | 3.4089 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72.5071 | 19.9512 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 25 | 75 | 22.5357 | 4" MERV 8 | 4" MERV 8 | 98.79% | 3 | 168.5455 | 130.8226 | 52.83 | 39.5137 | 45.6088 | 39.5137 | 7.2212 | 0 | 29416.9482 | 22608.0942 | 2.9685 | 1.8021 | 21.4667 | 10.1154 | 29498.6626 | 9133.4336 | 1.3962 | 0.11639 | 12.9596 | 0.3345 | 34.6182 | 8.7214 | 5.3655 | 15.9261 | 1.2054 | 1.0659 | 137.5 | 0 | 68.75 | 0 | 0 | 206.25 | 0 | 9.2651 | 0 | 0 | 0 | 1193.15 | 126 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.5981 | 45.5614 | 39.5981 | 7.2238 | 0 | 29347.6707 | 22610.0944 | 2.9483 | 1.7968 | 21.2705 | 10.0862 | 29427.7032 | 9148.1554 | 1.3903 | 0.11678 | 12.8741 | 0.33615 | 34.3818 | 8.7 | 5.3986 | 16.002 | 1.204 | 1.0657 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 1827 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 25 | 75 | 22.5357 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 11523.6173 | 0.81088 | 0.26107 | 4.7938 | 0.94664 | 23.6 | 9.1 | 5.0429 | 13.424 | 1.2122 | 1.0816 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 1067.15 | 1067.15 | 279.273 | 1448.2794 | 4777.8 | 4767 | 7282.4294 | 0 | 173.3912 | 7282.4294 | 1448.2794 | 1067.15 | 211.8015 | 4555.1985
5. | I did use generic performance data (excel formulas) for the ventilation units. | AW | 23 | 25 | 19.956 | 12.66 | 60.54% | 0.0015729 | 7.2 | 33530.32 | 47.8 | 99.9655 | 133.2873 | 19.9527 | 98.79% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 35.4168 | 3.7847 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.9527 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 23 | 75 | 19.956 | 4" MERV 8 | 4" MERV 8 | 98.79% | 3 | 168.5455 | 130.8324 | 52.8291 | 39.5133 | 45.6077 | 39.5133 | 7.2214 | 0 | 29414.8122 | 22587.3897 | 2.9681 | 1.7996 | 21.4629 | 10.1015 | 29496.481 | 8896.9226 | 1.396 | 0.11055 | 12.9569 | 0.30949 | 34.6182 | 8.6857 | 5.3662 | 16.0013 | 1.2054 | 1.0656 | 137.5 | 0 | 68.75 | 0 | 0 | 206.25 | 0 | 9.2645 | 0 | 0 | 0 | 750.7917 | 75 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 8910.704 | 1.3903 | 0.1109 | 12.8741 | 0.31096 | 34.3818 | 8.6571 | 5.3986 | 16.077 | 1.204 | 1.0654 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 1082.1429 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 23 | 75 | 19.956 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 10839.1207 | 0.81088 | 0.23083 | 4.7938 | 0.7873 | 23.6 | 8.9 | 5.0429 | 13.6322 | 1.2122 | 1.0803 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 675.7917 | 675.7917 | 173.8058 | 905.7561 | 2828.2143 | 2819.6429 | 4401.1906 | 0 | 176.0476 | 4401.1906 | 905.7561 | 675.7917 | 126.0723 | 2693.5705
|  | AX | 21 | 23 | 18.4913 | 12.19 | 65.07% | 0.0015371 | 6.68 | 36446 | 47.1 | 63.404 | 84.5386 | 19.9671 | 98.87% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 36.5424 | 3.8164 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.9671 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 21 | 75 | 18.4913 | 4" MERV 8 | 4" MERV 8 | 98.87% | 3 | 168.5455 | 130.9272 | 52.8207 | 39.5405 | 45.5974 | 39.5405 | 7.2234 | 0 | 29394.2777 | 22587.9817 | 2.9651 | 1.7998 | 21.426 | 10.1026 | 29475.5105 | 8630.6591 | 1.3943 | 0.10415 | 12.9316 | 0.28284 | 34.5636 | 8.6571 | 5.3736 | 16.0534 | 1.2051 | 1.0654 | 137.4 | 0 | 68.7 | 0 | 0 | 206.1 | 0 | 9.2594 | 0 | 0 | 0 | 728.065 | 69 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 8639.4941 | 1.3903 | 0.10437 | 12.8741 | 0.28374 | 34.3818 | 8.6357 | 5.3986 | 16.1211 | 1.204 | 1.0652 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 993.1071 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 21 | 75 | 18.4913 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 10241.3468 | 0.81088 | 0.20592 | 4.7938 | 0.6636 | 23.6 | 8.8 | 5.0429 | 13.7983 | 1.2122 | 1.0794 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 659.065 | 659.065 | 164.3888 | 859.1852 | 2591.7714 | 2585.8571 | 4104.1074 | 0 | 178.4395 | 4104.1074 | 859.1852 | 659.065 | 115.9865 | 2469.8706
6. | The most difficult task was calculating accurate wet bulb values for TMY data. | AY | 19 | 10 | 16.38 | 8.98 | 61.02% | 0.0013086 | 5.95 | 83825.8 | 46.5 | 156.3258 | 208.4345 | 19.9104 | 98.59% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 38.1226 | 4.0188 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.9104 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 19 | 75 | 16.38 | 4" MERV 8 | 4" MERV 8 | 98.59% | 3 | 168.5455 | 130.5552 | 52.8538 | 39.4337 | 45.6381 | 39.4337 | 7.2157 | 0 | 29475.0407 | 22585.6584 | 2.977 | 1.7992 | 21.5711 | 10.0982 | 29557.9895 | 8370.3856 | 1.4011 | 0.098051 | 13.0314 | 0.25825 | 34.7727 | 8.6357 | 5.3446 | 16.0565 | 1.2063 | 1.0652 | 137.7 | 0 | 68.85 | 0 | 0 | 206.55 | 0 | 9.2797 | 0 | 0 | 0 | 332.7833 | 30 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 8395.6006 | 1.3903 | 0.098655 | 12.8741 | 0.26063 | 34.3818 | 8.6143 | 5.3986 | 16.1587 | 1.204 | 1.0651 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 430.7143 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 19 | 75 | 16.38 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 9709.966 | 0.81088 | 0.18494 | 4.7938 | 0.56505 | 23.6 | 8.7 | 5.0429 | 13.9336 | 1.2122 | 1.0786 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 302.7833 | 302.7833 | 74.2124 | 389.361 | 1123.2857 | 1120.7143 | 1812.8586 | 0 | 181.2859 | 1812.8586 | 389.361 | 302.7833 | 50.4289 | 1070.2854
|  | AZ | 17 | 16 | 13.6313 | 1.78 | 46.49% | 0.00090429 | 5.04 | 52391.125 | 45.8 | 161.9005 | 215.8674 | 19.8963 | 98.52% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 40.0925 | 4.377 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8963 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 17 | 75 | 13.6313 | 4" MERV 8 | 4" MERV 8 | 98.52% | 3 | 168.5455 | 130.4626 | 52.8621 | 39.4072 | 45.6483 | 39.4072 | 7.2138 | 0 | 29495.2065 | 22585.0804 | 2.98 | 1.799 | 21.6075 | 10.0971 | 29578.5833 | 8148.5556 | 1.4028 | 0.092999 | 13.0564 | 0.23845 | 34.8182 | 8.6143 | 5.3374 | 16.0794 | 1.2066 | 1.0651 | 137.8 | 0 | 68.9 | 0 | 0 | 206.7 | 0 | 9.2848 | 0 | 0 | 0 | 558.4267 | 48 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 8176.9179 | 1.3903 | 0.093659 | 12.8741 | 0.24098 | 34.3818 | 8.6 | 5.3986 | 16.1908 | 1.204 | 1.0649 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 688 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 17 | 75 | 13.6313 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 9236.1195 | 0.81088 | 0.16715 | 4.7938 | 0.48578 | 23.6 | 8.7 | 5.0429 | 14.0444 | 1.2122 | 1.078 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 510.4267 | 510.4267 | 124.2028 | 654.4953 | 1793.1429 | 1790.4 | 2955.322 | 0 | 184.7076 | 2955.322 | 654.4953 | 510.4267 | 80.6863 | 1709.7137
7. | Because this is a model for an indirect evaporative cooling system, I decided | BA | 15 | 8 | 12.8625 | 5.83 | 63.19% | 0.0011143 | 4.79 | 104782.25 | 45.2 | 138.4562 | 184.6082 | 19.8995 | 98.53% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 40.6337 | 4.191 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8995 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 15 | 75 | 12.8625 | 4" MERV 8 | 4" MERV 8 | 98.53% | 3 | 168.5455 | 130.4835 | 52.8602 | 39.4132 | 45.6459 | 39.4132 | 7.2143 | 0 | 29490.6421 | 22585.2112 | 2.9793 | 1.7991 | 21.5992 | 10.0974 | 29573.9225 | 7963.0617 | 1.4024 | 0.088876 | 13.0508 | 0.22269 | 34.8091 | 8.6 | 5.3391 | 16.1071 | 1.2065 | 1.065 | 137.8 | 0 | 68.9 | 0 | 0 | 206.7 | 0 | 9.2837 | 0 | 0 | 0 | 292.2 | 24 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 7989.631 | 1.3903 | 0.089479 | 12.8741 | 0.22495 | 34.3818 | 8.5857 | 5.3986 | 16.2171 | 1.204 | 1.0648 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 343.4286 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 15 | 75 | 12.8625 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 8821.5121 | 0.81088 | 0.1523 | 4.7938 | 0.42276 | 23.6 | 8.6 | 5.0429 | 14.1337 | 1.2122 | 1.0775 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 268.2 | 268.2 | 62.8518 | 331.577 | 894.4 | 893.0286 | 1492.8056 | 0 | 186.6007 | 1492.8056 | 331.577 | 268.2 | 40.3431 | 852.6854
| to "split" the 2°F bin hours into two groupings, to more closely represent the | BB | 13 | 14 | 10.8643 | 3.02 | 60.35% | 0.00096429 | 4.15 | 59875.5714 | 44.5 | 102.5066 | 136.6755 | 19.9141 | 98.6% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 42.0191 | 4.3238 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.9141 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 13 | 75 | 10.8643 | 4" MERV 8 | 4" MERV 8 | 98.6% | 3 | 168.5455 | 130.5796 | 52.8516 | 39.4408 | 45.6354 | 39.4408 | 7.2162 | 0 | 29469.7149 | 22585.8112 | 2.9762 | 1.7992 | 21.5615 | 10.0985 | 29552.5507 | 7799.883 | 1.4007 | 0.085321 | 13.0248 | 0.20941 | 34.7545 | 8.5929 | 5.3465 | 16.1383 | 1.2062 | 1.0649 | 137.7 | 0 | 68.85 | 0 | 0 | 206.55 | 0 | 9.2784 | 0 | 0 | 0 | 534.0767 | 42 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 7821.7053 | 1.3903 | 0.085806 | 12.8741 | 0.21119 | 34.3818 | 8.5714 | 5.3986 | 16.2398 | 1.204 | 1.0647 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 600 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 13 | 75 | 10.8643 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 8447.6582 | 0.81088 | 0.13948 | 4.7938 | 0.37077 | 23.6 | 8.6 | 5.0429 | 14.2083 | 1.2122 | 1.0771 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 492.0767 | 492.0767 | 113.3524 | 599.6553 | 1564 | 1560.4 | 2652.132 | 0 | 189.438 | 2652.132 | 599.6553 | 492.0767 | 70.6005 | 1489.7995
| two phases if an indirect evaporative unit's intended sequence of operation, | BC | 11 | 19 | 8.1211 | -5.46 | 42.65% | 0.00061714 | 3.29 | 44118.8421 | 43.8 | 145.8029 | 194.4038 | 19.8556 | 98.31% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 43.8807 | 4.6314 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8556 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 11 | 75 | 8.1211 | 4" MERV 8 | 4" MERV 8 | 98.31% | 3 | 168.5455 | 130.1961 | 52.886 | 39.3306 | 45.6777 | 39.3306 | 7.2083 | 0 | 29553.43 | 22583.4161 | 2.9886 | 1.7986 | 21.7126 | 10.094 | 29638.0457 | 7637.2424 | 1.4078 | 0.081837 | 13.1289 | 0.19667 | 34.9727 | 8.5786 | 5.3167 | 16.1211 | 1.2075 | 1.0648 | 138 | 0 | 69 | 0 | 0 | 207 | 0 | 9.2995 | 0 | 0 | 0 | 755.6617 | 57 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 7673.6074 | 1.3903 | 0.082626 | 12.8741 | 0.19951 | 34.3818 | 8.5643 | 5.3986 | 16.259 | 1.204 | 1.0647 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 813.6071 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 11 | 75 | 8.1211 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 8111.4622 | 0.81088 | 0.12842 | 4.7938 | 0.32777 | 23.6 | 8.5 | 5.0429 | 14.2705 | 1.2122 | 1.0767 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 698.6617 | 698.6617 | 159.9663 | 849.1889 | 2117.4143 | 2114.1571 | 3662.0077 | 0 | 192.7372 | 3662.0077 | 849.1889 | 698.6617 | 95.815 | 2018.3422
| according to this design. See this distinction represented graphically on each | BD | 9 | 25 | 5.576 | -15.93 | 26.54% | 0.00034714 | 2.53 | 33530.32 | 43.2 | 149.1292 | 198.8389 | 19.8195 | 98.14% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 45.5259 | 4.8705 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8195 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 9 | 75 | 5.576 | 4" MERV 8 | 4" MERV 8 | 98.14% | 3 | 168.5455 | 129.9593 | 52.9075 | 39.2627 | 45.704 | 39.2627 | 7.2035 | 0 | 29605.3603 | 22581.9374 | 2.9963 | 1.7982 | 21.8067 | 10.0913 | 29691.0908 | 7502.5462 | 1.4122 | 0.079006 | 13.1937 | 0.18651 | 35.1091 | 8.5643 | 5.2983 | 16.1142 | 1.2083 | 1.0647 | 138.2 | 0 | 69.1 | 0 | 0 | 207.3 | 0 | 9.3127 | 0 | 0 | 0 | 1034.875 | 75 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 7547.0145 | 1.3903 | 0.079952 | 12.8741 | 0.18987 | 34.3818 | 8.5571 | 5.3986 | 16.275 | 1.204 | 1.0646 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 1069.6429 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 9 | 75 | 5.576 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 7811.47 | 0.81088 | 0.11892 | 4.7938 | 0.29229 | 23.6 | 8.5 | 5.0429 | 14.3223 | 1.2122 | 1.0765 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 959.875 | 959.875 | 217.6108 | 1158.4827 | 2781.7857 | 2779.6429 | 4898.0006 | 0 | 195.92 | 4898.0006 | 1158.4827 | 959.875 | 126.0723 | 2653.5705
| IDEC units' submittal tab. | BE | 7 | 16 | 3.9125 | -16.83 | 27.91% | 0.00033 | 2.03 | 52391.125 | 42.5 | 0.46608 | 0.62144 | 19.9993 | 99.03% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 46.6082 | 4.8857 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.9993 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 7 | 75 | 3.9125 | 4" MERV 8 | 4" MERV 8 | 99.03% | 3 | 168.5455 | 131.1381 | 52.7857 | 39.5936 | 45.5619 | 39.5936 | 7.2237 | 0 | 29348.6968 | 22589.2987 | 2.9484 | 1.7943 | 21.2723 | 10.0722 | 29428.76 | 7442.563 | 1.3904 | 0.077777 | 12.8754 | 0.18215 | 34.3818 | 8.55 | 5.3983 | 16.2873 | 1.204 | 1.0645 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2471 | 0 | 0 | 0 | 688.2933 | 48 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 7442.7408 | 1.3903 | 0.077781 | 12.8741 | 0.18216 | 34.3818 | 8.55 | 5.3986 | 16.2877 | 1.204 | 1.0645 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 684 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 7 | 75 | 3.9125 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 7545.4944 | 0.81088 | 0.11078 | 4.7938 | 0.26303 | 23.6 | 8.5 | 5.0429 | 14.3653 | 1.2122 | 1.0762 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 640.2933 | 640.2933 | 142.2726 | 758.7464 | 1777.6 | 1777.6 | 3176.6397 | 0 | 198.54 | 3176.6397 | 758.7464 | 640.2933 | 80.6863 | 1696.9137
|  | BF | 5 | 4 | 1.575 | -31.11 | 13.44% | 0.00014286 | 1.35 | 209564.5 | 41.9 | 82.0132 | 109.3509 | 19.8213 | 98.14% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 48.0802 | 5.0515 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 19.8213 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 5 | 75 | 1.575 | 4" MERV 8 | 4" MERV 8 | 98.14% | 3 | 168.5455 | 129.9712 | 52.9064 | 39.2661 | 45.7027 | 39.2661 | 7.2037 | 0 | 29602.7354 | 22582.012 | 2.9959 | 1.7983 | 21.802 | 10.0914 | 29688.4016 | 7314.4127 | 1.412 | 0.075134 | 13.1904 | 0.17293 | 35.1 | 8.5571 | 5.2992 | 16.1376 | 1.2083 | 1.0646 | 138.2 | 0 | 69.1 | 0 | 0 | 207.3 | 0 | 9.3119 | 0 | 0 | 0 | 178.5667 | 12 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 7356.1215 | 1.3903 | 0.075998 | 12.8741 | 0.17591 | 34.3818 | 8.5429 | 5.3986 | 16.2981 | 1.204 | 1.0645 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 170.8571 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 5 | 75 | 1.575 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 7305.9859 | 0.81088 | 0.10369 | 4.7938 | 0.23838 | 23.6 | 8.5 | 5.0429 | 14.4017 | 1.2122 | 1.076 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 166.5667 | 166.5667 | 36.5887 | 195.5745 | 444.7429 | 444.0571 | 806.1983 | 0 | 201.5496 | 806.1983 | 195.5745 | 166.5667 | 20.1716 | 423.8856
8. | There is a "dry" group of hours sorted by dry bulb containing hours below 65°F | BG | 3 | 0
| dry bulb outdoors. Below those a moist group containing the rest of the hours, | BH | 1 | 0
| during which the evaporative process takes place. | BI | -1 | 2 | -3.8 | -44.97 | 7.74% | 6e-05 | -0.18 | 419129 | 39.9 | 94.515 | 126.0201 | 20 | 104.1% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 51.3921 | 5.1249 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -1 | 75 | -3.8 | 4" MERV 8 | 4" MERV 8 | 104.1% | 3 | 168.5455 | 137.8939 | 52.7853 | 41.8249 | 45.5614 | 41.8249 | 7.2238 | 0 | 29347.6707 | 23752.1995 | 2.9483 | 1.9367 | 21.2705 | 11.4317 | 29427.7032 | 7614.5884 | 1.3903 | 0.080453 | 12.8741 | 0.19277 | 34.3818 | 9.6857 | 5.3986 | 15.1781 | 1.204 | 1.0732 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 0 | 99.0233 | 6 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 7215.1786 | 1.3903 | 0.073138 | 12.8741 | 0.16605 | 34.3818 | 8.5357 | 5.3986 | 16.3145 | 1.204 | 1.0644 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 85.3571 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -1 | 75 | -3.8 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 6736.0571 | 0.81088 | 0.08772 | 4.7938 | 0.18593 | 23.6 | 8.4 | 5.0429 | 14.4798 | 1.2122 | 1.0756 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 93.0233 | 93.0233 | 19.4425 | 104.4112 | 249.2571 | 221.6571 | 419.0917 | 0 | 209.5458 | 419.0917 | 104.4112 | 93.0233 | 10.0858 | 211.5714
|  | BJ | -3 | 0
| Here is the sequence for repeating / reviewing my calculation. | BK | -5 | 1 | -6.7 | -25.11 | 32.42% | 0.00020429 | -0.98 | 838258 | 38.6 | 0 | 0 | 20 | 99.03% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 53.1239 | 4.9971 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -5 | 75 | -6.7 | 4" MERV 8 | 4" MERV 8 | 99.03% | 3 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 7222.2983 | 1.3903 | 0.073282 | 12.8741 | 0.16654 | 34.3818 | 8.5357 | 5.3986 | 16.3137 | 1.204 | 1.0644 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 0 | 52.7583 | 3 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 7222.2983 | 1.3903 | 0.073282 | 12.8741 | 0.16654 | 34.3818 | 8.5357 | 5.3986 | 16.3137 | 1.204 | 1.0644 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 42.6786 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -5 | 75 | -6.7 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 6459.3698 | 0.81088 | 0.08042 | 4.7938 | 0.16346 | 23.6 | 8.4 | 5.0429 | 14.5136 | 1.2122 | 1.0755 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 49.7583 | 49.7583 | 10.0214 | 53.9373 | 110.8286 | 110.8286 | 214.5242 | 0 | 214.5242 | 214.5242 | 53.9373 | 49.7583 | 5.0429 | 105.7857
|  | BL | -7 | 4 | -8.125 | -19.29 | 50.54% | 0.00028714 | -1.37 | 209564.5 | 37.9 | 126.5295 | 168.7061 | 20 | 100% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 53.9681 | 4.9237 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -7 | 75 | -8.125 | 4" MERV 8 | 4" MERV 8 | 100% | 3 | 168.5455 | 132.434 | 52.7853 | 40.0193 | 45.5614 | 40.0193 | 7.2238 | 0 | 29347.6707 | 22811.7231 | 2.9483 | 1.821 | 21.2705 | 10.323 | 29427.7032 | 7335.4658 | 1.3903 | 0.075406 | 12.8741 | 0.17405 | 34.3818 | 8.75 | 5.3986 | 16.0827 | 1.204 | 1.0661 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 0 | 217.5267 | 12 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 7258.8506 | 1.3903 | 0.074019 | 12.8741 | 0.16907 | 34.3818 | 8.5357 | 5.3986 | 16.3095 | 1.204 | 1.0645 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 170.7143 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -7 | 75 | -8.125 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 6347.6665 | 0.81088 | 0.077557 | 4.7938 | 0.15491 | 23.6 | 8.4 | 5.0429 | 14.5264 | 1.2122 | 1.0754 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 205.5267 | 205.5267 | 40.6709 | 219.1263 | 453.6 | 443.3143 | 867.9672 | 0 | 216.9918 | 867.9672 | 219.1263 | 205.5267 | 20.1716 | 423.1427
9. | Maintain coordination with electrical design. Keep input values in rows 44-46 | BM | -9 | 2 | -10.95 | -54.68 | 6.27% | 3.1429e-05 | -2.12 | 419129 | 37.2 | 70.7761 | 94.3682 | 20 | 99.45% | 72 | 71.6 | 0.0058452 | 0.01169 | 23.5612 | 29.6929 | Heat-Hum | 55.5916 | 5.1502 | 0 | 0 | 41 | 1259.52 | 1854 | 78 | 72 | 20 | 41 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | -9 | 75 | -10.95 | 4" MERV 8 | 4" MERV 8 | 99.45% | 3 | 168.5455 | 131.7046 | 52.7853 | 39.7795 | 45.5614 | 39.7795 | 7.2238 | 0 | 29347.6707 | 22686.0837 | 2.9483 | 1.8059 | 21.2705 | 10.1808 | 29427.7032 | 7350.2698 | 1.3903 | 0.075804 | 12.8741 | 0.17532 | 34.3818 | 8.6286 | 5.3986 | 16.2035 | 1.204 | 1.0652 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 0 | 112.01 | 6 | 0 | 0 | 168.5455 | 131.1429 | 52.7853 | 39.595 | 45.5614 | 39.595 | 7.2238 | 0 | 29347.6707 | 22589.3284 | 2.9483 | 1.7943 | 21.2705 | 10.0723 | 29427.7032 | 7316.6804 | 1.3903 | 0.075192 | 12.8741 | 0.17311 | 34.3818 | 8.5429 | 5.3986 | 16.3027 | 1.204 | 1.0645 | 137.2 | 0 | 68.6 | 0 | 0 | 205.8 | 0 | 9.2468 | 0 | 0 | 85.4286 | 76 | 55 | 1259.52 | 111.24 | 65 | 55 | 21 | 41 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | -9 | 75 | -10.95 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.854 | 34.6515 | 14.1518 | 34.6515 | 19.7022 | 0 | 18050.1605 | 18132.2501 | 2.1906 | 2.199 | 9.7201 | 9.9848 | 18787.7997 | 6249.8655 | 0.81088 | 0.075089 | 4.7938 | 0.14767 | 23.6 | 8.4 | 5.0429 | 14.5373 | 1.2122 | 1.0753 | 79.8 | 0 | 39.9 | 0 | 0 | 119.7 | 0 | 8.1491 | 0 | 0 | 106.01 | 106.01 | 20.8983 | 112.8102 | 223.8857 | 221.8286 | 440.6487 | 0 | 220.3244 | 440.6487 | 112.8102 | 106.01 | 10.0858 | 211.7428
| of the Summary tab that are consistant with the electrical design. | BN | -11 | 0
|  |  | total | 6365 | hours
10. | Manual psychrometric solutions appear to the left here, in column 15 (or
| column "O" if you prefer). There are 98 such manual selections in this bin tab; | [194 empty] | NO | selected | Resulting | Resulting | Ventilation | Gen | UPS | ITE
| common psychrometric results may be copied to other scenario tabs | 2°F wet bulb bins (for hours above 65°F dry bulb) | [7 empty] | Annual HW demand of cafeteria: |  |  |  | recovery | zone | temp | [5 empty] | Properties for generic ventilation air handlers. | [17 empty] | Information used for hourly inputs for ITE room IDEC units (shown with heat recovery input) | [27 empty] | Outputs for ITE room IDEC units with heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | HR export |  | Generator room | [19 empty] | Outputs for ITE room IDEC units without heat recovery. NOTE: most of the performance values are PER UNIT | [18 empty] | Without HR | UPS room variables | [13 empty] | Information used for hourly inputs for UPS room IDEC units | [27 empty] | Outputs for UPS units. NOTE: most of the performance values are PER UNIT | [18 empty] | Generator Room |  | Ventilation system |  | ITE and UPS cooling |  | Recovery | recovery | Mechanical | Mechanical | system | room | room | room
|  | bin | Average | bin | Outdoor |  |  |  | Psychrometric values for averaged points: | café avg | entering | kwh from | H2O heater | delta T | % desigm | Temp | AHU | Min | Max | min. | max. | control | heat | liquid | Cooling | DX split | room air | Project | Design | Design | Reset | Resulting | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | energy avoided | Room heat | engine block | Recovery | Recovery | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | error | ITE cooling | UPS room | Battery | Project | Design | Design | Design | Alternate | Room air | Design | Design | Unit | Number | Primary | bleed/evap | Supplemental | compressor | condenser | Design | Alternate | Design | Alternate | Design | Alternate | %design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Alternate | Design | Design | Alternate | Design | Alternate | Error | with | without | with | without | with | without | whatsoever | savings | Input | energy | HVAC | HVAC | cooling | cooling
11. | Review equipment selections, ensure they are consistent with your design | name | dry bulb | hours | wet bulb | dewpoint | %rh | moisture | enthalpy | 140 | temp | hot aisle | input energy | w/ HR | w/ HR | into ITE | SAT: | moisture | moisture | enthalpy | enthalpy | mode | energy | added | needed | kW input: | dew point | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | elsewhere | need, kWh | heat, kWh | Potential | Savings | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | annual kWh | temp | temp | elevation | ITE | SAT | SAT | delta T | dew point | S&R. ESP | Scav. ESP | size | of units | cooling | a ratio | cooling | efficiency | location | OA db | OA db | OA wb | OA wb | filtration | filtration | load | N+? | load rej. | load rej. | Total w/fan | Total w/fan | HX/IEC | HX/IEC | tons DX | tons DX | SA fan flow | SA fan flow | SA fan TSP | SA fan TSP | SA fan hp | SA fan hp | Scav. flow | Scav. flow | Scav. TSP | Scav. TSP | Scav. hp | Scav. hp | unit power | unit power | COP | COP | pPUE | pPUE | Evap rate | Evap rate | Bleed | Bleed | Cycles | H2O use | H2O use | WUE | WUE | indication | recovery | recovery | recovery | recovery | recovery | recovery | at all | kWh: | Power | incl. Recov | Component | component | component | component
| especially during the extreme climate data. Fill out the remaining user input | CA | 66 | 4 | 46 | 25 | 20.24% | 0.0028629 | 18.95 | 209564.5 | 55.4 | 176.4013 | 235.2018 | 19.9709 | 98.88% | 77.2 | 76.8 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 15.6255 | 3.6171 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.2 | 19.9709 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 66 | 75 | 46 | 4" MERV 8 | 4" MERV 8 | 98.88% | 3 | 168.5455 | 130.9519 | 52.7986 | 39.5713 | 45.5795 | 39.5713 | 7.2191 | 0 | 29380.5114 | 22794.5368 | 2.9531 | 1.8188 | 21.3291 | 10.2065 | 29406.0513 | 5068.7793 | 1.3885 | 0.050625 | 12.848 | 0.080746 | 34.4 | 9.8143 | 5.3959 | 14.1787 | 1.2041 | 1.0741 | 137.2 | 44.7 | 68.6 | 22.35 | 0 | 205.8 | 67.05 | 9.2434 | 5.7482 | 0 | 0 | 0 | 10.8 | 0 | 0 | 168.5455 | 131.1429 | 52.7818 | 39.626 | 45.5588 | 39.626 | 7.223 | 0 | 29339.2726 | 22795.7286 | 2.947 | 1.8191 | 21.2555 | 10.2086 | 29364.0101 | 5077.6045 | 1.3851 | 0.050791 | 12.7976 | 0.081151 | 34.3 | 9.8143 | 5.4109 | 14.1976 | 1.2035 | 1.0741 | 137 | 44.8 | 68.5 | 22.4 | 0 | 205.5 | 67.2 | 9.233 | 5.7565 | 0 | 196.2857 | 77.6 | 56.6 | 1259.52 | 111.24 | 65 | 56.6 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 66 | 75 | 46 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8525 | 34.6595 | 14.1507 | 34.6595 | 19.7018 | 0 | 18044.9953 | 18181.2054 | 2.1898 | 2.2073 | 9.7138 | 10.0196 | 18747.7842 | 16928.7927 | 0.80802 | 0.66334 | 4.7667 | 3.5335 | 23.6 | 12.3 | 5.049 | 9.9191 | 1.2119 | 1.1104 | 79.7 | 62.5 | 39.85 | 31.25 | 0 | 119.55 | 93.75 | 8.1341 | 9.5772 | 0 | 10.8 | 10.8 | 14.0873 | 65.7558 | 520.2857 | 520.2857 | 596.8416 | -4.6185e-14 | 149.2104 | 596.8416 | 65.7558 | 10.8 | 20.1958 | 500.0899
| (yellow cells in boxes), including how much cooling equipment to install, | CB | 67.7765 | 34 | 48 | 29.1 | 23.04% | 0.0034686 | 20.04 | 24654.6471 | 56 | 165.4232 | 220.5643 | 19.9734 | 98.9% | 77.6 | 77.2 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 13.266 | 3.0805 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 77.6 | 19.9734 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 67.7765 | 75 | 48 | 4" MERV 8 | 4" MERV 8 | 98.9% | 3 | 168.5455 | 130.9685 | 52.7972 | 39.5785 | 45.5777 | 39.5785 | 7.2194 | 0 | 29376.9265 | 22811.0145 | 2.9526 | 1.8208 | 21.3227 | 10.2177 | 29402.3978 | 5209.3971 | 1.3882 | 0.053316 | 12.8436 | 0.087396 | 34.3909 | 9.8357 | 5.3972 | 14.1506 | 1.2041 | 1.0743 | 137.2 | 45.2 | 68.6 | 22.6 | 0 | 205.8 | 67.8 | 9.2426 | 5.8166 | 0 | 0 | 0 | 88.78 | 0 | 0 | 168.5455 | 131.1429 | 52.7818 | 39.6286 | 45.5588 | 39.6286 | 7.223 | 0 | 29339.2726 | 22812.1028 | 2.947 | 1.8211 | 21.2555 | 10.2197 | 29364.0101 | 5217.8047 | 1.3851 | 0.053478 | 12.7976 | 0.087803 | 34.3 | 9.8357 | 5.4109 | 14.1678 | 1.2035 | 1.0743 | 137 | 45.3 | 68.5 | 22.65 | 0 | 205.5 | 67.95 | 9.233 | 5.8242 | 0 | 4012.9714 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 67.7765 | 75 | 48 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8525 | 34.7094 | 14.1507 | 34.7094 | 19.7018 | 0 | 18044.9953 | 18465.4612 | 2.1898 | 2.2555 | 9.7138 | 10.2385 | 18747.7842 | 9329.43 | 0.80802 | 0.20859 | 4.7667 | 0.61235 | 23.6 | 10.1 | 5.049 | 12.1329 | 1.2119 | 1.0904 | 79.7 | 47.5 | 39.85 | 23.75 | 0 | 119.55 | 71.25 | 8.1341 | 7.2672 | 0 | 88.78 | 88.78 | 105.8367 | 478.7015 | 4356.3714 | 4356.3714 | 4923.8529 | -2.9843e-13 | 144.8192 | 4923.8529 | 478.7015 | 88.78 | 171.6644 | 4184.707
| when. Review accuracy of generator room heating load, HW export schedule | CC | 67.3902 | 102 | 50 | 35.69 | 30.93% | 0.0046029 | 21.18 | 8218.2157 | 56.7 | 145.474 | 193.9654 | 19.9765 | 98.91% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 10.7983 | 2.0757 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.9765 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 67.3902 | 75 | 50 | 4" MERV 8 | 4" MERV 8 | 98.91% | 3 | 168.5455 | 130.9887 | 52.7954 | 39.5868 | 45.5756 | 39.5868 | 7.2198 | 0 | 29372.5703 | 22827.5144 | 2.9519 | 1.8228 | 21.3149 | 10.2291 | 29397.9476 | 5396.1328 | 1.3879 | 0.056657 | 12.8383 | 0.096202 | 34.3818 | 9.8571 | 5.3988 | 14.1203 | 1.204 | 1.0744 | 137.2 | 44.5 | 68.6 | 22.25 | 0 | 205.8 | 66.75 | 9.2414 | 5.7293 | 0 | 0 | 0 | 268.31 | 0 | 0 | 168.5455 | 131.1429 | 52.7818 | 39.6311 | 45.5588 | 39.6311 | 7.223 | 0 | 29339.2726 | 22828.477 | 2.947 | 1.823 | 21.2555 | 10.2308 | 29364.0101 | 5403.8899 | 1.3851 | 0.05681 | 12.7976 | 0.096601 | 34.3 | 9.8571 | 5.4109 | 14.1354 | 1.2035 | 1.0744 | 137 | 44.6 | 68.5 | 22.3 | 0 | 205.5 | 66.9 | 9.233 | 5.7359 | 0 | 12065.1429 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 67.3902 | 75 | 50 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8525 | 34.7094 | 14.1507 | 34.7094 | 19.7018 | 0 | 18044.9953 | 18465.4612 | 2.1898 | 2.2555 | 9.7138 | 10.2385 | 18747.7842 | 10537.88 | 0.80802 | 0.2628 | 4.7667 | 0.8714 | 23.6 | 10.3 | 5.049 | 11.867 | 1.2119 | 1.0924 | 79.7 | 47.4 | 39.85 | 23.7 | 0 | 119.55 | 71.1 | 8.1341 | 7.2544 | 0 | 268.31 | 268.31 | 273.8815 | 1184.3953 | 13115.7429 | 13115.7429 | 14568.4481 | 0 | 142.8279 | 14568.4481 | 1184.3953 | 268.31 | 514.9933 | 12600.7496
| if those heat recovery options are to be considered in your design. | CD | 69.132 | 222 | 52 | 41.82 | 37.04% | 0.0058643 | 22.98 | 3775.9369 | 57.4 | 126.8763 | 169.1684 | 19.98 | 98.93% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 6.9018 | 0.95827 | 0 | 0 | 46 | 1259.52 | 1854 | 78 | 78 | 19.98 | 46 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 69.132 | 75 | 52 | 4" MERV 8 | 4" MERV 8 | 98.93% | 3 | 168.5455 | 131.0118 | 52.7934 | 39.5935 | 45.573 | 39.5935 | 7.2203 | 0 | 29367.5768 | 22827.6586 | 2.9512 | 1.8228 | 21.306 | 10.2293 | 29392.858 | 5701.8727 | 1.3874 | 0.062754 | 12.8322 | 0.11259 | 34.3727 | 9.8714 | 5.4006 | 14.1022 | 1.2039 | 1.0745 | 137.1 | 45.2 | 68.55 | 22.6 | 0 | 205.65 | 67.8 | 9.2401 | 5.8132 | 0 | 0 | 0 | 564.635 | 0 | 0 | 168.5455 | 131.1429 | 52.7818 | 39.6311 | 45.5588 | 39.6311 | 7.223 | 0 | 29339.2726 | 22828.477 | 2.947 | 1.823 | 21.2555 | 10.2308 | 29364.0101 | 5708.9473 | 1.3851 | 0.0629 | 12.7976 | 0.11299 | 34.3 | 9.8714 | 5.4109 | 14.115 | 1.2035 | 1.0745 | 137 | 45.2 | 68.5 | 22.6 | 0 | 205.5 | 67.8 | 9.233 | 5.8189 | 0 | 26297.4857 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 69.132 | 75 | 52 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8525 | 34.7094 | 14.1507 | 34.7094 | 19.7018 | 0 | 18044.9953 | 18465.4612 | 2.1898 | 2.2555 | 9.7138 | 10.2385 | 18747.7842 | 12163.068 | 0.80802 | 0.34703 | 4.7667 | 1.3282 | 23.6 | 10.7 | 5.049 | 11.4255 | 1.2119 | 1.096 | 79.7 | 50.2 | 39.85 | 25.1 | 0 | 119.55 | 75.3 | 8.1341 | 7.6854 | 0 | 564.635 | 564.635 | 446.1637 | 1712.7946 | 28672.8857 | 28672.8857 | 30950.3153 | -1.0232e-12 | 139.4158 | 30950.3153 | 1712.7946 | 564.635 | 1120.8678 | 27552.0179
|  | CE | 71.0419 | 332 | 54 | 47.12 | 42.47% | 0.0071914 | 24.89 | 2524.8735 | 58 | 126.7233 | 168.9644 | 19.9806 | 98.93% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Heat-Hum | 2.7673 | 0 | 0 | 0 | 46.9 | 1259.52 | 1854 | 78 | 78 | 19.9806 | 46.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 71.0419 | 75 | 54 | 4" MERV 8 | 4" MERV 8 | 98.93% | 3 | 168.5455 | 131.0154 | 52.7924 | 39.5942 | 45.5721 | 39.5942 | 7.2202 | 0 | 29365.1134 | 22826.3846 | 2.9508 | 1.8227 | 21.3016 | 10.2279 | 29379.4028 | 6071.7371 | 1.3863 | 0.070515 | 12.816 | 0.13472 | 34.3545 | 9.8929 | 5.4033 | 14.0768 | 1.2038 | 1.0747 | 137.1 | 46 | 68.55 | 23 | 0 | 205.65 | 69 | 9.2373 | 5.9208 | 0 | 0 | 0 | 812.705 | 0 | 0 | 168.5455 | 131.1429 | 52.7812 | 39.6308 | 45.5583 | 39.6308 | 7.2229 | 0 | 29337.6056 | 22827.18 | 2.9468 | 1.8229 | 21.2525 | 10.2294 | 29351.3666 | 6079.1621 | 1.384 | 0.070677 | 12.7824 | 0.1352 | 34.2818 | 9.8929 | 5.4133 | 14.0891 | 1.2034 | 1.0747 | 137 | 46.1 | 68.5 | 23.05 | 0 | 205.5 | 69.15 | 9.2303 | 5.9265 | 0 | 39413.1429 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 46.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 71.0419 | 75 | 54 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8523 | 34.7091 | 14.1505 | 34.7091 | 19.7018 | 0 | 18043.9701 | 18464.4121 | 2.1896 | 2.2553 | 9.7125 | 10.2372 | 18739.8446 | 14373.7242 | 0.80745 | 0.48014 | 4.7613 | 2.1716 | 23.6 | 11.4 | 5.0502 | 10.6921 | 1.2119 | 1.1026 | 79.6 | 54.2 | 39.8 | 27.1 | 0 | 119.4 | 81.3 | 8.1312 | 8.2978 | 0 | 812.705 | 812.705 | 429.3117 | 1188.8084 | 43197.9429 | 43197.9429 | 45199.4562 | 3.4106e-12 | 136.1429 | 45199.4562 | 1188.8084 | 812.705 | 1676.6519 | 41521.291
12. | Commence itterations, using manufacturer's tool. I automated | CF | 73.161 | 351 | 56 | 49.75 | 43.62% | 0.0079457 | 26.23 | 2388.1994 | 58.7 | 123.4961 | 164.6615 | 19.9816 | 98.94% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 48.9 | 1259.52 | 1854 | 78 | 78 | 19.9816 | 48.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 73.161 | 75 | 56 | 4" MERV 8 | 4" MERV 8 | 98.94% | 3 | 168.5455 | 131.0223 | 52.7902 | 39.5954 | 45.5702 | 39.5954 | 7.22 | 0 | 29359.7446 | 22823.403 | 2.95 | 1.8224 | 21.292 | 10.2247 | 29348.3799 | 6525.9639 | 1.3838 | 0.080628 | 12.7788 | 0.16557 | 34.3091 | 9.9143 | 5.4095 | 14.0434 | 1.2036 | 1.0749 | 137 | 47.1 | 68.5 | 23.55 | 0 | 205.5 | 70.65 | 9.2304 | 6.0634 | 0 | 0 | 0 | 822.025 | 0 | 0 | 168.5455 | 131.1429 | 52.7796 | 39.63 | 45.5571 | 39.63 | 7.2225 | 0 | 29333.7186 | 22824.1556 | 2.9462 | 1.8225 | 21.2456 | 10.2261 | 29321.8958 | 6533.6129 | 1.3816 | 0.080807 | 12.7471 | 0.16613 | 34.2455 | 9.9143 | 5.419 | 14.0548 | 1.2032 | 1.0749 | 136.9 | 47.2 | 68.45 | 23.6 | 0 | 205.35 | 70.8 | 9.224 | 6.069 | 0 | 41758.9714 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 48.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 73.161 | 75 | 56 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8516 | 34.7083 | 14.15 | 34.7083 | 19.7016 | 0 | 18041.5794 | 18461.9657 | 2.1892 | 2.2549 | 9.7096 | 10.234 | 18721.3225 | 17486.0619 | 0.80613 | 0.70382 | 4.7489 | 3.8726 | 23.6 | 12.9 | 5.053 | 9.4668 | 1.2117 | 1.1159 | 79.6 | 60.1 | 39.8 | 30.05 | 0 | 119.4 | 90.15 | 8.1242 | 9.2046 | 0 | 822.025 | 822.025 | 285.5221 | 285.5221 | 46286.8714 | 46286.8714 | 47394.4186 | 9.0949e-13 | 135.0268 | 47394.4186 | 285.5221 | 822.025 | 1773.5888 | 44513.2826
| that process to make this example happen. This calculation | CG | 74.8974 | 418 | 58 | 52.59 | 45.72% | 0.00884 | 27.64 | 2005.4019 | 59.3 | 128.7063 | 171.6084 | 19.9813 | 98.94% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 53.1 | 1259.52 | 1854 | 78 | 78 | 19.9813 | 53.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 74.8974 | 75 | 58 | 4" MERV 8 | 4" MERV 8 | 98.94% | 3 | 168.5455 | 131.0201 | 52.7867 | 39.593 | 45.5676 | 39.593 | 7.2191 | 0 | 29351.1667 | 22816.3563 | 2.9488 | 1.8215 | 21.2767 | 10.2169 | 29280.2362 | 7092.9969 | 1.3781 | 0.094021 | 12.6973 | 0.20985 | 34.2273 | 9.9429 | 5.4226 | 13.9978 | 1.2031 | 1.0751 | 136.8 | 48.1 | 68.4 | 24.05 | 0 | 205.2 | 72.15 | 9.2157 | 6.1924 | 0 | 0 | 0 | 942.645 | 0 | 0 | 168.5455 | 131.1429 | 52.7759 | 39.6283 | 45.5543 | 39.6283 | 7.2216 | 0 | 29324.6793 | 22817.1222 | 2.9449 | 1.8217 | 21.2295 | 10.2183 | 29253.3388 | 7101.5312 | 1.3759 | 0.094236 | 12.6653 | 0.21058 | 34.1636 | 9.9429 | 5.4322 | 14.0092 | 1.2027 | 1.0751 | 136.7 | 48.2 | 68.35 | 24.1 | 0 | 205.05 | 72.3 | 9.2091 | 6.1983 | 0 | 49873.3714 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 53.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 74.8974 | 75 | 58 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.85 | 34.7072 | 14.1488 | 33.0023 | 19.7012 | 1.7049 | 18036.0198 | 18456.2766 | 2.1884 | 2.2545 | 9.7027 | 10.2291 | 18678.2567 | 17989.487 | 0.80307 | 0.74166 | 4.7199 | 4.1983 | 23.5 | 14.1 | 5.0595 | 8.6763 | 1.2115 | 1.1264 | 79.4 | 59.2 | 39.7 | 29.6 | 0 | 119.1 | 88.8 | 8.1082 | 9.0706 | 0 | 942.645 | 942.645 | 340.0235 | 340.0235 | 55767.1714 | 55767.1714 | 57049.8399 | -2.5011e-12 | 136.4829 | 57049.8399 | 340.0235 | 942.645 | 2114.8601 | 53652.3113
| does not reflect any actual data center. I completed this for | CH | 78.9962 | 338 | 60 | 53.8 | 41.73% | 0.0092486 | 29.09 | 2480.0533 | 60 | 133.9147 | 178.553 | 19.9815 | 98.94% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 53.1 | 1259.52 | 1854 | 78 | 78 | 19.9815 | 53.1 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 78.9962 | 75 | 60 | 4" MERV 8 | 4" MERV 8 | 98.94% | 3 | 168.5455 | 131.0218 | 52.7865 | 39.5935 | 45.5674 | 39.5935 | 7.2191 | 0 | 29350.8083 | 22816.3667 | 2.9487 | 1.8215 | 21.2761 | 10.217 | 29279.8728 | 7820.7155 | 1.3781 | 0.11317 | 12.6969 | 0.27849 | 34.2273 | 10.0071 | 5.4227 | 13.9144 | 1.2031 | 1.0755 | 136.8 | 51.4 | 68.4 | 25.7 | 0 | 205.2 | 77.1 | 9.2156 | 6.6095 | 0 | 0 | 0 | 692.965 | 0 | 0 | 168.5455 | 131.1429 | 52.7759 | 39.6283 | 45.5543 | 39.6283 | 7.2216 | 0 | 29324.6793 | 22817.1222 | 2.9449 | 1.8217 | 21.2295 | 10.2183 | 29253.3388 | 7830.1362 | 1.3759 | 0.11343 | 12.6653 | 0.27947 | 34.1636 | 10.0071 | 5.4322 | 13.9253 | 1.2027 | 1.0756 | 136.7 | 51.4 | 68.35 | 25.7 | 0 | 205.05 | 77.1 | 9.2091 | 6.6158 | 0 | 40588.9714 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 53.1 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 78.9962 | 75 | 60 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.85 | 34.7078 | 14.1488 | 30.9569 | 19.7012 | 3.7509 | 18036.0198 | 18456.2766 | 2.1884 | 2.2551 | 9.7027 | 10.2316 | 18678.2567 | 18109.0149 | 0.80307 | 0.75216 | 4.7199 | 4.286 | 23.5 | 15.2 | 5.0595 | 8.0193 | 1.2115 | 1.1368 | 79.4 | 62.1 | 39.7 | 31.05 | 0 | 119.1 | 93.15 | 8.1082 | 9.5129 | 0 | 692.965 | 692.965 | 274.9472 | 274.9472 | 45726.5714 | 45726.5714 | 46694.4837 | -1.2506e-12 | 138.1494 | 46694.4837 | 274.9472 | 692.965 | 1710.1022 | 44016.4692
| example purposes only. | CI | 83.3602 | 241 | 62 | 54.97 | 37.78% | 0.0096571 | 30.62 | 3478.249 | 60.7 | 145.7169 | 194.2892 | 19.981 | 98.93% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 55 | 1259.52 | 1854 | 78 | 78 | 19.981 | 55 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 83.3602 | 75 | 62 | 4" MERV 8 | 4" MERV 8 | 98.93% | 3 | 168.5455 | 131.018 | 52.785 | 39.5915 | 45.5665 | 39.5915 | 7.2186 | 0 | 29347.1098 | 22812.8345 | 2.9482 | 1.8211 | 21.2695 | 10.2131 | 29246.4664 | 8782.7993 | 1.3754 | 0.14104 | 12.6571 | 0.38979 | 34.1818 | 10.1 | 5.429 | 13.785 | 1.2028 | 1.0763 | 136.7 | 55.7 | 68.35 | 27.85 | 0 | 205.05 | 83.55 | 9.2084 | 7.1647 | 0 | 0 | 0 | 441.51 | 0 | 0 | 168.5455 | 131.1429 | 52.7741 | 39.6274 | 45.5529 | 39.6274 | 7.2212 | 0 | 29320.1699 | 22813.6134 | 2.9442 | 1.8213 | 21.2214 | 10.2145 | 29219.1377 | 8793.8462 | 1.3731 | 0.14139 | 12.6246 | 0.39123 | 34.1182 | 10.1 | 5.4388 | 13.7957 | 1.2024 | 1.0763 | 136.6 | 55.8 | 68.3 | 27.9 | 0 | 204.9 | 83.7 | 9.2017 | 7.172 | 0 | 29209.2 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 55 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 83.3602 | 75 | 62 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8493 | 34.7075 | 14.1482 | 28.861 | 19.701 | 5.8465 | 18033.2463 | 18453.4384 | 2.1879 | 2.2552 | 9.6993 | 10.2306 | 18656.771 | 18210.6502 | 0.80154 | 0.76192 | 4.7055 | 4.366 | 23.5 | 16.4 | 5.0627 | 7.4472 | 1.2113 | 1.1473 | 79.3 | 65.4 | 39.65 | 32.7 | 0 | 118.95 | 98.1 | 8.1001 | 10.0134 | 0 | 441.51 | 441.51 | 196.0423 | 196.0423 | 33161.6 | 33161.6 | 33799.1523 | 2.1032e-12 | 140.2454 | 33799.1523 | 196.0423 | 441.51 | 1220.1159 | 31941.4841
|  | CJ | 87.0126 | 190 | 64 | 56.69 | 35.78% | 0.010289 | 32.19 | 4411.8842 | 61.3 | 147.0146 | 196.0195 | 19.9816 | 98.94% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Vent-only | 0 | 0 | 0 | 0 | 55.9 | 1259.52 | 1854 | 78 | 78 | 19.9816 | 55.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 87.0126 | 75 | 64 | 4" MERV 8 | 4" MERV 8 | 98.94% | 3 | 168.5455 | 131.0222 | 52.7838 | 39.5923 | 45.5653 | 39.5923 | 7.2184 | 0 | 29343.9726 | 22811.1228 | 2.9477 | 1.8209 | 21.2639 | 10.2112 | 29228.5965 | 10116.5462 | 1.3739 | 0.18401 | 12.6358 | 0.58575 | 34.1636 | 10.2643 | 5.4326 | 13.5587 | 1.2027 | 1.0775 | 136.6 | 60.6 | 68.3 | 30.3 | 0 | 204.9 | 90.9 | 9.2045 | 7.7969 | 0 | 0 | 0 | 313.38 | 0 | 0 | 168.5455 | 131.1429 | 52.7732 | 39.6269 | 45.5522 | 39.6269 | 7.2209 | 0 | 29317.9365 | 22811.8757 | 2.9439 | 1.8211 | 21.2174 | 10.2126 | 29202.1889 | 10128.8626 | 1.3717 | 0.18444 | 12.6045 | 0.58785 | 34.1 | 10.2714 | 5.4421 | 13.568 | 1.2023 | 1.0775 | 136.5 | 60.7 | 68.25 | 30.35 | 0 | 204.75 | 91.05 | 9.198 | 7.8047 | 0 | 23418.8571 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 55.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 87.0126 | 75 | 64 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8489 | 34.7077 | 14.1479 | 26.7552 | 19.7009 | 7.9525 | 18031.8726 | 18452.0328 | 2.1877 | 2.2556 | 9.6977 | 10.2314 | 18646.1277 | 18325.9841 | 0.80078 | 0.77134 | 4.6984 | 4.4479 | 23.5 | 17.6 | 5.0643 | 6.948 | 1.2113 | 1.1579 | 79.3 | 67.2 | 39.65 | 33.6 | 0 | 118.95 | 100.8 | 8.0961 | 10.2841 | 0 | 313.38 | 313.38 | 154.5561 | 154.5561 | 26746.5714 | 26762.8571 | 27230.7933 | 1.08e-12 | 143.32 | 27230.7933 | 154.5561 | 313.38 | 962.2226 | 25800.6346
|  | CK | 91.5062 | 97 | 68 | 57.99 | 32.54% | 0.010791 | 33.84 | 8641.8351 | 62.6 | 147.2851 | 196.3801 | 19.9825 | 98.94% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 0.23718 | 0.18974 | 57.9 | 1259.52 | 1854 | 78 | 78 | 19.9825 | 57.9 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 91.5062 | 75 | 68 | 4" MERV 8 | 4" MERV 8 | 98.94% | 3 | 168.5455 | 131.0279 | 52.7811 | 39.5929 | 45.5631 | 39.5929 | 7.2181 | 0 | 29337.5372 | 22807.1149 | 2.9468 | 1.8205 | 21.2524 | 10.2068 | 29187.8965 | 14656.7502 | 1.3705 | 0.36822 | 12.5875 | 1.6982 | 34.1091 | 11.2286 | 5.4406 | 12.3952 | 1.2024 | 1.0848 | 136.5 | 72.4 | 68.25 | 36.2 | 0 | 204.75 | 108.6 | 9.1957 | 9.313 | 0 | 0 | 0 | 138.195 | 0 | 0 | 168.5455 | 131.1429 | 52.7711 | 39.6259 | 45.5506 | 39.6259 | 7.2204 | 0 | 29312.7395 | 22807.832 | 2.9431 | 1.8206 | 21.2082 | 10.2081 | 29162.7743 | 14672.7639 | 1.3685 | 0.36902 | 12.5577 | 1.7038 | 34.0455 | 11.2357 | 5.4497 | 12.4001 | 1.202 | 1.0848 | 136.4 | 72.5 | 68.2 | 36.25 | 0 | 204.6 | 108.75 | 9.1895 | 9.3219 | 0 | 13078.3714 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 57.9 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 91.5062 | 75 | 68 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.848 | 34.708 | 14.1473 | 22.5446 | 19.7007 | 12.1634 | 18028.6763 | 18448.762 | 2.1872 | 2.2562 | 9.6937 | 10.2324 | 18621.3689 | 18562.601 | 0.79903 | 0.78554 | 4.6819 | 4.5883 | 23.5 | 19.9 | 5.0681 | 6.1332 | 1.2111 | 1.1789 | 79.2 | 64.8 | 39.6 | 32.4 | 0 | 118.8 | 97.2 | 8.0869 | 9.9223 | 0 | 138.195 | 138.195 | 97.3099 | 97.3099 | 15000.3571 | 15008.6714 | 15244.1763 | -5.1159e-13 | 157.1565 | 15244.1763 | 97.3099 | 138.195 | 491.6027 | 14517.0687
|  | CL | 95.7912 | 34 | 70 | 59.52 | 30.12% | 0.011411 | 35.58 | 24654.6471 | 63.3 | 150.9584 | 201.2779 | 19.9828 | 98.94% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 1.3084 | 1.0468 | 59 | 1259.52 | 1854 | 78 | 78 | 19.9828 | 59 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 95.7912 | 75 | 70 | 4" MERV 8 | 4" MERV 8 | 98.94% | 3 | 168.5455 | 131.0303 | 52.7797 | 39.593 | 45.5619 | 39.593 | 7.2178 | 0 | 29334.0151 | 22804.7952 | 2.9463 | 1.8202 | 21.2461 | 10.2043 | 29164.5921 | 18933.7588 | 1.3686 | 0.60077 | 12.5599 | 3.5792 | 34.0818 | 12.8643 | 5.4452 | 10.8207 | 1.2022 | 1.0971 | 136.4 | 87.5 | 68.2 | 43.75 | 0 | 204.6 | 131.25 | 9.1906 | 11.257 | 0 | 0 | 0 | 41.155 | 0 | 0 | 168.5455 | 131.1429 | 52.7698 | 39.6253 | 45.5497 | 39.6253 | 7.2201 | 0 | 29309.7388 | 22805.4972 | 2.9427 | 1.8204 | 21.2028 | 10.2056 | 29140.0165 | 18952.9344 | 1.3666 | 0.602 | 12.5308 | 3.5902 | 34.0182 | 12.8714 | 5.4541 | 10.8215 | 1.2018 | 1.0972 | 136.3 | 87.6 | 68.15 | 43.8 | 0 | 204.45 | 131.4 | 9.1845 | 11.2674 | 0 | 5251.5429 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 59 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 95.7912 | 75 | 70 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8475 | 34.7081 | 14.1469 | 20.3188 | 19.7006 | 14.3892 | 18026.8307 | 18446.8734 | 2.1869 | 2.2565 | 9.6915 | 10.2328 | 18607.0699 | 18684.5396 | 0.79801 | 0.79649 | 4.6723 | 4.6828 | 23.5 | 21.1 | 5.0702 | 5.7704 | 1.211 | 1.1901 | 79.2 | 67.5 | 39.6 | 33.75 | 0 | 118.8 | 101.25 | 8.0816 | 10.3414 | 0 | 41.155 | 41.155 | 63.2471 | 63.2471 | 5966.0286 | 5968.9429 | 6073.345 | -2.7001e-13 | 178.6278 | 6073.345 | 63.2471 | 41.155 | 172.3877 | 5796.5551
|  | CM | 99.7083 | 24 | 72 | 61.34 | 28.52% | 0.012189 | 37.4 | 34927.4167 | 64 | 152.2309 | 202.9745 | 19.9834 | 98.95% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 2.429 | 1.9432 | 61 | 1259.52 | 1854 | 78 | 78 | 19.9834 | 61 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 99.7083 | 75 | 72 | 4" MERV 8 | 4" MERV 8 | 98.95% | 3 | 168.5455 | 131.0338 | 52.7771 | 39.5931 | 45.5597 | 38.3847 | 7.2173 | 1.2084 | 29327.526 | 22800.3613 | 2.9453 | 1.8199 | 21.2345 | 10.2003 | 29120.3546 | 22363.5714 | 1.365 | 0.82744 | 12.5076 | 5.8227 | 34.0273 | 15.45 | 5.4539 | 9.0117 | 1.2019 | 1.1166 | 136.3 | 100.1 | 68.15 | 50.05 | 0 | 204.45 | 150.15 | 9.181 | 12.8812 | 0 | 0 | 0 | 24.35 | 0 | 0 | 168.5455 | 131.1429 | 52.7675 | 39.6244 | 45.5479 | 38.4084 | 7.2196 | 1.2161 | 29304.0121 | 22801.0413 | 2.9419 | 1.82 | 21.1926 | 10.2016 | 29096.5823 | 22363.9803 | 1.363 | 0.82757 | 12.4795 | 5.8237 | 33.9636 | 15.45 | 5.4625 | 9.0159 | 1.2015 | 1.1167 | 136.2 | 100.2 | 68.1 | 50.1 | 0 | 204.3 | 150.3 | 9.1751 | 12.8842 | 0 | 4449.6 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 61 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 99.7083 | 75 | 72 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8465 | 34.7077 | 14.1461 | 18.0769 | 19.7003 | 16.6307 | 18023.3085 | 18443.2691 | 2.1864 | 2.2566 | 9.6871 | 10.231 | 18579.7865 | 18796.7559 | 0.79608 | 0.80611 | 4.6542 | 4.7679 | 23.5 | 22.4 | 5.0743 | 5.4485 | 1.2108 | 1.2013 | 79.1 | 69.4 | 39.55 | 34.7 | 0 | 118.65 | 104.1 | 8.0714 | 10.6285 | 0 | 24.35 | 24.35 | 66.1591 | 66.1591 | 4987.2 | 4987.2 | 5077.7091 | 3.908e-13 | 211.5712 | 5077.7091 | 66.1591 | 24.35 | 121.7843 | 4865.4157
|  | CN | 103.8875 | 8 | 74 | 63.09 | 26.77% | 0.012983 | 39.31 | 104782.25 | 64.6 | 153.1348 | 204.1798 | 19.9839 | 98.95% | 78 | 77.6 | 0.006946 | 0.013892 | 26.1684 | 33.4548 | Dehum | 0 | 0 | 3.6049 | 2.8839 | 63 | 1259.52 | 1854 | 78 | 78 | 19.9839 | 63 | 0.6 | 0 | PV-W30-PVT (19,000 - 32,000 CFM) | 11 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 106 | 103.8875 | 75 | 74 | 4" MERV 8 | 4" MERV 8 | 98.95% | 3 | 168.5455 | 131.0376 | 52.7743 | 39.5934 | 45.5575 | 35.6899 | 7.2168 | 3.9035 | 29320.6166 | 22795.6447 | 2.9443 | 1.8196 | 21.2222 | 10.1968 | 29073.2929 | 22498.0045 | 1.3611 | 0.83802 | 12.4521 | 5.9326 | 33.9636 | 16.9571 | 5.4631 | 8.2106 | 1.2015 | 1.128 | 136.1 | 103.2 | 68.05 | 51.6 | 0 | 204.15 | 154.8 | 9.1708 | 13.2685 | 0 | 0 | 0 | 6.445 | 0 | 0 | 168.5455 | 131.1429 | 52.7651 | 39.6236 | 45.5461 | 35.7128 | 7.219 | 3.9108 | 29297.92 | 22796.3011 | 2.941 | 1.8198 | 21.1818 | 10.198 | 29050.3778 | 22498.3967 | 1.3593 | 0.83814 | 12.4252 | 5.9336 | 33.9091 | 16.9571 | 5.4714 | 8.2146 | 1.2012 | 1.1281 | 136 | 103.2 | 68 | 51.6 | 0 | 204 | 154.8 | 9.1651 | 13.2715 | 0 | 1627.8857 | 86 | 65 | 1259.52 | 111.24 | 65 | 65 | 21 | 63 | 0.6 | 0 | PV-W25-PVT (16,000 - 25,000 CFM) | 1 | Indirect Evaporative Cooler (IEC) | 0.5 | Direct Expansion (DX) | 0.5 | Scavenger Exhaust | 110 | 103.8875 | 75 | 74 | 4" MERV 8 | 4" MERV 8 | 102.3% | 0 | 111.24 | 113.832 | 33.8454 | 34.7072 | 14.1454 | 15.801 | 19.7001 | 18.9062 | 18019.5616 | 18439.4349 | 2.1858 | 2.2566 | 9.6826 | 10.229 | 18550.7606 | 18910.6551 | 0.79403 | 0.81633 | 4.6349 | 4.8576 | 23.4 | 23.7 | 5.0787 | 5.1559 | 1.2106 | 1.2128 | 79 | 71.7 | 39.5 | 35.85 | 0 | 118.5 | 107.55 | 8.0606 | 10.9805 | 0 | 6.445 | 6.445 | 29.579 | 29.579 | 1817.4857 | 1817.4857 | 1853.5097 | -6.2172e-14 | 231.6887 | 1853.5097 | 29.579 | 6.445 | 40.6298 | 1776.8559
|  | CO |  | 0
|  |  | total | 2395 | hours | [194 empty] | Ventilation MLC component | Generator MLC component | UPS room MLC component | ITE room MLC component
[200 empty] | 0.0096715 | 0.0048398 | 0.0028053 | 0.068023

## Ventilation AHU Submittals
Assumptions: | Design airflow: | 1500
| Design Fan Static Pressure: | 3
| Direct evaporative (wet bulb approach) efficiency: | 80%
| Combined fan & motor efficiency: | 65%
| Design supply fan & motor temperature rise: | 1.6814
| Evap sump pump: | 250
| Filters | Merv 8
| DX efficiency during warm weather | 0.8
| fan motor power | 0.81345
Ventilation preheat is accomplished by electric resistance heat

## ITE AHU submittals
System Design Inputs
Project location | Quincy
Project elevation | 1260 |  | ft
Total power consumed by servers | 1872 |  | kW
Target supply air temperature (Max / Min) | 75 | 70 | Deg F
Design temperature rise through IT eqmt. | 20 |  | Deg F
Room air dew point | 45 |  | Deg F
Total Duct ESP (Process / Scavenger) | 0.6 | 0 | IN-WC
Unit size | PV-W30-PVT (19,000 - 32,000 CFM)
Number of units (N) | 11
Primary cooling type | Indirect Evaporative Cooler (IEC)
IEC sump water bleed rate* | 0.5 |  | x water evaporated
Supplemental Mechanical Cooling type | Direct Expansion (DX)
Compressor efficiency (est) | 0.5 |  | kW / ton
Condenser coil location | Scavenger Exhaust |  | #N/A
| Critical | Operating
Ambient DB | 110 | 110 | Deg F
Ambient WB | 73 | 73 | Deg F
Air filtration | 4" MERV 8 | 4" MERV 8
% Design load |  | 100% | 1872
Rate performance for N+(__) units operating |  | 4
ESP Adjustment Min Max |  | 100% | %
Estimated Unit Operating Performance
| Critical | Operating
ITE load rejected | 187.2 | 144 | kW
Total heat rejected (ITE load + fan heat) | 59.492 | 44.1958 | Refrigeration Tons
Heat rejected by IEC/HX | 48.247 | 35.9465 | Refrigeration Tons
Mech. cooling required | 11.245 | 8.2494 | Refrigeration Tons
Supply fan air volume | 32413.2142 | 24933.2417 | CFM
Supply fan calculated TSP | 3.4409 | 2.3191 | IN-WC
Supply fan motor brake horsepower | 27.4174 | 14.2144 | bhp
Scavenger fan air volume | 32515.1109 | 24990.7058 | CFM
Scavenger fan calculated TSP | 1.702 | 1.0326 | IN-WC
Scavenger fan motor brake horsepower | 17.4137 | 8.1196 | bhp
Estimated Unit Electrical Performance
| Critical | Operating
Unit operating power (+/- 5%) | 45.77 | 35.6545 | kW
Unit coefficient of performance | 4.5702 | 5.2392
Unit partial PUE | 1.2445 | 1.2095
Estimated Unit Water Performance
| Critical | Operating
Water evaporation rate | 170.3 | 154.1 | Gal/hr
Water bleed rate | 85.15 | 77.05 | Gal/hr
Cycles of concentration | 3
Total water consumption | 255.45 | 231.15 | Gal/hr
Unit WUE | 10.3324 | 15.4283 | L / kWh
(All Values are Per Unit)
(All Values are Per Unit)
(All Values are Per Unit)

## UPS AHU Submittals
System Design Inputs
Project location | Quincy, WA
Project elevation | 1260 |  | ft
Total power consumed by servers | 112.32 |  | kW
Target supply air temperature (Max / Min) | 55 | 65 | Deg F
Design temperature rise through IT eqmt. | 19 |  | Deg F
Room air dew point | 63 |  | Deg F
Total Duct ESP (Process / Scavenger) | 0.6 | 0 | IN-WC
Unit size | PV-W25-PVT (16,000 - 25,000 CFM)
Number of units (N) | 1
Primary cooling type | Indirect Evaporative Cooler (IEC)
IEC sump water bleed rate* | 0.5 |  | x water evaporated
Supplemental Mechanical Cooling type | Direct Expansion (DX)
Compressor efficiency (est) | 0.5 |  | kW / ton
Condenser coil location | Scavenger Exhaust
| Critical | Operating
Ambient DB | 110 |  | Deg F
Ambient WB | 75 |  | Deg F
Air filtration | 4" MERV 8
% Design load |  | 100% | 36.36
Rate performance for N+(__) units operating |  | 0
ESP Adjustment Min Max |  | 0% | %
Estimated Unit Operating Performance
| Critical | Operating
ITE load rejected | 112 |  | kW
Total heat rejected (ITE load + fan heat) | 34.5941 |  | Refrigeration Tons
Heat rejected by IEC/HX | 0.80063 |  | Refrigeration Tons
Mech. cooling required | 33.7935 |  | Refrigeration Tons
Supply fan air volume | 19611.4484 |  | CFM
Supply fan calculated TSP | 2.493 |  | IN-WC
Supply fan motor brake horsepower | 12.0191 |  | bhp
Scavenger fan air volume | 20839.2888 |  | CFM
Scavenger fan calculated TSP | 1.0942 |  | IN-WC
Scavenger fan motor brake horsepower | 7.1753 |  | bhp
Estimated Unit Electrical Performance
| Critical | Operating
Unit operating power (+/- 5%) | 35.1 |  | kW
Unit coefficient of performance | 3.4663
Unit partial PUE | 1.3133
Estimated Unit Water Performance
| Critical | Operating
Water evaporation rate | 73.2 | 5.7 | Gal/hr
Water bleed rate | 36.6 | 2.85 | Gal/hr
Cycles of concentration | 3
Total water consumption | 109.8 | 8.55 | Gal/hr
Unit WUE | 7.4248 | 1.727 | L / kWh
*Estimated value. Accurate value to be determined from customer-supplied water analysis.
(All Values are Per Unit)
(All Values are Per Unit)
(All Values are Per Unit)