## KADJ CALCULATION - IP
ASHRAE 2010 and 2013 Standard Kadj Calculations
IP Units
Item | Value | Units | Comment | A
ASHRAE 90.1 Standard | 2013 After 1/2015 | 2010 or 2013 | Select from the 2010 or 2013 ASHRAE 90.1 Standard | B
Full Load Capacity | 600 | Tons | Rating full load capacity
Compliance Path | A | A or B | Selected compliance path
Reference cell | 0
Standard Full Load Efficiency | 0.56 | kW/ton | From table 6.8.1c for ASHRAE 2010, and from table 6.8.1-3 for ASHRAE 2013 at standard fouling | 2010
Standard Part Load Efficiency IPLV) | 0.5 | kW/ton | From table 6.8.1c for ASHRAE 2010, and from table 6.8.1-3 for ASHRAE 2013 at standard fouling | 2013 Before 1/2015
LvgEvap | 42 | ºF | Cooler Leaving Water Temperature (Minimum of 36 F) | 2013 After 1/2015
LvgCond | 91.16 | ºF | Condenser Leaving Water Temperature (Maximum of 115 F)
LIFT | 49.16 | ºF | CEWT-CLWT
LIFT Check | 1
LIFT Check | OK | ─ | Insure that input values do not result in an Lift >=20 or <=80
A | 1.0228 | ─ | A=0.00000014592*(LIFT)^4-0.0000346496*(LIFT)^3+0.00314196*(LIFT)^2-0.147199*(LIFT)+3.9302
B | 0.997 | ─ | B=0.0015*LvgEvap+0.934
Kadj | 1.0197 | ─ | Off design condition adjustment for full load efficiency and IPLV
Adjusted Full Load Efficiency | 0.54918 | kW/ton | full load efficiency / Kadj
Adjusted Part Load Efficiency | 0.49034 | kW/ton | part load efficiency / Kadj
Input Items
Calculation Outputs | do not change

## KADJ CALCULATION - SI
ASHRAE 2010 Standard Kadj Calculations
SI Units
Item | Value | Units | Comment | A
ASHRAE 90.1 Standard | 2013 After 1/2015 | 2010 or 2013 | Select from the 2010 or 2013 ASHRAE 90.1 Standard | B
Full Load Capacity | 2110 | kW | Rating full load capacity
Compliance Path | A | A or B | Selected compliance path
Reference cell | 0
Full Load Efficiency | 6.286 | COP | From table 6.8.1c for ASHRAE 2010, and from table 6.8.1-3 for ASHRAE 2013 at standard fouling
Part Load Efficiency (IPLV) | 7.041 | COP | From table 6.8.1c for ASHRAE 2010, and from table 6.8.1-3 for ASHRAE 2013 at standard fouling | 2010
LvgEvap | 6 | ºC | Cooler Leaving Water Temperature (Minimum of 2.2 C) | 2013 Before 1/2015
LvgCond | 37 | ºC | Condenser Leaving Water Temperature (Maximum of 46.1 C) | 2013 After 1/2015
LIFT | 31 | ºK | CEWT-CLWT
LIFT Check | 1
LIFT Check | OK | ─ | Insure that input values do not result in an Lift >=20 or <=80
A | 0.89408 | ─ | 0.0000015318*LIFT^4-0.000202076*LIFT^3+0.0101800*LIFT^2-0.264958*LIFT+3.930196
B | 0.9982 | ─ | B=0.0027*LvgEvap+0.982
Kadj | 0.89247 | ─ | Off design condition adjustment for full load efficiency and IPLV
Adjusted Full Load Efficiency | 5.6101 | COP | full load efficiency * Kadj
Adjusted Part Load Efficiency | 6.2839 | COP | part load efficiency * Kadj
Input Items
Calculation Outputs | do not change

## 2010
Table 6.8.1c 2010 Centrifugal Minimum Efficiencies IP
Path | A |  | B
Capacity | Full | Part | Full | Part
<Tons | kW/ton | kW/ton | kW/ton | kW/ton
0 | 0.634 | 0.596 | 0.639 | 0.45
150 | 0.634 | 0.596 | 0.639 | 0.45
300 | 0.576 | 0.549 | 0.6 | 0.4
600 | 0.57 | 0.539 | 0.59 | 0.4
Table 6.8.1c 2010 Centrifugal Minimum Efficiencies SI
Path | A |  | B
Capacity | Full | Part | Full | Part
kW | COP | COP | COP | COP
0 | 5.547 | 5.901 | 5.504 | 7.815
528 | 5.547 | 5.901 | 5.504 | 7.815
1055 | 6.106 | 6.406 | 5.856 | 8.792
2110 | 6.17 | 6.525 | 5.961 | 8.792

## 2013 Before 1-2015
Table 6.8.1-3 2013 ASHRAE 90.1 Efficiency Requirements after 1/1/2015 IP
Path | A |  | B
Capacity | Full | Part | Full | Part
<Tons | kW/ton | kW/ton | kW/ton | kW/ton
0 | 0.634 | 0.596 | 0.639 | 0.45
150 | 0.634 | 0.596 | 0.639 | 0.45
300 | 0.576 | 0.549 | 0.6 | 0.4
400 | 0.576 | 0.549 | 0.6 | 0.4
600 | 0.57 | 0.539 | 0.59 | 0.4
Table 6.8.1-3 2013 ASHRAE 90.1 Efficiency Requirements after 1/1/2015 SI
Path | A |  | B
Capacity | Full | Part | Full | Part
kW | COP | COP | COP | COP
0 | 5.533 | 5.907 | 5.509 | 7.832
528 | 5.533 | 5.907 | 5.509 | 7.832
1055 | 6.112 | 6.412 | 5.867 | 8.801
1407 | 6.112 | 6.412 | 5.867 | 8.801
2110 | 6.176 | 6.531 | 5.967 | 8.801

## 2013 After 1-2015
Table 6.8.1-3 2013 ASHRAE 90.1 Efficiency Requirements after 1/1/2015 IP
Path | A |  | B
Capacity | Full | Part | Full | Part
<Tons | kW/ton | kW/ton | kW/ton | kW/ton
0 | 0.61 | 0.55 | 0.695 | 0.44
150 | 0.61 | 0.55 | 0.635 | 0.4
300 | 0.56 | 0.52 | 0.595 | 0.39
400 | 0.56 | 0.5 | 0.585 | 0.38
600 | 0.56 | 0.5 | 0.585 | 0.38
Table 6.8.1-3 2013 ASHRAE 90.1 Efficiency Requirements after 1/1/2015 SI
Path | A |  | B
Capacity | Full | Part | Full | Part
kW | COP | COP | COP | COP
0 | 5.571 | 6.401 | 5.065 | 8.001
528 | 5.571 | 6.401 | 5.544 | 8.801
1055 | 6.286 | 6.77 | 5.917 | 9.027
1407 | 6.286 | 7.041 | 6.018 | 9.264
2110 | 6.286 | 7.041 | 6.018 | 9.264