## Assumptions
90.1-2010 User's Manual
PRM assumptions are equal to ECB except where noted below.
Model Input Parameter | ECB Proposed Design | ECB Budget Design | PRM Proposed Design | PRM Budget Design | Comments
Exterior wall | U-0.133 (R-13 metal frame) | U-0.084 nonres (R-13+R3.8) U-0.064 res (R-13+R-7.5)
Below-grade wall | Uninsulated concrete | No requirement, unconditioned
Roof | U-0.048 (R-20 c.i.), reflectance 0.55 | U-0.048 (R-20 c.i.), reflectance 0.55
Floor | U-0.107 (R-6.3 c.i.) nonres mass | U-0.107 (R-6.3 c.i.) nonres mass |  | U-0.052, steel joist floor R-19
Window-to-gross wall ratio | 30.5% | Same as proposed (<40%) And S > W and S> E (per 5.5.4.5)
Fenestration U-factor | 1.22 | 0.65 Assembly (0.806 Glass)
Fenestration SHGC | Retail & residential 0.82 Office 0.61 | All 0.25
Fenestration Visual Light Transmittance | Retail & residential 0.88 Office 0.75 | na
Shading devices | Retail: 10 ft overhangs Office: 5 ft overhangs | None |  | No self shading
Interior lighting power density (W/sf) | Parking 0.15 Retail 1.1 Office 0.78 Apartments 1.65 Residential hallways 0.80 Overall 1.11 | Parking 0.25 Retail 1.40 Office 0.90 Apartments 1.65 Residential hallways 0.60 Overall 1.18
Daylighting controls | Dimming in perimeter office zones; 30 fc setpoint, 10% min light output at 19% power | None. No office space >250sf (NOT CLEAR WHETHER CREDIT ALLOWED, NOT EXPLICIT IN ECB)
Other lighting control credits | None | None |  |  | Could take credit in PRM for controls beyond mandatory, but motion sensors are required in small offices, restrooms, etc.
Exterior lighting power (kW) | None | None |  |  | Only building façade lighting included in PRM. Not explicit in ECB, but assume it's not included.
Receptable equipment power density (W/sf) | Retail: 0.25 W/sf Office: 1.5 W/sf Residential: 0.75 W/sf Hallways: 0.1 W/sf | Same as proposed
HVAC system type | Retail: fan coils Office: VAV reheat Residential: fan coils | Retail: System7, fan coils Office: System 2, VAV reheat Residential: System 7, fan coils |  | Retail: System 5, PVAVS Office: System 5, PVAVS Residential: System 1, PTAC with HW heat
Other HVAC system type | Garage ventilation, 2kW, 16 hr/day | Same as proposed
Fan supply volume | Retail: 15,800 cfm Office: 28,000 cfm Residential: 48,000 cfm | Same sizing ratio as proposed. Retail: 13,300 cfm Office: 22,800 cfm Residential: 33,700 cfm |  | Sizing ratio 1.15. Retail: 14,900 cfm Office: 22,800 cfm Residential: 33,900 cfm
Fan power | Fan coils: 0.25 W/cfm VAV system: 0.9 W/cfm | Same bhp/cfm as proposed. |  | PTAC: 0.3 W/cfm PVAVS: 0.0013*746/0.80 = 1.21 W/cfm
Fan control | Retail: constant speed fan coils. Office: Variable speed for VAV. Residential: Intermittent for fan coils. | Retail: constant speed fan coils. Office: Variable speed for VAV (>25hp). Residential: Intermittent for fan coils. | Constant volume for residential fan coils (to match PRM baseline fan control) | PTAC: constant volume PVAVS: fan curve per Table G3.1.3.15
Fan operating schedule | Retail fan coils: 8am-10pm Office VAV: 7am-6pm Residential fan coils: 24 hr, intermittent | Same as proposed
Zone min. airflow | 30% for VAV | 30% for VAV
Economizer control | Differential enthalpy for VAV | For >54kBtu/h, office system in this case. Fixed enthalpy 28 Btu/lb. Not required for residential systems <270 kBtu/h. |  | None. Not required for zone 3A per Table G3.1.2.6A
Supply air temperature control | Reset by warmest zone for VAV system. | Reset by warmest zone for VAV system.
Cooling capacity | 175 tons | Same sizing ratio as proposed. |  | 1.15 sizing ratio
Unitary equipment cooling efficiency | na | na |  | PTAC: EER 9.94 = EER 11.9 with fan power removed (EIR=0.288) PVAVS: EER 10.0 = EER 12.0 with fan power removed (EIR=0.286), for size range 240-760 kBtu/h
Chiller parameters | Water-cooled screw, 0.63 kW/ton (EIR=0.179), 175 tons | One screw chiller, 0.775 kW/ton (EIR=0.220) (for 75-150 tons), 139 tons (same sizing ratio as proposed). |  | None
Chilled water loop and pump parameters | 90 ft head, primary-only, variable speed pump, 50% min flow, 44F supply, 56F return. CHWS reset 44 at 80F/54 at 60F. | Pump power same as proposed. 44F supply, 56F return. CHWS reset. Primary-only. Variable speed pump (>5 hp). |  | None
Cooling tower parameters | 78F design wetbulb, 85F design CWS, 10F range, variable-speed fan, 70F setpoint, fan power 38.2 gpm/hp (EIR=0.0133) | 85F design, 10F range, two-speed fan, 70F setpoint, 38.2 gpm/hp. |  | None
Condenser water loop | 50 ft head, constant-flow | Pump power same as proposed. |  | None
Heating capacity | 1.2MBtu/h | Same sizing ratio as proposed. |  | 1.25 sizing ratio
Unitary equipment heating efficiency | na | na
Boiler parameters | Two boilers, 600 kBtu/h each, 80% efficiency | Two equally sized units. 325 kBtu/h each (same sizing ratio as proposed), 80% efficiency |  | Two equally sized units. 345kBtu/h each (1.25 sizing ratio), 80% efficiency
Hot water loop and pump parameters | 70 ft head, 180F supply, 130F return, reset by OA 180 at 20F/150 at 50F, variable speed pump | 180F supply, 130F return, reset by OA, pump power same as proposed, primary-only variable-flow, pump riding curve (<= 5hp) |  | 19 W/gpm. 60 ft at 60% combined efficiency. Constant-speed pump riding curve.
Demand control ventilation | None | None
Exhaust air heat recovery | None | Not required
Thermostat setpoints | 76/70 | Same as proposed.
DHW system | Gas, 80% efficiency | Gas, 80% efficiency
Utility rate (gas) | $0.49/therm, flat rate | Same as proposed.
Utility rate (electricity) | $0.067/kWh, flat rate | Same as proposed.