## 1. Cover & Guide
O&M Best Practice Checklist
LIGHTING & DAYLIGHTING
A Preventive Maintenance Checklist for Facility Operators
AUDIENCE
Facility maintenance staff, building operators, lighting / electrical technicians, chief building engineers, and facility managers responsible for the operation, inspection, and maintenance of interior and exterior lighting, daylighting, and lighting-controls systems. Designers, lighting professionals (IES), commissioning agents, and owners may also use this checklist as a reference.
MINDSET
Proactive vs. Reactive. Healthy buildings start with healthy systems and stay ready for reactive scenarios when they arise.
WHY
Lighting and daylighting directly affect occupant visual comfort, productivity, mood, circadian function, task performance, safety, and energy use. Poor lighting performance in operating buildings is most often not caused by poor but caused by operations and maintenance issues that are not corrected: dirty luminaires and fenestration, failed lamps and drivers, miscalibrated sensors, unmaintained controls, blocked or unmanaged shading, glare from uncontrolled daylight, and flicker from incompatible drivers/dimmers. Please note, that when the space use or layout changes and the light fixutres are not adjusted an no longer match how the space is used is also an issue that needs to be noted but falls to the Owner, Occupant and Designer doing the renovations to the space. Routine, documented preventive maintenance of lighting, controls, and daylight-management systems is one of the most cost-effective tools a facility team has to protect occupants, support energy compliance, and preserve the asset value of the building.
BACKGROUND & OBJECTIVES
The goals of this lighting preventive-maintenance checklist are to:
• | Provide facility staff with a practical schedule of monthly, quarterly, semi-annual, annual, and multi-year lighting and daylighting tasks aligned with ANSI/ASHRAE/IES Standard 90.1, IES recommended practices (RP / LP series), and applicable rating systems.
• | Maintain interior lighting, exterior lighting, daylighting apertures, and lighting controls so that the original design intent for illuminance, uniformity, color, and controllability is sustained through the life of the building.
• | Detect and correct common lighting failure modes — failed lamps/drivers, dirty luminaires and fenestration, sensor drift, broken controls, flicker, glare, lighting-load creep — before they become occupant complaints or code-compliance issues.
• | Reduce occupant exposure to visually uncomfortable or unsafe conditions: glare, flicker, low light levels for the task, poor uniformity, and inappropriate color quality.
• | Establish the proactive baseline that supports controls retro-commissioning, daylight-harvesting calibration, lighting-power-density (LPD) compliance, and emergency-lighting code requirements.
• | If applicable, align with voluntary rating systems including LEED v5 (Quality Views, Daylight, Interior Lighting), WELL Light, and IES design and verification recommendations.
• | Create a documented, auditable record (logs, dates, findings, corrective actions) supporting energy-code, life-safety, accessibility, and warranty/insurance requirements.
• | Promote a 'good is better than perfect' culture: complete the basic checks every cycle, capture observations, and iterate.
MEASURES OF SUCCESS
✓ | All lighting maintenance tasks completed at minimum required frequency.
✓ | Measured illuminance at representative task surfaces meets or exceeds IES recommendations for space type.
✓ | No lamps/luminaires out (interior or exterior) at the time of the monthly walk; failed lamps replaced or scheduled within a defined service window.
✓ | Lighting controls — occupancy / vacancy / daylight / time / dimming — operate as designed; sensors respond to programmed cues.
✓ | Daylight glare is controlled at occupied workstations and primary view positions; shading and electric light interlock correctly.
✓ | No occupant complaints related to flicker, glare, color quality, or controls intuitiveness outstanding > one cycle.
✓ | Emergency / egress lighting tested per code (typically monthly functional and annual 90-minute discharge); records retained.
✓ | Exterior and parking lighting operate per schedule / photocell; light trespass and uplight are within design intent and any local dark-sky requirements.
✓ | Lighting power density (interior and exterior) remains compliant with the building's applicable energy code as alterations occur.
✓ | Reduction in unscheduled lighting service calls and occupant complaints year over year.
HOW TO USE THIS CHECKLIST
Each frequency tab (Monthly, Quarterly, Semi-Annual, Annual, Multi-Year) is a stand-alone inspection sheet. For each task, record the date completed, the technician initials, and a status (Pass / Fail / N/A / Deferred). If a task fails or cannot be verified, log a corrective action in the 'Findings / Corrective Action' column and on the 'Observations Log' tab. Attach photometric readings, before/after photos, and controls test reports to the building's O&M manual. Increase frequency for any task that repeatedly fails, that operates in unusual conditions, or that supports critical occupancies. Tasks marked (Vd) require calibrated tools (illuminance meter, luminance meter, flicker meter) or a qualified technician.
PRIMARY SOURCES
– | ANSI/ASHRAE/IES Standard 90.1 — Energy Standard for Sites and Buildings (Sections on Interior & Exterior Lighting and Lighting Controls).
– | IES Lighting Handbook, 11th Edition — Reference & Application.
– | IES Recommended Practices (RP / LP series) for office, education, industrial, healthcare, retail, residential, exterior, and lighting controls applications.
– | IES TM-30 — Method for Evaluating Light Source Color Rendition.
– | IES TM-33 / IEEE Std 1789 / CIE TN 006 — Temporal Light Modulation (flicker) evaluation guidance.
– | ANSI/IES LP-16 — Documenting Control Intent Narrative; LP-1 Lighting Control Systems — Properties, Selection and Specification.
– | NFPA 70 (NEC), NFPA 101 Life Safety Code, and NFPA 110 — emergency, egress, and standby lighting test and recordkeeping.
– | USGBC LEED v5 — Indoor Environmental Quality credits (Daylight, Quality Views, Interior Lighting, Acoustic Performance — Lighting related strategies).
– | WELL Building Standard — Light concept (visual lighting design, electric light glare control, circadian lighting, daylight simulation).
– | Local energy code (e.g., IECC, IBC) and any adopted dark-sky / outdoor-lighting ordinance.
– | IES TM-15 - Technical Memorandum: Luminaire Classification System for Outdoor Luminaires

## 2. Monthly
Lighting Preventive Maintenance — Monthly Tasks
Walk-through inspections to be completed every 30 days. These tasks catch the most common and fastest-moving lighting failures: lamps out, dirty fixtures, controls drift, broken shading, glare complaints, and emergency-lighting issues. Most can be completed visually with a flashlight, the BAS / lighting-control front-end, and a handheld illuminance meter.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
INTERIOR LIGHTING — VISUAL & FUNCTIONAL
1 | Lamp-out / luminaire-out walk | Walk all occupied floors, lobbies, restrooms, stairwells, and back-of-house spaces. Identify and log lamps/luminaires that are off, flickering, or visibly dim. Issue replacement work orders. | V | IES Lighting Handbook 11th Ed. | Interior maintenance / group relamping
2 | Occupant lighting complaints | Review the lighting-complaint log for the past 30 days (too bright, too dark, glare, flicker, controls not intuitive, warm/cool light). Dispatch follow-up and document corrective action. | V | Facility complaint program; LEED v5 EQ | Occupant feedback / IEQ Management Plan
3 | Visual glare check at workstations | Quickly inspect representative workstations and screens for direct-source, reflected, or daylight glare. Confirm shades are operating; tag any luminaires with damaged louvers or missing baffles. | V | IES Lighting Handbook 11th Ed.; WELL Light | Visual comfort / glare control
LIGHTING CONTROLS — FUNCTIONAL SPOT CHECK
4 | Occupancy / vacancy sensors | Spot-check a sample of occupancy and vacancy sensors in offices, classrooms, conference rooms, restrooms, and storage areas. Confirm correct response to presence and absence; verify time-delay setting is reasonable. Also confirm that they are not being falsely triggered to be on due to poor sensor placement. | V | ASHRAE 90.1 §9; LEED v5 EQ | Automatic shut-off / occupant sensor controls
5 | Daylight sensors / harvesting | Spot-check daylight-harvesting zones near windows and skylights at multiple times of day. Confirm electric light dims/extinguishes when sufficient daylight is present. | V | ASHRAE 90.1 §9; IES LP-1 | Daylight responsive controls
6 | Time-clock / scheduled controls | Verify time-of-day schedules for offices, common areas, and exterior lighting are correct for the current season (sunrise/sunset offset, holiday calendar, after-hours overrides). | V | ASHRAE 90.1 §9 | Time-switch controls
7 | Switch & control-station labels | Verify switchplates, dimmer faceplates, and control-station screens are clean, legible, and labeled. Re-engrave or re-label faceplates where intent is unclear. | V | ANSI/IES LP-1; ANSI/IES LP-16 | Controls intuitiveness / user interface
DAYLIGHT, FENESTRATION & SHADING
8 | Window / skylight cleanliness | Inspect occupied-side window and skylight surfaces for dirt, smudges, or fogging that materially reduce daylight transmission. Schedule cleaning per facility program. | V | IES Lighting Handbook; LEED v5 EQ | Daylight / Quality Views
9 | Operable / automated shading | Verify manual blinds, roller shades, and any motorized/automated shading are operational, undamaged, and within reach of occupants. Confirm automated shades follow the intended schedule or sun-tracking response. | V | WELL Light; LEED v5 EQ | Glare control
EXTERIOR & EGRESS LIGHTING
10 | Exterior lamp-out walk | After dusk (or via photocell trend in BAS), walk/drive the site to identify dark exterior fixtures: parking, walkways, building façade, entrances, and loading docks. Note safety-critical outages first. | V | IES Lighting Handbook; local code | Exterior lighting — operation
11 | Exit / egress signs | Visually inspect all exit signs and egress lighting for illuminated face, damage, missing diffusers, and obstructions. Tag faulty units for repair. | V | NFPA 101 / IBC | Means of egress illumination
12 | Emergency lighting — monthly functional test | Perform monthly functional (30-second) test of all emergency lighting fixtures, exit signs, and egress unit equipment per NFPA 101 §7.9. Record date, location, and result; replace failed units. | Vd | NFPA 101 §7.9; NFPA 70 | Emergency illumination monthly test
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)

## 3. Quarterly
Lighting Preventive Maintenance — Quarterly Tasks
Quarterly tasks add closer attention to controls performance, photometric verification at representative locations, and the condition of drivers, dimmers, sensors, and exterior fixtures.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
PHOTOMETRIC SPOT-CHECKS
1 | Illuminance verification — interior | Using a calibrated illuminance meter, spot-check task surfaces in representative office, classroom, lab, kitchen, and circulation spaces. Compare to IES recommended illuminance for space type. Document deviation. | Vd | IES Lighting Handbook 11th Ed. | Illuminance recommendations by space type
2 | Uniformity check | At representative open-office or classroom areas, measure illuminance at multiple points along a grid to evaluate uniformity ratio (avg / min). Investigate when uniformity is materially worse than design intent. | Vd | IES Lighting Handbook 11th Ed. | Illuminance uniformity
3 | Color quality observation | Visually evaluate apparent color rendition and color temperature consistency among adjacent fixtures and between zones. Note inconsistent CCT or fading where lamps have aged unevenly. | V | IES TM-30; IES Lighting Handbook | Color rendition / consistency
4 | Flicker observation | Observe representative dimmed and non-dimmed luminaires for visible flicker, including under camera (smartphone) and when dimmed to low levels. Flag spaces where occupants report flicker, headaches, or visual fatigue. | V | IES TM-33; IEEE 1789 | Temporal Light Modulation (TLM)
CONTROLS — SENSORS & DIMMING
5 | Sensor cleaning & lens check | Clean lenses on photocells, occupancy sensors, and daylight sensors. Verify sensor placement is not blocked by furniture, fixtures, or stored materials. | V | ANSI/IES LP-1; ASHRAE 90.1 §9 | Sensor maintenance
6 | Dimming behavior | Cycle dimmers/controls in representative spaces full bright to lowest setting. Verify smooth dimming, no popcorning, no audible buzz, and consistent response across grouped fixtures. | V | ANSI/IES LP-1 | Dimming compatibility / commissioning
7 | Daylight-response calibration check | In one or two daylight-harvesting zones, override the daylight sensor and verify electric-light setpoint matches design intent. Calibrate or rezone if drift is observed. | Vd | ASHRAE 90.1 §9; IES LP-1 | Daylight-responsive control commissioning
8 | Networked controls / BAS integration | Pull a status report from the lighting control system or BAS: device offline counts, communication errors, and override flags. Issue work orders for offline gateways, panels, or fixtures. | V | ANSI/IES LP-16 | Control intent narrative / system health
EXTERIOR & SITE LIGHTING
9 | Exterior fixture cleaning | Clean lenses and reflectors on a representative sample of exterior wall packs, bollards, area / parking-lot, façade, and signage fixtures. Trim vegetation blocking light distribution. | V | IES Lighting Handbook 11th Ed. | Exterior maintenance
10 | Photocell / time-clock review | Verify exterior-lighting photocells turn on at dusk and off at dawn, and that astronomical time-clocks track seasonal change. Confirm dawn/dusk offsets and holiday schedules are correct. | V | ASHRAE 90.1 §9 | Exterior automatic control
11 | Light trespass / uplight observation | After dusk, walk the site perimeter; observe any light trespass onto adjacent properties or uplight beyond design. Adjust aiming or shielding where local code or dark-sky requirements apply. | V | IES TM-15; local ordinance | Outdoor lighting performance
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)

## 4. Semi-Annual
Lighting Preventive Maintenance — Semi-Annual Tasks
Semi-annual tasks (twice per year) include luminaire cleaning at scale, lens & reflector inspection, deeper controls health, glare/shading commissioning, and verification of emergency/egress equipment beyond the monthly functional test.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
LUMINAIRE CLEANING & INSPECTION
1 | Group cleaning — interior | Clean lenses, reflectors, and louvers on interior luminaires in occupied areas. Address dust accumulation that depresses delivered illuminance; replace damaged diffusers/louvers. | V | IES Lighting Handbook 11th Ed. | Group cleaning / maintained illuminance
2 | Lamp / driver / module inspection | Inspect representative luminaires for failed or end-of-life LED modules, drivers showing fault codes, audible buzz, discoloration, lens yellowing, or heat distress. Replace per OEM. | V | Manufacturer O&M | LED / driver service life
3 | Recessed fixture / housing integrity | Inspect recessed downlights and troffer housings for damaged trims, missing reflectors, broken hangers, or fire-rated penetration concerns above accessible ceilings. | V | NFPA 70; manufacturer O&M | Fixture installation integrity
CONTROLS — DEEPER VERIFICATION
4 | Control sequence review | Walk each major control zone through its programmed sequence (occupancy + daylight + schedule + override). Confirm sequence matches the Control Intent Narrative; document any drift or operator-modified overrides. | Vd | ANSI/IES LP-16 | Control intent narrative review
5 | Time-clock / schedule audit | Audit all time-clock schedules across panels and BAS for accuracy with current building hours, after-hours rentals, summer/winter time shifts, and holiday calendars. | V | ASHRAE 90.1 §9 | Scheduled lighting controls
6 | Sensor placement / coverage | Spot-check occupancy / daylight sensor coverage in changed-use rooms (new furniture, relocated workstations). Reposition or recommission as needed. | V | ANSI/IES LP-1 | Sensor placement / coverage
DAYLIGHTING & SHADING SYSTEMS
7 | Daylight aperture inspection | Inspect window film, glazing seals, light shelves, clerestories, and skylights for dirt, damage, fogged units, or failed seals reducing visible-light transmission. | V | LEED v5 EQ; WELL Light | Daylight maintenance
8 | Shading-system service | Service motorized shades and automated blind systems: limit-switch calibration, motor noise, fabric condition, and group response. Replace controllers showing fault codes. | V | Manufacturer O&M; WELL Light | Shading commissioning
9 | Glare zone review | Reassess perimeter workstations and conference rooms with the sun angle of the current season. Adjust shading rules or workstation orientation if glare is recurrent. | V | WELL Light; IES Lighting Handbook | Glare evaluation
EMERGENCY & LIFE-SAFETY LIGHTING
10 | Battery-pack functional test | Verify monthly functional-test records are current. Conduct supplemental functional checks of self-contained battery-pack egress fixtures and stairwell unit equipment. | Vd | NFPA 101 §7.9 | Emergency lighting periodic test
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)

## 5. Annual
Lighting Preventive Maintenance — Annual Tasks
Annual inspections — the deepest verification cycle short of full lighting re-commissioning. These tasks form the foundation of the building's Lighting Management Plan, the O&M Manual, and any LEED v5 / WELL documentation.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
ANNUAL PHOTOMETRIC ASSESSMENT
1 | Annual illuminance audit | Conduct a building-wide annual illuminance audit using a calibrated meter at representative task surfaces in each space type. Compare to IES recommendations and design intent; report deviations and remediation plan. | Vd | IES Lighting Handbook 11th Ed. | Annual illuminance verification
2 | Color quality audit (CCT, CRI/TM-30) | Verify color temperature and color rendition consistency across major space types. Where mixed-age lamps create visible CCT shift, schedule group replacement. | V | IES TM-30 | Color rendition consistency
3 | Flicker assessment | Conduct flicker observation across dimmable lighting zones using a TLM/flicker meter at representative settings. Document Pst LM and stroboscopic visibility measures (SVM) where measured. Address out-of-tolerance drivers/dimmer pairings. | Vd | IES TM-33; IEEE 1789 | Temporal Light Modulation
CONTROLS RETRO-COMMISSIONING (LIGHT-LEVEL)
4 | Sensor calibration audit | Calibrate or replace photocells, daylight sensors, and occupancy sensors as needed; document calibration date. Trend sensor data for drift across zones. | Vd | ANSI/IES LP-1; ASHRAE 90.1 §9 | Sensor calibration
5 | Controls health & sequence | Perform a controls retro-commissioning walk: each zone exercised through occupancy, daylight, schedule, override, and demand-response (where present). Compare to Control Intent Narrative. | Vd | ANSI/IES LP-16 | Controls retro-commissioning
6 | Demand response / load shedding (if applicable) | If the building participates in utility demand-response or load-shedding programs, exercise the load-shed sequence annually and verify graceful return to normal operation. | V | ANSI/IES LP-16; utility program | Demand response sequence
EXTERIOR LIGHTING — FULL INSPECTION
7 | Exterior cleaning & re-lamping | Clean all exterior fixtures (parking, walkways, façade, signage, security). Group-replace lamps/modules approaching end of life; document fixture-level service history. | V | IES Lighting Handbook | Exterior maintenance
8 | Photocell / time-clock validation | Validate astronomical time-clock and photocell operation across a full day cycle (or via trend). Verify dark-sky / curfew controls are operating where required. | Vd | ASHRAE 90.1 §9; local code | Exterior automatic control
9 | Light trespass / uplight survey | Conduct a perimeter survey at night and document any trespass, uplight, or glare exceeding local ordinance or design intent. Update site-lighting documentation. | V | IES TM-15; local ordinance | Outdoor lighting performance
EMERGENCY LIGHTING — ANNUAL DISCHARGE TEST
10 | Annual 90-minute discharge test | Conduct annual 90-minute (or duration-of-record) discharge test for all emergency egress fixtures, exit signs, and stairwell unit equipment per NFPA 101 §7.9. Replace batteries/fixtures that fail. Retain dated records. | Vd | NFPA 101 §7.9 | Emergency illumination annual test
LIGHTING-POWER & ENERGY COMPLIANCE
11 | Lighting Power Density (LPD) review | Review any tenant fit-outs, renovations, or fixture replacements completed during the year for continued compliance with the building's applicable energy code (ASHRAE 90.1 or local IECC) interior LPD allowances. | Vd | ASHRAE 90.1 §9; IECC | Interior lighting power
12 | Exterior lighting power review | Review exterior lighting power against the project's exterior lighting zone (LZ0–LZ4) allowance under ASHRAE 90.1 / IECC. | Vd | ASHRAE 90.1 §9; IECC | Exterior lighting power
13 | As-built lighting drawings update | Update the building's lighting / control drawings, fixture schedules, and Control Intent Narrative to reflect any changes from the past year. | V | ANSI/IES LP-16 | As-built documentation
DOCUMENTATION & OCCUPANT FEEDBACK
14 | Occupant lighting survey (optional) | Distribute or review the occupant satisfaction / visual-comfort survey where program is in place. Trend results and address recurring complaints (glare, color, controls intuitiveness, flicker). | V | LEED v5 EQ; WELL Light | Occupant survey
15 | Lighting Management Plan refresh | Update the building's written Lighting Management Plan: maintenance schedules, group-relamping plan, controls intent, sensor calibration log, complaint procedures, and emergency-lighting records. | V | ANSI/IES LP-16 | Lighting Management Plan
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)

## 6. Multi-Year & As-Required
Lighting Preventive Maintenance — Multi-Year (2–5 Years) & As-Required
Multi-year tasks include the group-relamping cycle, full re-commissioning of lighting controls, deep daylight modeling updates, and the event-driven actions (renovation, change-of-use, after a complaint cluster). Schedule these into a rolling 3-5 year plan in the O&M manual.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
EVERY 2–3 YEARS
1 | Controls re-commissioning | Engage the lighting controls integrator or commissioning agent to re-commission lighting controls: sequence verification, sensor calibration, network health, dimming-curve verification, and Control Intent Narrative update. | Vd | ANSI/IES LP-16 | Controls re-commissioning
2 | Lamp / module group replacement | Implement group relamping/module replacement at the design service life (LM-80 / TM-21 projections, typically 3-5 years for high-runtime LED applications). Document service date and projected next interval. | V | IES TM-21 / LM-80 | Group relamping
EVERY 3–5 YEARS
3 | Daylight performance re-evaluation | Re-evaluate daylight performance (sDA, ASE, or annual daylight glare probability) after any major façade alterations, shading changes, or interior reconfigurations. Re-train daylight-harvesting setpoints accordingly. | Vd | LEED v5 EQ; IES LM-83 | Annual daylight metrics
4 | Flicker / dimming compatibility re-check | Where drivers, dimmers, or controls have been replaced, perform a flicker and dimming-compatibility re-check; update the approved-equipment list and Control Intent Narrative. | Vd | IES TM-33; IEEE 1789 | Flicker / dimming compatibility
AS REQUIRED (event-driven)
5 | Renovation / tenant fit-out | After any tenant fit-out, renovation, or change of space type, re-verify illuminance, glare, LPD compliance, controls integration, and emergency-lighting coverage in the affected area. | Vd | ASHRAE 90.1 §9; IES; NFPA 101 | Renovation / change-of-use
6 | Complaint cluster / IEQ investigation | When complaints cluster around a space (glare, flicker, dimness, controls), conduct an investigation including illuminance, luminance, and flicker measurement; modify shading, controls, or fixtures and document outcome. | Vd | WELL Light; IES Lighting Handbook | Complaint response
7 | Energy-audit / retrofit study | Conduct an energy-audit / lighting-retrofit study (ASHRAE Level I/II) when fixtures approach end of life, when energy code is updated, or when the lighting represents an outsized share of operating cost. | Vd | ASHRAE 211 / ASHRAE 90.1 | Energy audit
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)

## 7. Emergency & Egress
Lighting Preventive Maintenance — Emergency & Egress Lighting
Dedicated tab for life-safety lighting: emergency egress lighting, exit signs, stairwell unit equipment, and the corresponding inspection, functional, and annual discharge testing required by NFPA 101 / NFPA 70 / NFPA 110. Inspection frequencies below are minimum code requirements; increase as required by AHJ.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
MONTHLY
1 | Monthly 30-second functional test | Test every emergency fixture, exit sign, and stairwell unit equipment for 30 seconds. Verify illuminated condition and proper operation under simulated power loss. | Vd | NFPA 101 §7.9.3 | Monthly functional test
2 | Battery / charging indicator | Inspect indicator LEDs on self-contained units; replace units with fault indicators or that fail the 30-second test. | V | NFPA 101 §7.9.3 | Battery condition
ANNUAL
3 | Annual 90-minute discharge test | Disconnect normal power and verify each emergency unit operates for the required 90 minutes (or design duration). Document start time, end time, location, and pass/fail; replace failed units immediately. | Vd | NFPA 101 §7.9.3 | Annual 90-minute test
4 | Exit sign condition | Verify all exit signs are illuminated, undamaged, and visible from all egress paths per NFPA 101 / IBC. | V | NFPA 101 §7.10 | Exit signs
5 | Standby / generator-served lighting | Where egress / standby lighting is served by an emergency generator (NFPA 110), coordinate with monthly/annual generator testing; verify ATS transfer and runtime per NFPA 110 §8.4. | Vd | NFPA 110 §8.4 | Emergency power testing
RECORDKEEPING
6 | Test log retention | Maintain a written or electronic test log of all functional and discharge tests for the time period required by the AHJ (typically the life of the building or per local fire code). | V | NFPA 101 §7.9.3.1.3 | Test log retention
7 | AHJ inspection support | Support periodic fire-marshal / AHJ inspections by providing the test log, layout drawings, and corrective-action records. | V | Local fire code | AHJ coordination
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)
Standards:
NFPA 101 = Life Safety Code ¦ NFPA 70 = National Electrical Code (Article 700/701/702) ¦ NFPA 110 = Emergency and Standby Power Systems ¦ AHJ = Authority Having Jurisdiction

## 8. Observations Log
Additional Lighting Observations & Concerns Log
Use this log to record any lighting-related observation, concern, or occupant complaint that arises between scheduled inspections, or to document follow-up on items flagged as 'Fail' or 'Deferred' on the frequency tabs. Common observations: too bright / too dark / glare / inconsistent uniformity / controls not intuitive / automated controls not working / flicker / solar heat at windows. Each entry should be linkable back to its source standard.
Date | Time | Location / Room | Equipment / System | Observation / Concern | Level of Concern | Tested? | Measurement / Reading | Source / Reference | Action Taken / Next Steps | Performed By | Status

## 9. Common Observations
Common Negative Observations | Technical Description | Metric(s) | Considerations | Next Steps / Remediation
Space is uncomfortably bright | More illuminance than needed for space type | Illuminance Recommendations (FC or lux), illuminance meter | Materials and finishes (colors and reflectance values), room size, tasks performed | Consider dimming options and recommissioning, changes to task surfaces and proximity to lighting
Space is too dark | Not enough illuminance to complete tasks | Illuminance Recommendations (FC or lux), illuminance meter | Materials and finishes (colors and reflectance values), room size, tasks performed | Consider dimming levels, additional opportunities for supplemental lighting later
Visually uncomfortable / glare | Contrast is too high (luminance) against background finishes | Luminance meter (cd/m²) | Materials and finishes (contrast, specularity, etc.), tasks performed, sight lines, shading (daylight contribution) | Consider dimming levels,
Light is inconsistent / lacks uniformity | Lack of uniformity is creating undesirable visual effects | Illuminance Recommendations (FC or lux) for uniformity, illuminance meter | Design intent for accents & highlights, materials and finishes, poor maintenance
Controls are not intuitive | Controls switch plate isn't clear, lacks description of on/off/dimming | Refer to best practices including specification guidelines and recommendations (IES RP/LPs) |  | Engrave switch plates or add labels, educate users, consider automation options
Automated controls are not working | Daylight, occupancy, and/or vacancy sensors aren't responding to cues (people, daylight). Timed events aren't deploying. | ASHRAE 90.1, illuminance meter | Commissioning may have not been completed correctly, sensors might be blocked or bad, additional programming may be needed | Integrator or controls manufacturer for site visit, commissioning review with owners
Flicker | Temporal Lighting Modulation, Visually perceivable flash/murmur/fluctuation in lighting emission | SVM (stroboscopic visibility measure), Hz (frequency), flicker index, Pst LM (short-term flicker severity) | Driver design, dimming system expectations (light may be dimmed too low), AC power ripple, incompatible controls, PWM dimming, or poor power quality | TLM meter of space, compatibility check (reverse lookup of compatibility of luminaire and controls system)
Space is warm | Solar heat gain is perceivable by occupants in close proximity to windows/fenestration |  |  | HVAC trends in mitigation, installing shading systems

## 10. Standards Crosswalk
Lighting Source & Standards Crosswalk
This crosswalk maps the requirements of ANSI/ASHRAE/IES Standard 90.1, IES Lighting Handbook and RP / LP / TM documents, NFPA life-safety codes, and LEED v5 / WELL Light credits to the tabs in this workbook so a reviewer can confirm coverage.
Standard / Rating System | Section / Credit | Title / Topic | Frequency | Where in this Workbook | Review Notes / Basis | Public Reference URL
ANSI/ASHRAE/IES STANDARD 90.1 — INTERIOR & EXTERIOR LIGHTING
ASHRAE 90.1 | §9.4 | Interior lighting power (LPD) | Annual / Event-driven | Annual / Multi-Year | Verify continued compliance after fit-outs and renovations. | https://www.ashrae.org/technical-resources/standards-and-guidelines/standards-addenda/standard-90-1-2022-energy-standard-for-sites-and-buildings
ASHRAE 90.1 | §9.4 Mandatory | Automatic shut-off / occupant sensor controls | Monthly / Quarterly | Monthly / Quarterly | Map to occupancy / vacancy sensor spot-checks and Quarterly cleaning. | https://www.ashrae.org/technical-resources/standards-and-guidelines/standards-addenda/standard-90-1-2022-energy-standard-for-sites-and-buildings
ASHRAE 90.1 | §9.4 Mandatory | Daylight-responsive controls | Monthly / Quarterly / Annual | Monthly / Quarterly / Annual | Map to daylight harvesting spot-checks and annual calibration audit. | https://www.ashrae.org/technical-resources/standards-and-guidelines/standards-addenda/standard-90-1-2022-energy-standard-for-sites-and-buildings
ASHRAE 90.1 | §9.4 Mandatory | Scheduled / time-of-day controls | Monthly / Semi-Annual | Monthly / Semi-Annual | Map to time-clock review at the start of each season. | https://www.ashrae.org/technical-resources/standards-and-guidelines/standards-addenda/standard-90-1-2022-energy-standard-for-sites-and-buildings
ASHRAE 90.1 | §9.4 Exterior | Exterior lighting controls — astronomical time / photocell / curfew | Quarterly / Annual | Quarterly / Annual | Map to exterior controls review and dark-sky / curfew checks. | https://www.ashrae.org/technical-resources/standards-and-guidelines/standards-addenda/standard-90-1-2022-energy-standard-for-sites-and-buildings
ASHRAE 90.1 | §9.4 Exterior | Exterior lighting power (LZ0-LZ4) | Annual / Event-driven | Annual / Multi-Year | Map to annual exterior LPD review. | https://www.ashrae.org/technical-resources/standards-and-guidelines/standards-addenda/standard-90-1-2022-energy-standard-for-sites-and-buildings
IES — LIGHTING HANDBOOK / RECOMMENDED PRACTICES / TECHNICAL MEMORANDA
IES Lighting Handbook (11th Ed.) | Application chapters | Recommended illuminance / uniformity / glare by space type | Quarterly / Annual | Quarterly / Annual | Map to photometric spot-checks and annual illuminance audit. | https://www.ies.org/standards/
IES TM-30 | — | Method for Evaluating Light Source Color Rendition | Annual | Annual | Map to annual color-quality audit. | https://www.ies.org/standards/
IES TM-33 / IEEE 1789 / CIE TN 006 | — | Temporal Light Modulation (flicker) evaluation | Quarterly / Annual | Quarterly / Annual / Multi-Year | Map to flicker observation and annual TLM measurement. | https://www.ies.org/standards/
IES TM-21 / LM-80 | — | LED light source / module life projection | Multi-year | Multi-Year & As-Required | Used to set group-relamping interval. | https://www.ies.org/standards/
ANSI/IES LP-1 | — | Lighting Control Systems — Properties, Selection and Specification | Monthly / Quarterly / Semi-Annual | Monthly / Quarterly / Semi-Annual | Map to control-station review, sensor placement, and dimming behavior tasks. | https://www.ies.org/standards/
ANSI/IES LP-16 | — | Documenting Control Intent Narrative | Semi-Annual / Annual / Multi-year | Semi-Annual / Annual / Multi-Year | Map to control sequence reviews, retro-commissioning, and as-built updates. | https://www.ies.org/standards/
IES TM-15 | — | Outdoor Site-Lighting Performance (BUG ratings, uplight, light trespass) | Quarterly / Annual | Quarterly / Annual | Map to exterior light-trespass / uplight survey. | https://www.ies.org/standards/
NFPA — EMERGENCY, EGRESS, AND STANDBY LIGHTING
NFPA 101 | §7.9 / §7.10 | Means of egress illumination and exit signs | Monthly / Annual | Monthly / Annual / Emergency & Egress tab | Map to monthly functional test, annual 90-minute discharge test, and exit-sign condition checks. | https://www.nfpa.org/codes-and-standards/all-codes-and-standards/list-of-codes-and-standards/detail?code=101
NFPA 70 (NEC) | Article 700 / 701 / 702 | Emergency, legally required standby, and optional standby systems | Monthly / Annual | Monthly / Annual / Emergency & Egress tab | Cross-references for branch-circuit and equipment requirements for emergency lighting. | https://www.nfpa.org/codes-and-standards/all-codes-and-standards/list-of-codes-and-standards/detail?code=70
NFPA 110 | §8.4 | Emergency and Standby Power Systems — testing and maintenance | Monthly / Annual | Emergency & Egress tab | Applies where egress / standby lighting is served by an on-site generator. | https://www.nfpa.org/codes-and-standards/all-codes-and-standards/list-of-codes-and-standards/detail?code=110
USGBC LEED v5 — INDOOR ENVIRONMENTAL QUALITY
LEED v5 EQ | Daylight | Daylight credits (sDA, ASE) and continued performance | Annual / Multi-year | Annual / Multi-Year | Map to annual daylight performance check after façade or shading changes. | https://www.usgbc.org/leed/v5
LEED v5 EQ | Quality Views | Continued occupant access to quality views | Annual | Annual | Map to annual occupant survey and shading reviews. | https://www.usgbc.org/leed/v5
LEED v5 EQ | Interior Lighting | Interior lighting quality and controllability | Quarterly / Annual | Quarterly / Annual | Map to controls review, dimming behavior, and occupant feedback. | https://www.usgbc.org/leed/v5
WELL BUILDING STANDARD — LIGHT CONCEPT
WELL Light | Visual Lighting Design | Illuminance levels and visual comfort | Quarterly / Annual | Quarterly / Annual | Map to illuminance verification and occupant survey. | https://standard.wellcertified.com/light
WELL Light | Electric Light Glare Control | Glare control performance | Monthly / Quarterly | Monthly / Quarterly | Map to glare observation walks and luminance follow-up. | https://standard.wellcertified.com/light
WELL Light | Circadian Lighting Design / Daylight Modeling | Circadian and daylight strategies | Annual / Multi-year | Annual / Multi-Year | Map to annual daylight reassessment and circadian setpoint review. | https://standard.wellcertified.com/light
OCCUPANT-FACING — COMMON NEGATIVE OBSERVATIONS (SOURCE: IEQ Technical Guide)
IEQ Source | Common Observation | Space is uncomfortably bright — more illuminance than needed for space type | As observed | Observations Log / Quarterly | Consider dimming, recommissioning, changes to task surfaces and proximity to lighting. | https://www.ies.org/standards/
IEQ Source | Common Observation | Space is too dark — not enough illuminance to complete tasks | As observed | Observations Log / Quarterly | Consider dimming levels, additional supplemental task lighting. | https://www.ies.org/standards/
IEQ Source | Common Observation | Visually uncomfortable / glare — contrast too high vs. background finishes | As observed | Observations Log / Quarterly | Consider dimming levels, shading, and material/finish review (contrast, specularity). | https://www.ies.org/standards/
IEQ Source | Common Observation | Light is inconsistent / lacks uniformity | As observed | Quarterly / Annual | Check design intent for accents/highlights, materials and finishes, maintenance. | https://www.ies.org/standards/
IEQ Source | Common Observation | Controls are not intuitive — switchplate unclear, lacks description of on/off/dimming | As observed | Monthly / Semi-Annual | Engrave / re-label switchplates, educate users, consider automation. | https://www.ies.org/standards/
IEQ Source | Common Observation | Automated controls are not working — daylight, occupancy, vacancy sensors not responding; timed events not deploying | As observed | Monthly / Quarterly / Annual | Integrator or controls manufacturer for site visit; commissioning review with owners. | https://www.ies.org/standards/
IEQ Source | Common Observation | Flicker — perceivable flash / fluctuation in emission | As observed | Quarterly / Annual / Multi-Year | TLM meter assessment; compatibility check (reverse lookup of luminaire ↔ controls). | https://www.ies.org/standards/
IEQ Source | Common Observation | Space is warm — solar heat gain perceivable near windows / fenestration | As observed | Monthly / Semi-Annual | Coordinate with HVAC trends, install shading systems; cross-reference Thermal Comfort checklist. | https://www.ies.org/standards/