## 1. Cover & Guide
O&M Best Practice Checklist
INDOOR AIR QUALITY (IAQ)
A Preventive Maintenance Checklist for Facility Operators
AUDIENCE
Facility maintenance staff, building operators, and chief building engineers responsible for the operation, inspection, verification, and maintenance of building HVAC and ventilation systems. Designers, industrial hygienists, commissioning agents, and owners may also use this checklist as a reference.
MINDSET
Proactive vs. Reactive. Healthy buildings start with healthy systems and stay ready for reactive scenarios when they arise.
WHY
Indoor air quality (IAQ) directly affects occupant health, productivity, cognitive function, attendance, and long-term wellbeing. Poor IAQ has been associated with increased respiratory illness, asthma, allergies, infectious disease transmission, sick-building symptoms, and reduced learning and work performance. Most IAQ problems in operating buildings are not design failures, they are operations and maintenance failures: clogged or bypassed filters, fouled coils, blocked condensate drains, insufficient outdoor air, damaged ductwork, uncalibrated sensors, microbial growth, unmanaged moisture, and cleaning using chemicals. Routine, documented preventive maintenance of the ventilation system is the single most cost-effective tool a facility team has to protect occupants and the asset value of the building.
BACKGROUND & OBJECTIVES
The goals of this IAQ preventive-maintenance checklist are to:
• | Provide facility staff with a single, practical schedule of monthly, quarterly, semi-annual, annual, and multi-year IAQ inspection tasks aligned with ANSI/ASHRAE Standard 62.1-2025 Section 8 (Operations & Maintenance) and ANSI/ASHRAE/ACCA Standard 180.
• | Maintain ventilation and air-cleaning systems so that the design intent for outdoor air, filtration, exhaust, and pressurization is sustained throughout the life of the building.
• | Detect and correct common IAQ failure modes such as moisture intrusion, biological growth, filter bypass, blocked drains, damper failures, sensor drift, before they become occupant complaints, illness, or property damage.
• | Reduce occupant exposure to airborne particulate matter (PM2.5 / PM10), VOCs, formaldehyde, mold, dust, allergens, combustion byproducts (CO, NO2), and infectious aerosols.
• | Establish the proactive baseline that supports event-driven ASHRAE consensus documents — Standard 241 (Control of Infectious Aerosols) and Guideline 44 (Protecting Building Occupants from Smoke During Wildfire and Prescribed Burn Events).
• | If applicable, align with voluntary rating systems including LEED v5 (Enhanced IAQ Strategies, IAQ Performance, Source Control, Healthy Cleaning).
• | Create a documented, auditable record (logs, dates, findings, corrective actions) that supports building-water-quality plans, ASHRAE Standard 188 / Guideline 12, infectious-disease and smoke readiness, and warranty/insurance requirements.
• | Promote a 'good is better than perfect' culture: complete the basic checks every cycle, capture observations, and iterate.
MEASURES OF SUCCESS
✓ | All ventilation tasks in ASHRAE 62.1 Table 8-1 completed at minimum required frequency
✓ | Designed outdoor airflow rates verified annually and within ±10% of design
✓ | Filters installed, sealed, and replaced on schedule (or by ΔP)
✓ | Cooling-coil, drain-pan, and condensate-drain inspections show no biological growth or standing water
✓ | Humidity maintained during cooling season; dew-point control verified
✓ | Building pressurization positive vs. outdoors (where designed); zone pressure relationships maintained
✓ | Documented IAQ Management / Legionella / Combustion-Safety plans current and signed
✓ | Standard 241 Infection-Risk-Mitigation Mode and Guideline 44 Smoke Readiness Plan documented and verified annually (if applicable)
✓ | No active occupant complaints related to odor, dust, mold, stuffiness, or temperature/humidity
✓ | Reduction in unscheduled work orders and HVAC service calls year over year
HOW TO USE THIS CHECKLIST
Each frequency tab (Monthly, Quarterly, Semi-Annual, Annual, Multi-Year) is a stand-alone inspection sheet. For each task, record the date completed, the technician initials, and a status (Pass / Fail / N/A / Deferred). If a task fails or cannot be verified, log a corrective action in the 'Findings / Corrective Action' column and on the 'Additional Observations Log' tab. Attach photos, readings, and TAB reports to the building's O&M manual. Increase frequency for any task that repeatedly fails, that operates in unusual conditions, or that supports critical-care occupancies. Validation tasks marked (V) require calibrated tools or a qualified technician (per ASHRAE 62.1 Note 3).
PRIMARY SOURCES
– | ANSI/ASHRAE Standard 62.1-2025 — Ventilation and Acceptable Indoor Air Quality, Section 8 (Operations & Maintenance) and Table 8-1
– | ANSI/ASHRAE/ACCA Standard 180-2018 — Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems
– | ANSI/ASHRAE Standard 188-2021 — Legionellosis: Risk Management for Building Water Systems (referenced for cooling tower & drift)
– | ASHRAE Standard 241-2023 — Control of Infectious Aerosols
– | ASHRAE Guideline 12 — Managing the Risk of Legionellosis Associated with Building Water Systems
– | U.S. EPA — Building Air Quality: A Guide for Building Owners and Facility Managers; IAQ Tools for Schools
– | USGBC LEED v5 — Indoor Environmental Quality credits (Enhanced IAQ Strategies, Indoor Air Quality Performance, Source Control, Cleaning & Maintenance)
– | ASHRAE Standard 52.2 — Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size (MERV)
– | ASHRAE Guideline 44-2024 — Protecting Building Occupants from Smoke During Wildfire and Prescribed Burn Events
– | NFPA 96
– | Local building codes, such as IRC, IFC or IMC
– | ASHRAE 154-2022, Ventilation for Commercial Cooking Operations, 54 - , 211
– | ANSI/ASSP Z9.5-2022, Laboratory Ventilation
– | NADCA ACR, The NADCA Standard for Assessment, Cleaning & Restoration of HVAC Systems--2025 Edition
– | SMACNA, IAQ Guidelines for Occupied Buildings
– | NIOSH - National Institute for Occupational Safety and Health,
– | ASHRAE Handbook 2023 = ASHRAE Handbook-HVAC Applications, Chapter 34 §1.14 Operations & Maintenance

## 2. Monthly
IAQ Preventive Maintenance — Monthly Tasks
Walk-through inspections to be completed every 30 days. These tasks catch the most common and fastest-moving IAQ failures: clogged filters, blocked drains, biological growth on coils, humidity excursions, and occupant complaints. Most can be completed visually using the BAS front-end and a flashlight.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
VENTILATION SYSTEM OPERATION
1 | Ventilation schedule | Verify that the BAS / control system is operating mechanical ventilation during all expected occupied periods per the building schedule and design intent. Confirm no overrides have been left active. | V | ASHRAE 62.1-2025 | §8.3 Ventilation System Operation
2 | Outdoor airflow | Spot-check outdoor airflow rate at AHUs equipped with airflow stations. Confirm OA is not below the design minimum during occupied operation. Trend OA% over the past 30 days for anomalies. | V | ASHRAE 62.1-2025 | §6.2 / §8.5 Task 11a
3 | Demand-Control Ventilation (DCV) | Spot-check CO2 levels in densely occupied spaces (conference rooms, classrooms, auditoriums). Confirm CO2-DCV strategy is responding to occupancy and not stuck at minimum or maximum. | V | LEED v5 EQ + ASHRAE 62.1 | EQ Indoor Air Quality Performance / §5.19
4 | BAS alarms | Review BAS alarm log for filter ΔP, low/high RH, low OA flow, freeze-stat trips, and supply-air-temp deviations. Acknowledge and dispatch as required. | V | ASHRAE 180-2018 | AHU controls maintenance
AIR FILTRATION
5 | Air filter pressure drop | Read filter ΔP gauges or BAS trends at each AHU. Replace any filter exceeding the maximum ΔP listed in the O&M manual or manufacturer's data. | V | ASHRAE 62.1-2025 | §5.5 / §8.5 Task 5a
6 | Filter integrity & seal | Visually inspect accessible filters for tears, damage, sagging, dust bypass, or moisture. Verify gasket/seal integrity so airflow cannot bypass the filter. | V | ASHRAE 62.1-2025 | §5.5 / §8.5 Task 5a
7 | Filter housing & rack | Inspect filter rack and housing for damage, gaps, or daylight visible at edges. Confirm correct filter thickness, fit, and size for the housing assembly. | V | ASHRAE 180-2018 | Filter section
8 | Walk-off mat / entryway system | Inspect entryway walk-off mats (≥ 10 ft / 3 m in primary direction of travel). Vacuum or replace as needed to reduce particulate ingress. | V | LEED v5 EQ | Enhanced IAQ Strategies — Entryway Systems
OUTDOOR AIR INTAKES & EXHAUST
9 | OA intakes — visual | Visually inspect outdoor air intakes for blockage, debris, ice, snow accumulation, bird/insect/rodent activity, vegetation, and proximity of new exhaust or contaminant sources. | V | ASHRAE 62.1-2025 | §5.4 / §8.5 Task 4a
10 | Exhaust openings | Confirm exhaust fans are running during occupied hours (kitchen, bathroom, janitor closet, parking, lab). Verify exhaust openings are not blocked and discharge away from intakes. | V | ASHRAE 62.1-2025 | §5.4 / §6.5 / §8.5 Task 18a
11 | Source separation | Walk the perimeter and roof; confirm no new dumpsters, cooling towers, generators, loading docks, or smoking areas have been placed within minimum separation distances of OA intakes. | V | ASHRAE 62.1-2025 | §5.4 / §8.5 Task 3a
MOISTURE, DRAINS & HUMIDITY
12 | Drain pans & condensate drains | Visually inspect accessible drain pans for standing water, biological growth, sediment, or rust. Verify condensate drains freely; clear traps and prime as needed. | V | ASHRAE 62.1-2025 | §5.7 / §8.5 Task 6a
13 | Humidifier operation | Verify humidifier feed and drain are operational. Inspect for scale, biological growth, leaks, and dispersion-pattern wetting on duct walls. | V | ASHRAE 62.1-2025 | §5.8 / §8.5 Task 7a
14 | Space humidity | Verify space relative humidity is within design limits (typically 30–60% RH). Investigate persistent excursions > 60% RH that can drive microbial growth. | V | ASHRAE 62.1-2025 | §5.12 / §8.5 Task 12a
15 | Moisture indicators | Walk occupied spaces and look for ceiling-tile staining, wall discoloration, peeling paint, bubbling flooring, or musty odors — any of which indicate active or historical moisture intrusion. | V | U.S. EPA Building Air Quality | BAQ Guide — Moisture
AIR-CLEANING DEVICES
16 | UV-C / air cleaners | Verify operation status indicators on UV-C lamps and other air-cleaning devices. Note any lamp-out or fault alarms. | V | ASHRAE 62.1-2025 | §5.9 / §8.5 Task 8a (Quarterly minimum)
OCCUPANT-FACING & SOURCE CONTROL
17 | Smoking / source-control compliance | Verify no-smoking signage at all building entrances and within 25 ft (7.6 m) of OA intakes, operable windows, and entrances. Confirm no combustion sources have been placed indoors. | V | LEED v5 EQ + ASHRAE 62.1 | EQ Environmental Tobacco Smoke / §5.4
18 | Cleaning chemicals storage | Verify cleaning chemicals, paints, solvents, pesticides, and other contaminants are NOT stored in mechanical rooms, return-air plenums, or other air-handling spaces. | V | ASHRAE 62.1-2025 | §5.10 / §8.5 Task 10a
19 | CO / combustion-safety alarms | Test carbon-monoxide alarms in parking garages, mechanical rooms with combustion equipment, and any space served by combustion appliances. Replace batteries; log test date. | V | LEED v5 + NFPA / IRC | EQ Source Control
20 | Occupant complaint log | Review and respond to all occupant IAQ complaints (odor, dust, stuffiness, headaches, irritation) received in the past 30 days. Document response and disposition. | V | LEED v5 EQ | EQ IAQ Management Plan
21 | Integrated Pest Management (IPM) | Confirm no rodent, bird, or insect activity in mechanical rooms, plenums, or near OA intakes. Verify pest-control service records are current. | V | LEED v5 EQ | EQ Cleaning & Maintenance — IPM
22 | Diffusers & return grilles | Visually inspect supply diffusers, return grilles, and exhaust grilles for dust accumulation, blockage by furniture or stored items, and damaged louvers/dampers. | V | ASHRAE 180-2018 | Air distribution
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician — per ASHRAE 62.1 §8.5 Note 3)

## 3. Quarterly
IAQ Preventive Maintenance — Quarterly Tasks
Quarterly tasks add a closer look at filtration performance, air-cleaning device function, damper operation, and BAS sensor accuracy. Several ASHRAE 62.1-2025 Table 8-1 tasks have a minimum frequency of Quarterly.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
AIR FILTRATION — VERIFY
1 | Filter fit, function & performance | Verify air filtration efficiency and PM rating meet or exceed the minimum requirements. Confirm filter thickness, fit, and seal so that airflow cannot bypass the media. Replace any filter exceeding maximum ΔP per the O&M manual. | V | ASHRAE 62.1-2025 | §5.5 / §8.5 Task 5a
2 | Electronic-air-cleaner operation | Verify electronic air-cleaning devices (electrostatic precipitators, ionizers, photocatalytic units) are operating in accordance with the manufacturer's instructions. Check fault and indicator lights. | V | ASHRAE 62.1-2025 | §5.9 / §8.5 Task 8a
3 | UV-C lamp condition | Inspect UV-C lamps for malfunction or end-of-life indication. Determine root cause for any lamp failure. Clean lamps per manufacturer instructions; replace per manufacturer schedule or upon failure. | V | ASHRAE 62.1-2025 | §5.9 / §8.5 Task 8a
4 | Gas-phase / activated-carbon media | Inspect activated-carbon and other gas-phase filtration modules for media life. Replace per manufacturer schedule or per occupant odor / VOC complaint trend. | V | ASHRAE 180-2018 + LEED v5 | Gas-phase filtration / EQ Enhanced Strategies
DAMPERS, ECONOMIZERS & FANS
5 | Outside-air dampers — operation | Stroke OA, return-air, exhaust, and economizer dampers full open / full close via the BAS. Verify smooth travel, full closure (no daylight), tight actuator clamps, and fail-safe direction on power loss. | V | ASHRAE 62.1-2025 | §5.19 / §8.5 Task 14a
6 | Backdraft & isolation dampers | Verify backdraft dampers and combination smoke/fire dampers operate freely and seal under no-flow conditions. | V | ASHRAE 180-2018 | Damper assembly maintenance
7 | Fan-assembly inspection | Inspect supply, return, exhaust, and dedicated outdoor air fans for belt wear, sheave alignment, bearing noise, balance, vibration, and cleanliness. Lubricate per OEM. | V | ASHRAE 180-2018 | Fan section
SENSORS & CONTROLS — VERIFY
8 | CO2 sensor reasonableness | Compare BAS-displayed CO2 readings in dense spaces against a calibrated handheld instrument. Investigate drift > ±100 ppm. Confirm sensors not at end of OEM calibration interval. | V | ASHRAE 62.1-2025 | §5.19 / §8.5 Task 11a
9 | Humidity & temperature sensors | Cross-check space and duct humidity and temperature sensors against a calibrated reference. Investigate drift exceeding manufacturer tolerance. | V | ASHRAE 62.1-2025 | §5.8 / §8.5 Task 7a
10 | CO / NO2 sensors | Functionally test CO and NO2 sensors in parking garages and mechanical rooms with combustion equipment. Verify alarms shed power to ignition sources or activate exhaust as designed. | V | LEED v5 EQ + IFC/IMC | EQ Source Control / Local Code
KITCHEN / EXHAUST / SPECIALTY
11 | Kitchen exhaust grease filters | Inspect and clean grease filters in commercial kitchen exhaust hoods. Inspect duct condition. Coordinate hood cleaning per NFPA 96 schedule. | V | ASHRAE 154 / NFPA 96 | Commercial cooking exhaust
12 | Bathroom & janitor exhaust | Verify continuous or scheduled bathroom and janitor closet exhaust fans are operating, achieving design CFM, and discharging to exterior (not into a return plenum). | V | ASHRAE 62.1-2025 | §6.5 / §8.5 Task 18a
13 | Lab / fume-hood exhaust | Confirm lab fume-hood face velocity, sash position alarm function, and lab-room negative pressurization where applicable. | V | ANSI/ASSP Z9.5 | Laboratory ventilation
AHU INTERIOR & DISTRIBUTION
14 | AHU interior cleanliness | Open AHU access doors and visually inspect mixing-box, filter section, coil section, and fan section for dust accumulation, biological growth, microbial staining, and debris. Photograph any concerns. | V | ASHRAE 180-2018 | AHU interior
15 | Diffuser & return-grille cleaning | Vacuum/wipe diffusers, return-air grilles, and transfer grilles. Inspect ceiling-cavity (if return plenum) for dust accumulation on top side of tiles. | V | ASHRAE 180-2018 + LEED v5 | Air distribution / EQ Cleaning
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician — per ASHRAE 62.1 §8.5 Note 3)

## 4. Semi-Annual
IAQ Preventive Maintenance — Semi-Annual Tasks
Semi-annual tasks (twice per year, typically aligned with cooling-season start-up and heating-season start-up). Several ASHRAE 62.1-2025 Table 8-1 tasks have a minimum frequency of Semiannually. These checks dig deeper into AHU internals, drains, humidifiers, intakes, and access provisions.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
OUTDOOR AIR INTAKES & EXHAUST OPENINGS — DETAILED
1 | OA intakes — full inspection | Inspect outdoor air intakes, exhaust openings, bird screens, louvers, dampers, and attached components and ducting for: (a) biological growth, (b) corrosion, (c) buildup of dirt and debris, (d) presence of birds/insects/animals, (e) integrity. Clean and repair as needed; determine root cause. | V | ASHRAE 62.1-2025 | §5.4 / §8.5 Task 4a
2 | Bird screens / insect screens | Remove, clean, and inspect bird and insect screens. Verify minimum 1/2 in mesh on bird screens and that screens have not collapsed or been damaged. | V | ASHRAE 62.1-2025 + ASHRAE 180 | §5.4.5 / Intake hood
3 | Louver drainage | Verify louver drain pans and weep holes are clear; confirm rain/snow does not enter the airstream. | V | ASHRAE 180-2018 | Outdoor air intake
DRAIN PANS, TRAPS & CONDENSATE
4 | Drain pans — full inspection | Inspect drain pans within all air-handling equipment, ductwork, and plenums. Verify: pan is positioned under all water-producing devices; pan slopes toward drain outlet; no biological growth, corrosion, or debris; water drains freely; traps/seals/priming devices are wet and operational; pumps are operational; no signs of overflow or carryover; shutoff/alarm devices function as intended. Clean and repair as needed. | V | ASHRAE 62.1-2025 | §5.7 / §8.5 Task 6a
5 | Drain pan treatment | Apply EPA-registered antimicrobial drain-pan treatment (tablets/strips) per manufacturer schedule. Do NOT use ozone or unapproved chemicals. | V | ASHRAE 180-2018 + LEED v5 | Drain pan / EQ Cleaning
6 | Condensate drain priming | Confirm draw-through and blow-through trap depths are sized correctly for the AHU static pressure. Re-prime traps that may have evaporated during shoulder season. | V | ASHRAE 62.1-2025 | §5.7.4 / §7.2.3
HUMIDIFIERS & DEHUMIDIFIERS
7 | Humidifier — full inspection | Inspect humidifiers and dehumidifiers: verify drain components function as intended; verify water-feed components function; inspect for biological growth, corrosion, or debris on units or associated ducting; verify humidity / dew-point / moisture sensors read within design ranges; verify operation of desiccant dehumidifiers per manufacturer. | V | ASHRAE 62.1-2025 | §5.8 / §8.5 Task 7a
8 | Dispersion-tube wetting | Inspect dispersion zones for wetting of duct walls, downstream coils, or absorption distance. Adjust setpoint or modulation to eliminate wetting. | V | ASHRAE 180-2018 | Humidifier maintenance
9 | Steam humidifier cylinder / canister | For electrode / steam-cylinder type humidifiers, inspect cylinder fouling and replace canister per OEM schedule. | V | ASHRAE 180-2018 | Humidifier maintenance
ACCESS, SPACE & EQUIPMENT INTEGRITY
10 | Access for maintenance | Verify space and access is provided and unobstructed for: balancing/verification/measurement areas; routine maintenance and inspection per §8.2; verification of components per §8.5; sensors, instruments, controls, equipment; access doors and panels (functional, sealed when closed). Clean, repair, and provide access as needed. | V | ASHRAE 62.1-2025 | §5.10 / §5.21 / §8.5 Task 9a
11 | AHU casing & insulation integrity | Inspect AHU casing, doors, gaskets, and internal liner / insulation in accessible areas for damage, moisture, biological growth, and corrosion. Repair as needed. | V | ASHRAE 62.1-2025 + ASHRAE 180 | §5.1.2 / §8.5 Task 2a
12 | Coil cleanliness — visual | Inspect cooling and heating coils for fouling, fin damage, biological staining, and air-side bypass. Schedule deep coil cleaning if visual loading exceeds OEM threshold. | V | ASHRAE 180-2018 | Coil maintenance
13 | Energy-recovery ventilator (ERV) cores | Inspect ERV / HRV cores, plates, or wheels for fouling, frost damage, gasket condition, and seal-bypass. Clean per OEM. Verify purge sector (wheel) is set correctly. | V | ASHRAE 180-2018 | ERV/HRV
DUCTWORK & PLENUMS
14 | Accessible duct insulation | Inspect piping and ductwork insulation system in accessible areas for integrity and signs of moisture or biological growth and repair as needed. | V | ASHRAE 62.1-2025 | §5.1.2 / §8.5 Task 2a
15 | Plenum / mechanical-room cleanliness | Inspect floor, ceiling, and mechanical-room plenum systems and ductwork — verify no biological growth, corrosion, insects, or animals; verify chemicals, cleaning products, equipment, or other materials are not stored in air-handling spaces or plenums. | V | ASHRAE 62.1-2025 | §5.10 / §5.11 / §8.5 Task 10a
OCCUPANT-FACING & DOCUMENTATION
16 | IAQ Management Plan refresh | Walk-through review of the IAQ Management Plan, including procedures for new occupant complaints, construction/renovation IAQ controls, smoking policy, and pollutant source control. Update as needed. | V | LEED v5 EQ | EQ Indoor Air Quality Management Plan
17 | Occupant survey (optional) | Distribute or review occupant satisfaction / IAQ comfort survey results (where program is in place). Trend results and address recurring complaints. | V | LEED v5 EQ | EQ Occupant Comfort Survey
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician — per ASHRAE 62.1 §8.5 Note 3)

## 5. Annual
IAQ Preventive Maintenance — Annual Tasks
Annual inspections — the deepest verification cycle short of full TAB validation. These tasks comprise most of ASHRAE 62.1-2025 Table 8-1 and are the foundation of the building's IAQ Management Plan, the O&M Manual, and any LEED v5 IAQ documentation.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
REGIONAL & PROGRAMMATIC
1 | Nonattainment-area status | Verify that the building is located in an area not designated as a nonattainment area for criteria pollutants (40 CFR 50). If newly designated nonattainment, prepare and implement a plan to comply with §6.1.4. | V | ASHRAE 62.1-2025 | §4.1 / §6.1.4 / §8.5 Task 1a
2 | Building alteration / change-of-use review | Document any alterations, changes in occupancy, density, or use over the past year. If any are inconsistent with system design assumptions, re-evaluate ventilation system design, operation, and maintenance and update the O&M manual. | V | ASHRAE 62.1-2025 | §8.1.2
3 | Separation distances | Verify that no modifications to the HVAC system or facility have been made that impact separation distances between OA intakes and exhausts/contaminant sources. Document deficiencies and corrective actions. | V | ASHRAE 62.1-2025 | §5.4.1 / §8.5 Task 3a
AIR BALANCE & VENTILATION RATES
4 | Annual air-balance verification | Review design documents and most recent TAB report. Determine if reported airflows meet design intent. When OA airflow is displayed: verify outdoor airflows meet design; in spaces requiring exhaust per Table 6-2, verify exhaust > supply. Verify dynamic-reset and OA per Task 14a. | V | ASHRAE 62.1-2025 | §5.10.3 / §7.2.2 / §8.5 Task 11a
5 | CO2 sensor calibration date & DCV setup | Verify CO2 sensor calibration date is within manufacturer interval; if not, calibrate. Determine space type and design occupancy and verify maximum CO2 limit is correctly set. Verify ventilation reduction or occupancy-standby behavior in unoccupied spaces. | V | ASHRAE 62.1-2025 | §5.19 / §8.5 Task 11a
6 | Humidity-limit compliance | Verify cooling systems maintain indoor conditions below the humidity limits referenced in §5.12. Take corrective actions for excursions. | V | ASHRAE 62.1-2025 | §5.12 / §8.5 Task 12a
7 | Building pressurization & directional airflow | Verify directional airflow and building pressurization. Verify zones are pressurized positive or negative per design and that flow moves toward exhaust. Verify operation of any pressure indication / measurement sensors. | V | ASHRAE 62.1-2025 | §5.14 / §5.18 / §6.5.1.4 / §8.5 Task 13a
LEGIONELLA & WATER-AEROSOL CONTROL
8 | Legionella plan | Verify Legionella risk-management plan is implemented and maintained per ASHRAE Standard 188 / Guideline 12. Confirm cooling tower drift eliminator, biocide program, and inspection records are current. | V | ASHRAE 62.1-2025 + Std 188 | §5.22 / §8.5 Task 15a
NATURAL & EXHAUST VENTILATION
9 | Natural ventilation | Verify occupant-operated natural-ventilation openings are functional and accessible. Verify automated controls operate during occupied periods and openings cannot close except during unoccupied periods or when mechanical ventilation is active. Verify mechanical-ventilation backup operates when natural is inadequate. | V | ASHRAE 62.1-2025 | §6.4.3 / §8.5 Task 17a
10 | Exhaust-system verification | For Prescriptive path (§6.5.1): review TAB report and verify exhaust airflow rates per Tables 6-2 and 6-3. For Performance path (§6.5.2): verify exhaust monitoring/control is detecting and maintaining concentrations below limits, and design airflow rates are maintained by airflow sensors. | V | ASHRAE 62.1-2025 | §6.5 / §8.5 Task 18a
AHU INTERIOR — DEEP CLEAN
11 | Cooling-coil deep clean | Perform full cooling-coil cleaning (chemical or steam) per OEM and IAQ guidance. Inspect for fin damage, corrosion, and biological loading. Photograph before/after. | V | ASHRAE 180-2018 + LEED v5 | Coil cleaning / EQ Cleaning
12 | Heating-coil inspection | Inspect heating coil (hot water, steam, or electric) for cleanliness, leaks, corrosion, and proper drainage of condensate from steam coils. Clean as needed. | V | ASHRAE 180-2018 | Heating coil
13 | AHU full interior cleaning | Open all AHU access doors. Clean mixing-box, filter section, fan section, and downstream-of-coil surfaces. Wipe down internal liner. Document any insulation damage requiring repair. | V | ASHRAE 180-2018 + LEED v5 | AHU cleaning / EQ Cleaning
14 | ERV/HRV core service | Service ERV/HRV cores: replace gaskets and seals, deep-clean plates or wheel, verify purge angle (wheel), verify defrost strategy, and confirm bypass damper function. | V | ASHRAE 180-2018 | ERV/HRV service
15 | Duct cleaning assessment | Inspect supply and return ductwork (with camera or borescope where accessible) for dust loading, biological growth, debris, and rodent activity. Engage a NADCA-certified contractor if cleaning is warranted. | V | NADCA ACR / ASHRAE 180 | Duct cleaning
HUMIDIFIERS & DEHUMIDIFIERS — ANNUAL
16 | Humidifier media replacement | Replace humidifier media (evaporative pads, electrode cylinders, ultrasonic transducers) per OEM schedule. Inspect dispersion nozzles and steam-line trap function. | V | ASHRAE 180-2018 | Humidifier service
17 | Desiccant dehumidifier | Inspect desiccant rotor, regeneration heater, purge sector, and seals. Verify performance per OEM data. | V | ASHRAE 62.1-2025 + 180 | §5.8
CONTROLS & SENSORS
18 | Sensor calibration audit | Audit calibration records for all IAQ-relevant sensors: CO2, OA flow stations, RH, dewpoint, T, static pressure, CO, NO2, occupancy. Re-calibrate per OEM. | V | ASHRAE 62.1-2025 | §5.19 / Task 11a
19 | Demand-control ventilation logic | Audit BAS sequences for DCV: minimum OA per zone, maximum CO2 setpoint, occupancy-standby behavior, and dynamic-reset-to-design logic. | V | ASHRAE 62.1-2025 | §5.19 / §6.2.5
20 | Standard 241 Infection-Risk-Mitigation Mode (if applicable) | If the building has implemented Standard 241 (control of infectious aerosols), verify the Infection-Risk-Mitigation Mode (IRMM) controls are operational, the equivalent clean airflow is being delivered, and the BMP equipment is in compliance. | V | ASHRAE 241-2023 | § Building Readiness / IRMM
21 | Guideline 44 Smoke Readiness (if applicable) | If the building is in a wildfire-impacted region and has implemented Guideline 44, verify the Smoke Readiness Plan is current and the building is ready to switch to Smoke-Ready Mode: outdoor-air dampers can be closed and economizer / DCV overridden via the BAS while maintaining positive building pressure; MERV 13 (or highest practical) filtration is in place with seals intact; supplemental OA-intake filters and portable air cleaners (PACs) are stocked; envelope sealing is intact; PM2.5 monitors are functional and a non-event baseline is captured; smoke detectors have been cleaned/tested pre-season; and staff are trained on plan activation, supplemental filter installation, and return-to-normal procedures. | V | ASHRAE Guideline 44 | §6.1 / §6.2 / Checklist 1
SOURCE CONTROL & DOCUMENTATION
22 | IAQ assessment / measurement | Conduct an annual IAQ assessment. At minimum measure CO2, PM2.5, TVOC, formaldehyde, RH, and T at representative locations. Compare results to LEED v5 thresholds and ASHRAE / WHO guidelines. | V | LEED v5 EQ + ASHRAE 62.1 IAQP | EQ Indoor Air Quality Performance / §6.3
23 | Combustion-safety check | Inspect all combustion appliances (boilers, furnaces, water heaters, fireplaces, generators) — flue/vent integrity, draft, spillage, CO output. Document corrective actions. | V | LEED v5 + NFPA 54 / 211 | EQ Source Control
24 | Garage & loading dock CO/NO2 management | Verify garage exhaust systems are interlocked with CO/NO2 sensors and operate to maintain concentrations below the limits in §6.5 / §8.5 Task 18a. | V | ASHRAE 62.1-2025 | §6.5 / Task 18a
25 | O&M Manual update | Review and update the written or electronic O&M manual: O&M procedures, ventilation operating schedules, design drawings, manufacturer maintenance schedules, inspection/maintenance frequencies from Table 8-1 and Std 180. | V | ASHRAE 62.1-2025 | §8.2
26 | Staff training & competency | Provide annual IAQ-focused training for all O&M staff: ventilation fundamentals, filter handling, mold awareness, sensor calibration basics, occupant-complaint response. | V | LEED v5 EQ | EQ Cleaning & Maintenance
27 | Construction / renovation IAQ controls | Review controls used during any construction, renovation, or major repair work in the past year (SMACNA IAQ Guidelines for Occupied Buildings; flush out if any). Confirm protections were documented. | V | LEED v5 + SMACNA | EQ Construction IAQ Management
28 | Cleaning chemical / Green Cleaning policy | Confirm Green-Cleaning policy is in effect; cleaning products and procedures comply with low-VOC criteria; SDS file is current; pesticide / IPM record is current. | V | LEED v5 EQ | EQ Cleaning & Maintenance / IPM
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician — per ASHRAE 62.1 §8.5 Note 3)

## 6. Multi-Year & As-Required
IAQ Preventive Maintenance — Multi-Year (2–3 Years) & As-Required
Multi-year tasks include the validation activities that require calibrated instruments and qualified technicians (per ASHRAE 62.1 §8.5 Note 3), and the deeper IAQP / dynamic-reset reviews. Schedule these into a 3-year rolling plan in the O&M manual.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
EVERY 2 YEARS
1 | Variable-load / dynamic-reset controls | Inspect and test damper assemblies (seals, linkages, full-range travel, actuator-clamp tightness, fail-safe direction). Inspect fan assemblies (belt tension, sheave alignment, bearings, balance, cleanliness, electrical, VFDs). For ventilation zones with airflow sensors, verify zone-level controls reset to changing conditions; verify zone air ventilation rates during fan turndown; verify DCV zones respond to occupancy; verify occupancy controls shut off zone ventilation when unoccupied or in standby. | V | ASHRAE 62.1-2025 | §5.19 / §6.2.5–6.2.6 / §8.5 Task 14a
2 | IAQP system change review | For systems designed per the Indoor Air Quality Procedure (IAQP, §6.3), verify whether changes to occupancy, space utilization, new procedures (printers, computers, cleaning chemicals), new components (new furniture), or refurbishments (carpet, paint, tile, windows) have been made that could increase the design compounds in Table 6-5. If yes, trigger Task 16b validation. | V | ASHRAE 62.1-2025 | §6.3 / §8.5 Task 16a
EVERY 3 YEARS
3 | Humidity-sensor validation | Validate (calibrated tools, qualified technician) that humidity, dew point, and other moisture-measurement sensors are calibrated and function as intended. | Vd | ASHRAE 62.1-2025 | §5.8 / §8.5 Task 7b
4 | TAB air-balance validation | Measure outdoor airflows of all units and adjust as necessary. Spot-check space-level airflows at minimum 20% of all zones at outlets and inlets. Rebalance as necessary to comply with design intent and the standard. Rebalance exhaust airflows to maintain pressurization. Validate CO2 sensor calibration date and DCV setup; calibrate when past manufacturer interval. Validate, maintain, and calibrate ventilation sensors (static / differential pressure transducers used for fan, room, VAV, airflow, and filter control). Validate airflow rates of airflow sensors; clean and calibrate per OEM. | Vd | ASHRAE 62.1-2025 | §5.10.3 / §5.19 / §6.2.5–6.2.6 / §7.2.2 / §8.5 Task 11b
AS REQUIRED (event-driven)
5 | IAQP design-compound (DC) and PM2.5 validation | For systems designed per the IAQP, validate that concentrations of design compounds (DCs) and PM2.5 remain less than the design limits per §6.3.1. Perform objective evaluation per §7.3.1; if any limit is exceeded, perform root-cause analysis (flow rates, cleaner repair/replacement). Conduct subjective occupant evaluation per §7.3.2 and address concerns. | Vd | ASHRAE 62.1-2025 | §6.3.1 / §6.3.3.2 / §7.3 / §8.5 Task 16b
6 | Post-renovation flush-out | After major renovation or new construction, perform a building flush-out using 100% outdoor air per LEED v5 or conduct post-construction IAQ testing prior to occupancy. | V | LEED v5 EQ | EQ Construction IAQ Management — Flush-out
7 | Event-driven IAQ assessment | Initiate special IAQ investigation in response to: occupant complaint clusters, water intrusion / flooding, fire / smoke event, sewer-gas event, microbial contamination event, infectious-disease outbreak. During wildfire or prescribed-burn smoke events, implement the building's Smoke Readiness Plan per ASHRAE Guideline 44 (place building in Smoke-Ready Mode and return to normal operation when smoke clears). | V | U.S. EPA / NIOSH / ASHRAE 241 / Guideline 44 | Incident response
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician — per ASHRAE 62.1 §8.5 Note 3)

## 7. Commercial Kitchen
IAQ Preventive Maintenance - Commercial Kitchen Ventilation
Operations & maintenance tasks for commercial kitchen ventilation (CKV) systems. CKV is a complex system covering exhaust hoods, grease ducts, exhaust fans, makeup/replacement air, fire suppression, and pollution control. Improper O&M creates fire, IAQ, and energy risks. Frequencies and procedures below are drawn from the 2023 ASHRAE Handbook-HVAC Applications, Chapter 34 §1.14. Refer to NFPA 96 for additional operation and maintenance requirements related to fire and life safety.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
DAILY / EACH SHIFT
1 | Cooking surfaces | Clean solid cooking surfaces between each cycle if possible, or at least once daily; baked-on product insulates and retards heat transfer. | V | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Cooking Equipment
2 | Frying medium | Filter frying medium daily; change on the schedule recommended by the supplier. | V | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Cooking Equipment
3 | Hood grease filters | Clean hood grease filters at least daily. High-efficiency grease extractors may require cleaning during each shift. | V | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Exhaust Systems
MONTHLY
4 | Solid-fuel appliances | Monthly duct cleaning with weekly inspections; verify spark arrestors and required spacing from fryers. | Vd | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Cooking Equipment
QUARTERLY
SEMI-ANNUAL (every 6 months)
5 | AHU / coils / fan seasonal cleaning | Clean replacement-air AHU, coils, and fan in spring and fall (seasonal change). More frequent cleaning may be required in contaminated environments. Check that the replacement air system is operating. Check that dampers are set correctly, filters and exchangers are clean, the belts are tight, the fan is turning in the correct direction, and supply and return ductwork and registers are open, with supply air discharging in the correct direction and pattern. If drafts persist, the system may need to be rebalanced. If noise persists in a balanced system, system changes may be required. | Vd | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Supply, Replacement & Return Air
ANNUAL
6 | Capture-and-containment verification | Capture-and-containment verification check of kitchen exhaust hoods. | Vd | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Recommissioning
7 | Control-system performance verification | Performance verification check of all control systems related to the CKV system. | Vd | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Recommissioning
EVERY 2 YEARS
8 | Outside-air verification | Verify proper outside-air quantities to the kitchen. | Vd | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Recommissioning
EVERY 5 YEARS (MINIMUM) / MULTI-YEAR
9 | CKV system recommissioning | Recommission and rebalance the CKV system at minimum every 5 years. | Vd | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Recommissioning
AS-REQUIRED / EVENT-DRIVEN
10 | Recommission after change | Recommission and rebalance any time CKV/related HVAC equipment is changed (replacing exhaust or makeup fans, relocating supply/return grilles), or cooking equipment is replaced with equipment of a different function (e.g., fryer to broiler). | Vd | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Recommissioning
11 | Recommission after performance issue | Recommission and rebalance whenever performance issues arise - smoke or heat loss from hoods, abnormal space temperatures, high-velocity drafts at pass-through windows, condensation, or negative building pressure. | Vd | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Recommissioning
12 | Professional cleaning contractor | Use trained, qualified, certified persons (acceptable to the AHJ) for exhaust-system cleaning. Verify adequate liability insurance. Reference PWNA / IKECA member directories and best practices. | V | ASHRAE Handbook 2023 | Ch. 34 §1.14 - Supply, Replacement & Return Air
Type Codes:
V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)

## 8. Observations Log
Additional IAQ Observations & Concerns Log
Use this log to record any IAQ-related observation, concern, or occupant complaint that arises between scheduled inspections, or to document follow-up on items flagged as 'Fail' or 'Deferred' on the frequency tabs. Each entry should be linkable back to its source standard or rating-system requirement.
Date | Time | Location / Room | Equipment / System | Observation / Concern | Level of Concern | Tested? | Measurement / Reading | Source / Reference | Action Taken / Next Steps | Performed By | Status

## 9. Common Observations
Common Observations and Path Forward
This indicates some common issues that can be observed and the potential path forward towards resolution. Please know that this information is captured in the proactive checklists and will be checked accordingly.
Common Negative Observations | Technical Description | Metric(s) | Considerations | Next Steps / Remediation

## 10. Standards Crosswalk
Source & Standards Crosswalk
This crosswalk maps the requirements of ASHRAE Standard 62.1-2025 §8 Table 8-1, ANSI/ASHRAE/ACCA Standard 180, and LEED v5 Indoor Environmental Quality credits to the tabs in this workbook so a reviewer can confirm coverage.
Standard / Rating System | Section / Credit | Title / Topic | Frequency | Where in this Workbook
ASHRAE STANDARD 62.1-2025 — §8 OPERATIONS & MAINTENANCE
ASHRAE 62.1-2025 | §8.1.1 | Application of O&M requirements to in-service buildings | — | Cover & Guide
ASHRAE 62.1-2025 | §8.1.2 | Reevaluate when building is altered or use changes; update O&M manual | Event-driven | Annual
ASHRAE 62.1-2025 | §8.2 | Develop and maintain written/electronic O&M Manual | Ongoing | Annual
ASHRAE 62.1-2025 | §8.3 | Operate ventilation systems consistent with O&M manual; ventilate spaces during occupancy | Ongoing | Monthly
ASHRAE 62.1-2025 | §8.4 | Maintain ventilation system components per O&M manual | Ongoing | All freq tabs
ASHRAE 62.1-2025 | §8.5 Task 1a | Verify nonattainment-area status (4.1 / 6.1.4) | Annually | Annual
ASHRAE 62.1-2025 | §8.5 Task 2a | Inspect piping/ductwork insulation in accessible areas (5.1.2) | Annually | Annual / Semi-Annual
ASHRAE 62.1-2025 | §8.5 Task 3a | Verify no modifications affecting separation distances (5.4.1) | Annually | Annual / Monthly
ASHRAE 62.1-2025 | §8.5 Task 4a | Inspect OA intakes & exhaust openings, screens, louvers, dampers (5.4.3–5.4.5) | Semi-annually | Semi-Annual / Monthly
ASHRAE 62.1-2025 | §8.5 Task 5a | Verify air filtration fit, function, and performance (5.5 / 5.9) | Quarterly or scheduled replacement if sooner | Quarterly / Monthly
ASHRAE 62.1-2025 | §8.5 Task 6a | Inspect drain pans, seals, traps, drains within AHE (5.7) | Semi-annually | Semi-Annual / Monthly
ASHRAE 62.1-2025 | §8.5 Task 7a | Inspect humidifiers and dehumidifiers (5.8) | Semi-annually | Semi-Annual / Monthly
ASHRAE 62.1-2025 | §8.5 Task 7b | Validate humidity / dew-point sensor calibration (5.8) | Every 3 years | Multi-Year
ASHRAE 62.1-2025 | §8.5 Task 8a | Verify operation of electrical air-cleaners and UV devices (5.9) | Quarterly | Quarterly / Monthly
ASHRAE 62.1-2025 | §8.5 Task 9a | Verify space and access for maintenance and inspection (5.10.1 / 5.21) | Semi-annually | Semi-Annual
ASHRAE 62.1-2025 | §8.5 Task 10a | Inspect floor/ceiling/mech-room plenums and ductwork; no chemicals stored (5.10.2 / 5.11) | Annually | Annual / Semi-Annual
ASHRAE 62.1-2025 | §8.5 Task 11a | Air-balance verification; CO2 sensor cal date; DCV setup | Annually | Annual
ASHRAE 62.1-2025 | §8.5 Task 11b | TAB air-balance validation; sensor calibration | Every 3 years | Multi-Year
ASHRAE 62.1-2025 | §8.5 Task 12a | Verify cooling systems maintain humidity below limits (5.12) | Annually | Annual / Monthly
ASHRAE 62.1-2025 | §8.5 Task 13a | Verify directional airflow and building pressurization (5.14 / 5.18) | Annually | Annual
ASHRAE 62.1-2025 | §8.5 Task 14a | Verify variable-load / dynamic-reset controls (5.19 / 6.2.5–6.2.6) | Every 2 years | Multi-Year / Quarterly
ASHRAE 62.1-2025 | §8.5 Task 15a | Verify Legionella plan implemented (5.22) | Annually | Annual
ASHRAE 62.1-2025 | §8.5 Task 16a | IAQP — verify changes to occupancy / use / components (6.3) | Every 2 years | Multi-Year
ASHRAE 62.1-2025 | §8.5 Task 16b | IAQP — validate DC and PM2.5 below design limits (6.3 / 7.3) | As required | Multi-Year
ASHRAE 62.1-2025 | §8.5 Task 17a | Verify natural-ventilation controls and accessibility (6.4.3) | Annually | Annual
ASHRAE 62.1-2025 | §8.5 Task 18a | Verify exhaust ventilation per Tables 6-2 / 6-3 (6.5) | Annually | Annual / Quarterly
ANSI/ASHRAE/ACCA STANDARD 180-2018
ASHRAE 180-2018 | Filters | Filter inspection, ΔP, replacement, seal integrity | Monthly to Quarterly | Monthly / Quarterly
ASHRAE 180-2018 | Coils | Cooling and heating coil inspection, cleaning, biological growth | Quarterly to Annually | Semi-Annual / Annual
ASHRAE 180-2018 | Drain pans / condensate | Pan slope, biological growth, trap depth, drainage | Monthly to Semi-Annually | Monthly / Semi-Annual
ASHRAE 180-2018 | Humidifiers / Dehumidifiers | Operation, scale, water quality, dispersion | Monthly to Annually | All freq tabs
ASHRAE 180-2018 | Dampers | Stroke, seal, linkage, fail-safe direction | Quarterly to Bi-annual | Quarterly / Multi-Year
ASHRAE 180-2018 | Fans | Belt, sheave, bearings, balance, cleanliness | Quarterly to Annually | Quarterly / Annual
ASHRAE 180-2018 | AHU casing / interior | Interior cleanliness, gaskets, seals, insulation | Quarterly to Annually | Quarterly / Annual
ASHRAE 180-2018 | Ductwork & plenums | Cleanliness, leakage, insulation, biological growth | Semi-Annually to Annually | Semi-Annual / Annual
ASHRAE 180-2018 | ERV / HRV | Core fouling, gasket condition, seal bypass, defrost | Semi-Annually to Annually | Semi-Annual / Annual
ASHRAE 180-2018 | Sensors | Functional verification of CO2, RH, T, OA flow | Quarterly to Annually | Quarterly / Annual
ASHRAE 180-2018 | Exhaust systems | Kitchen, bathroom, lab, garage exhaust | Monthly to Quarterly | Monthly / Quarterly
USGBC LEED v5 — INDOOR ENVIRONMENTAL QUALITY (EQ)
LEED v5 EQ | Minimum IAQ Performance (Prereq) | Comply with ASHRAE 62.1-2022/2025 design and O&M minimums | Ongoing | All freq tabs
LEED v5 EQ | Environmental Tobacco Smoke Control (Prereq) | Prohibit smoking inside; signage; 25 ft from openings | Ongoing / Monthly | Monthly
LEED v5 EQ | Enhanced IAQ Strategies — Entryway Systems | Walk-off mats ≥ 10 ft at primary entrances | Monthly | Monthly
LEED v5 EQ | Enhanced IAQ Strategies — Filtration | MERV 13 (or higher) filters; verify fit and function | Quarterly | Quarterly / Monthly
LEED v5 EQ | Enhanced IAQ Strategies — Source-Capture Exhaust | Exhaust at chemical / printing / janitorial spaces | Quarterly to Annually | Quarterly / Annual
LEED v5 EQ | Indoor Air Quality Performance | Annual measurements: CO2, PM2.5, TVOC, formaldehyde, RH, T | Annually | Annual
LEED v5 EQ | Source Control — Combustion Safety | Inspect flues/vents/draft on all combustion appliances | Annually | Annual
LEED v5 EQ | Source Control — CO Monitoring | CO sensors in garages, mechanical rooms with combustion | Quarterly | Monthly / Quarterly
LEED v5 EQ | IAQ Management Plan | Written plan: complaint response, source control, O&M procedures | Annually + ongoing | Cover / Semi-Annual / Annual
LEED v5 EQ | Construction IAQ Management | SMACNA IAQ Guidelines during construction; flush-out or testing | Event-driven | Multi-Year
LEED v5 EQ | Cleaning & Maintenance — Green Cleaning | Low-VOC cleaning products; SDS file; training | Annually + ongoing | Annual / Monthly
LEED v5 EQ | Cleaning & Maintenance — Integrated Pest Mgmt | IPM plan; non-toxic-first hierarchy; service records | Monthly + Annually | Monthly / Annual
LEED v5 EQ | Occupant Comfort Survey | Distribute occupant satisfaction / IAQ survey, address findings | Semi-Annually to Annually | Semi-Annual
ASHRAE STANDARD 188 / GUIDELINE 12 / STANDARD 241 / GUIDELINE 44
ASHRAE 188-2021 | §5–7 | Building Water System Risk Management — Legionella | Ongoing / Annual | Annual
ASHRAE Guideline 12 | — | Managing the Risk of Legionellosis | Ongoing / Annual | Annual
ASHRAE 241-2023 | Building Readiness / IRMM | Infectious-Aerosol Risk-Mitigation Mode | Annual + event-driven | Annual
ASHRAE Guideline 44 | §6 | Smoke Readiness Plan — wildfire & prescribed-burn smoke events | Annual + event-driven | Annual / As-Required
ASHRAE Handbook-HVAC Applications - 2023 | Chapter 34 §1.14 | Operations & maintenance tasks for commercial kitchen ventilation (CKV) systems | Annual + event-driven | Separate Tab