## 1. Cover & Guide
O&M Best Practice Checklist
BUILDING WATER QUALITY
A Preventive Maintenance Checklist for Facility Operators
AUDIENCE
Facility maintenance staff, building operators, plumbing and HVAC technicians, chief building engineers, water treatment providers, and facility leaders responsible for the operation and maintenance of domestic water and hydronic systems.
MINDSET
Proactive vs. Reactive. Healthy buildings rely on water systems that are routinely monitored, maintained, and documented. Water quality management is not a one-time design activity; it is an ongoing operations responsibility.
WHY
Building water quality directly impacts occupant safety, system reliability, equipment life, and operational risk. Poorly managed water systems can contribute to pathogen growth, inconsistent temperatures, corrosion, scaling, sediment buildup, odor, discoloration, and premature equipment failure. In most operating buildings, water quality issues are not caused by system design alone, but by gaps in operations and maintenance — including stagnant water conditions, inadequate flushing, failed recirculation, poor temperature control, unmanaged treatment chemistry, fouled strainers, sensor drift, and incomplete documentation. Routine, documented preventive maintenance is one of the most effective tools facility teams can use to protect occupants, improve system performance, extend equipment life, and preserve the long-term value of the building asset.
BACKGROUND & OBJECTIVES
The goals of this water quality preventive-maintenance checklist are to:
• | Provide facility staff with a practical schedule of monthly, quarterly, semi-annual, annual, and event-driven water quality checks.
• | Maintain domestic water, hydronic, cooling tower, and water treatment systems so that they continue to perform as intended.
• | Detect and correct common water quality failure modes such as stagnation, poor temperature control, failed recirculation, inadequate flushing, treatment drift, sediment buildup, corrosion, scaling, and sensor drift.
• | Reduce occupant exposure to waterborne pathogens, objectionable taste or odor, discoloration, and other water quality concerns.
• | Support water management program practices aligned with ASHRAE Standard 188, CDC water management guidance, ASHRAE Guideline 12, EPA drinking water guidance, and applicable plumbing / backflow requirements.
• | Support voluntary programs and rating systems related to building water quality, water safety, and public health, including WELL Water, LEED v5 water-related strategies, CDC Water Management Program guidance, and ASHRAE Standard 188.
• | Create a documented, auditable record of readings, findings, corrective actions, and responsible parties to support facility risk management and operational continuity.
• | Promote a 'good is better than perfect' culture: complete the basic checks every cycle, capture observations, and escalate abnormal findings before they become larger failures.
MEASURES OF SUCCESS
✓ | Hot water temperatures at representative fixtures remain within the facility target range.
✓ | Cold water temperatures remain within acceptable limits and do not trend toward conditions that increase microbial risk.
✓ | Time-to-temperature at distal fixtures is measured and trended to identify circulation or balancing issues.
✓ | Disinfectant residuals are measured at representative points and remain within the facility water management plan target range.
✓ | Low-use areas are flushed as scheduled; dead legs and low-flow areas are identified and addressed.
✓ | Recirculation pumps, mixing valves, strainers, filters, treatment equipment, and sensors are inspected and maintained on schedule.
✓ | Humidifiers, misters, air washers, evaporative coolers, cooling towers and open water systems are inspected, treated, cleaned, and documented as applicable.
✓ | Water heaters, storage tanks, piping insulation, backflow devices, and associated components are inspected and maintained.
✓ | Water management plan, testing records, complaint trends, and corrective actions are reviewed and updated at least annually.
✓ | Reduction in water quality complaints, unplanned plumbing service calls, and unresolved corrective actions year over year.
✓ | Hydronic system operates as designed, without premature failure due to corrosion or scaling, and maintains high energy efficiency.
HOW TO USE THIS CHECKLIST
Each frequency tab is a stand-alone inspection form. Complete the required checks, record dates and responsible personnel, and document findings or corrective actions. Use the Observations Log for abnormal readings, complaints, testing results, and follow-up items. This workbook should be used together with the facility Water Management Plan (WMP), manufacturer instructions, adopted codes, and local authority requirements.
PRIMARY SOURCES
– | ANSI/ASHRAE Standard 188 — Legionellosis: Risk Management for Building Water Systems.
– | ASHRAE Guideline 12 — Managing the Risk of Legionellosis Associated with Building Water Systems.
– | CDC — Developing a Water Management Program to Reduce Legionella Growth & Spread in Buildings: A Practical Guide to Industry Standards.
– | U.S. EPA — National Primary and Secondary Drinking Water Regulations and drinking water monitoring guidance.
– | International Plumbing Code (IPC) and applicable local plumbing / cross-connection control requirements.
– | ASSE product performance standards and manufacturer O&M requirements for mixing valves, backflow devices, water heaters, treatment equipment, and related components.
– | Facility Water Management Plan (WMP), treatment provider reports, commissioning records, BAS trend logs, and site-specific preventive maintenance procedures.
– | WELL Building Standard — Water concept and performance verification requirements; LEED v5 water-related strategies where applicable.
– | Cooling Technology Institute (CTI), AWWA guidance, and treatment-provider recommendations for cooling tower, storage, filtration, and water chemistry practices.
– | BSRIA BG 50/2021 - Water Treatment for Closed Heating and Cooling Systems
– | VDI 2035, Part 1: Guideline for Prevention of Damage in Water Heating Installations
WMP CLARIFICATION
WMP means Water Management Program or Water Management Plan. In this workbook, Facility WMP refers to the site-specific documented program/plan used to identify building-water-system hazards, control measures, monitoring locations, corrective actions, verification, validation, and recordkeeping responsibilities.

## 2. Monthly
Water Quality Preventive Maintenance — Monthly
Walk-through inspections to be performed monthly; document readings, abnormal observations, corrective actions, and follow-up.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
DOMESTIC WATER TEMPERATURE & CIRCULATION
1 | Hot water | Verify hot water temperatures in hot water heater storage tanks is set at 140 deg F (60 deg C) and thermostatic mixing valves are used to prevent scalding locally at sink and shower fixtures . | Vd | ASHRAE Standard 188-2021; CDC Water Management Program Toolkit; Facility WMP; manufacturer O&M requirements | WMP control measures, monitoring procedures, control limits, corrective actions, and recordkeeping; verify against Facility WMP hot-water temperature limits.
2 | Cold water | Verify cold water temperatures are 68 deg F (20 deg C) or less at the taps and shower heads. | Vd | CDC Water Management Program Toolkit; Facility WMP; domestic water system best practices | Water age, stagnation, and temperature-control considerations; confirm against Facility WMP cold-water temperature targets and trend logs.
3 | Distal fixtures | Check time to hot water at distal fixtures. | Vd | Facility domestic hot water performance criteria; commissioning / recommissioning procedures; Facility WMP | Time-to-temperature verification at distal fixtures; recirculation balancing, return-temperature, and occupant-use considerations.
4 | Disinfectant residual | Measure disinfectant residual at representative points in the building system. If no residual is detectable, contact your water provider. | Vd | EPA drinking water guidance; local utility water-quality information; Facility WMP / water treatment program | Disinfectant residual monitoring at representative points; compare to Facility WMP limits, utility targets, and treatment provider guidance.
MIXING, STAGNATION & LOW-USE FIXTURES
5 | Recirculation pumps | Confirm recirculation pumps are operating properly. | V | Manufacturer O&M manuals; Facility PM Program; Facility WMP | Pump status, alarm review, operating schedule, control sequence, and confirmation that recirculation is not disabled or overridden.
6 | Mixing valves | Inspect mixing valves for proper function and setpoint stability. | Vd | IPC; ASSE product performance standards; manufacturer O&M requirements; Facility WMP | Thermostatic mixing valve inspection, setpoint stability, scald protection, and downstream temperature verification.
7 | Low-use fixtures / areas | Check for low-use fixtures/areas and perform flushing as needed. | Vd | CDC Water Management Program Toolkit; Facility Flushing Plan; Facility WMP | Water age management, low-use outlet flushing, documentation of locations flushed, and corrective action if abnormal conditions are observed.
8 | Trap seals | Confirm trap seals are intact in infrequently used drains. | V | International Plumbing Code (IPC) Chapter 10; Facility plumbing preventive maintenance program | Trap seal inspection and protection to reduce sewer gas/odor risk; verify infrequently used floor drains and fixtures remain sealed.
9 | Dead legs | Inspect potable water piping changes that may have occurred in the building. Identify and eliminate any dead legs that exist due to plumbing modifications or improper installation. | V | ASHRAE Standard 188-2021; Guide 12-2023 CDC Water Management Program Toolkit; Facility WMP; manufacturer O&M requirements | ASHRAE Guideline 12-2023 §8 and §9 — eliminate dead-end piping, low-flow areas, and stagnant sections that may promote microbial growth.
WATER QUALITY OBSERVATIONS & WATER USING HVAC&R EQUIPMENT
10 | Taste / odor / discoloration | Inspect for unusual taste, odor, or discoloration complaints. | V | EPA Secondary Drinking Water Standards; occupant complaint tracking procedures; Facility WMP | EPA Secondary Drinking Water Standards — investigate taste, odor, discoloration, turbidity, sediment, and staining complaints; document corrective action.
11 | Evaporative Heat Rejection Equipment | Inspect evaporative heat rejection equipment (cooling towers, evaporative condensers, hybrid or adiabatic coolers or chillers, or other open water systems) for visible condition and treatment levels, if applicable. | V | ASHRAE Standard 188-2021; ASHRAE Guideline 12-2023; Cooling Technology Institute (CTI); water treatment provider guidance, manufacturer O&M guidance | ASHRAE 188-2021 §5.2 / Guideline 12-2023 §8 — open-water system inspection, biological growth, basin condition, drift control, and treatment verification.
12 | Water Chemistry | Monitor pH levels, Conductivity values, dissolved Oxygen, and biocide levels, top up inhibitor and/or biocide and/or pH solution if necessary. | V | BSRIA Guide 50 (for chemically inhibited systems), VDI 2050 (for non-chemically inhibited systems). Or similar in North America. | BSRIA BG 50 — water chemistry control limits for closed-loop systems; VDI 2050 — corrosion, scaling, and conductivity management.
13 | Humidification Equipment | Ensure equipment with automatic drain-down cycles are purging standing water at least once every 24 hours to prevent stagnation. Utilize distilled, demineralized, or reverse osmosis (RO) water to minimize mineral deposits that harbor microbes. Check that water temperatures are maintained outside the 77 deg F - 113 deg F (25 deg C-45 deg C) range to inhibit Legionella bacteria growth. | Vd | ASHRAE Standard 188-2021; Guide 12-2023 CDC Water Management Program Toolkit; Facility WMP; manufacturer O&M requirements | Guideline 12-2023 §9.3 — eliminate dead-end piping, low spots, and areas susceptible to stagnation during shutdown.
14 | Produce and Recreational Misters | For produce misters check integrity of pipe insulation to maintain water temperatures outside the Legionella growth range. Avoid stagnation by running regularly or draining when not in use. Drain and clean the reservoir regularly if recreational misting equipment has one. Use an EPA approved disinfectant appropriate for the system. | Vd | ASHRAE Standard 188-2021; Guide 12-2023 CDC Water Management Program Toolkit; Facility WMP; manufacturer O&M requirements | Guideline 12-2023 §9 — minimize stagnation and maintain water quality in aerosol-generating water systems.
15 | Evaporative Air Coolers, Air Washers | Unit shall have a fully drainable sump with a high level alarm. Sumps shall be sized to hold all returned water when pumps are shut off. No water carry over through sufficient sizing of the system or using a mist eliminator. When mist eliminators are used, the captured water shall be returned to the evaporative cooler sump. Bleed off shall be controlled by conductivity controllers | V | ASHRAE Standard 188-2021; Guide 12-2023; proposed ASHRAE Standard 191 | Guideline 12-2023 §8 / proposed ASHRAE 191 — inspect sump condition, drift eliminators, strainers, and visible biological growth.
Type Codes: | V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)

## 3. Quarterly
Water Quality Preventive Maintenance — Quarterly
Quarterly tasks add a closer review of treatment data, sensors, trends, backflow observations, and open water systems.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
TREATMENT PERFORMANCE & WATER QUALITY REVIEW
1 | Treatment provider report | Review quarterly water-treatment service reports, action items, and chemistry trends. | Vd | Water treatment provider reports; Facility WMP; ASHRAE Standard 188-2021; CDC Toolkit | Review control limits, residuals, pH/conductivity trends, treatment recommendations, corrective actions, and open service items.
2 | Sensor verification | Verify calibration or reasonableness of temperature, conductivity, pH, ORP, and related sensors where installed. | Vd | Treatment provider guidance; BAS / controls documentation; sensor manufacturer O&M; Facility WMP | Reasonableness/calibration check for temperature, conductivity, pH, ORP, residual, and related monitoring devices; document drift.
3 | Water quality sample points | Confirm designated sample points remain accessible, labeled, and representative. | V | Facility WMP; CDC Toolkit; ASHRAE Standard 188-2021 | Verify representative sample points/control locations remain accessible, labeled, and appropriate for monitoring building-water-system risk.
4 | Trend review | Review three months of temperature, residual, complaints, and corrective-action trends. | Vd | Facility WMP; BAS trend logs; maintenance records; occupant complaint log | Quarterly trend review of temperatures, disinfectant residuals, complaints, microbial data when applicable, and corrective-action closure.
PUMPS, VALVES & COMPONENTS
5 | Domestic water pumps | Inspect booster, recirculation, and transfer pumps for leaks, abnormal noise, vibration, or alarms. | V | Manufacturer O&M manuals; Facility PM Program | CDC Water Management Program Toolkit — verify monitoring records, flushing activities, and corrective action documentation.
6 | Valves and controls | Exercise or inspect representative isolation, balancing, and control valves. | V | Manufacturer O&M manuals; Facility PM Program | Valve inspection, balancing, and operability verification procedures
7 | Backflow devices | Visually inspect accessible backflow preventers for leakage, discharge, missing tags, or obvious damage. | V | International Plumbing Code (IPC) Chapter 6; local AHJ requirements; cross-connection control program | Visual inspection of accessible backflow assemblies; verify certification status is tracked for annual testing by qualified personnel.
WATER USING HVAC&R EQUIPMENT
8 | Cooling tower basin/Air handler Condensate drain pan | Inspect pan/basin, fill, drift eliminators, strainers, and visible biological growth. | V | ASHRAE Standard 188-2021; ASHRAE Guideline 12-2023; CTI guidance; treatment provider guidance | Cooling tower/open-water inspection: basin, fill, drift eliminators, strainers, biological growth, treatment status, and service recommendations. Air handler condensate drain pans a
9 | Humidification Equipment | Regularly remove mineral buildup, as scale acts as a breeding ground for bacteria. For larger systems, use EPA-registered microbicides to kill mold and bacteria. | Vd | ASHRAE Standard 188-2021; ASHRAE Guideline 12-2023; CDC Water Management Program Toolkit; Facility WMP; manufacturer O&M requirements | Scale build up increases over time. Regular maintenance minimizes effort to maintain safe condition and proper functionality
10 | Microbial testing review | Review bacteria / Legionella results if included in the water management program. | Vd | Facility WMP; ASHRAE Guideline 12-2023; treatment provider guidance; local health department guidance when applicable | Review microbial results, action levels, response procedure, retesting, remediation, and documentation requirements where included in the WMP.
Type Codes: | V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)

## 4. Semi-Annual
Water Quality Preventive Maintenance — Semi-Annual
Semi-annual tasks focus on water quality profiling, treatment adjustment, distribution components, and trend review.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
WATER QUALITY PROFILE & TREATMENT
1 | Water quality profile | Test and record full water quality profile, such as pH, hardness, turbidity, iron, manganese, and other site-specific parameters. | Vd | EPA drinking water regulations and secondary standards; AWWA water quality guidance; water treatment provider recommendations; Facility WMP | Profile may include pH, hardness, alkalinity, turbidity, iron, manganese, disinfectant residual, conductivity, and other site-specific parameters.
2 | Treatment program | Review and adjust water treatment program, including chemical feed, filtration, softening, or supplemental treatment as applicable. | Vd | Water treatment provider guidance; Facility water-chemistry program; manufacturer O&M requirements; Facility WMP | Review chemical feed, filtration, softening, corrosion/scale control, inhibitor levels, and treatment control ranges/action levels.
3 | Strainers, filters, screens | Inspect and clean strainers, filters, and screens. | Vd | Manufacturer O&M manuals; Facility PM Program; treatment provider recommendations | Inspect and clean strainers, filters, screens, separators, and related components; note pressure drop, debris, fouling, and cleaning frequency.
DISTRIBUTION SYSTEM COMPONENTS
4 | Water heaters / storage tanks | Inspect water heaters, storage tanks, and associated components. | Vd | Manufacturer O&M requirements; domestic hot-water maintenance program; Facility WMP; ASHRAE Guideline 12-2023 | Guideline 12-2023 §8 and §9 — inspect system cleanliness, treatment effectiveness, and areas prone to stagnation.
5 | Piping insulation | Verify insulation condition on hot and cold water piping. | V | ASHRAE energy-efficiency and condensation-control best practices; Facility PM Program; manufacturer insulation requirements | Inspect hot and cold-water piping insulation for damage, missing sections, condensation, heat gain/loss, and impacts on temperature stability.
6 | Dead legs / low-flow areas | Inspect system for dead legs or low-flow areas. | Vd | CDC Toolkit; Facility Water Age Management Plan; Facility WMP; record drawings / renovation closeout documents | Identify dead legs, low-flow branches, abandoned piping, and changed-use areas; update flushing plan and corrective-action list.
7 | Circulation Pump | Inspect propeller and pump chamber for any corrosion residual build up. | Vd | Facility PM Program; manufacturer maintenance requirements | Inspect visually for any corrosion or residual sediment on pump chamber or around the propeller, check pump energy performance as indicator.
RECORDS & TREND REVIEW
8 | Backflow prevention | Inspect backflow prevention devices visually. | V | International Plumbing Code (IPC) Chapter 6; local AHJ requirements; cross-connection control program | Visual backflow inspection plus certification-status check; annual testing/certification remains per local requirements and qualified tester.
9 | Complaint / maintenance trends | Review trends in occupant complaints or maintenance records. | Vd | Facility complaint tracking process; work order records; Facility WMP; water treatment provider service reports | Review recurring complaints, maintenance events, treatment excursions, sediment/odor/color issues, and corrective-action effectiveness.
Type Codes: | V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)

## 5. Annual
Water Quality Preventive Maintenance — Annual
Annual tasks validate the overall water management program, domestic water system operation, backflow compliance, and stagnation risk management.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
WATER MANAGEMENT PROGRAM
1 | Domestic water system review | Perform comprehensive system review of domestic water system design and operation. | Vd | Facility WMP; domestic water system assessment procedures; commissioning / record drawings; CDC Toolkit | Annual operational review of system layout, flow paths, process diagrams, control points, building-use changes, and high-risk areas.
2 | Water management plan | Review and update water management plan, if applicable. | Vd | ASHRAE Standard 188-2021; CDC Water Management Program Toolkit; Facility WMP | Annual review of WMP team, system description, process flow diagrams, hazard analysis, control measures, monitoring, corrective actions, verification, and documentation.
3 | Documentation update | Document findings and update maintenance procedures as needed. | Vd | Facility Preventive Maintenance Documentation Program; Facility WMP; CDC Toolkit | Document annual findings, update PM procedures, revise flushing/testing schedules, assign corrective actions, and close completed items.
SYSTEM PERFORMANCE VALIDATION
4 | Backflow certification | Test and certify backflow prevention devices, per local requirements. | Vd | International Plumbing Code (IPC) Chapter 6; local AHJ requirements; certified backflow testing requirements | CDC Toolkit / Facility WMP — verify annual review, corrective actions, and validation activities are documented.
5 | Microbial testing | Conduct microbial testing, such as Legionella, where required or appropriate. | Vd | ASHRAE Guideline 12-2023; Facility Legionella response plan; local health department guidance; Facility WMP | Microbial testing where required or appropriate; document action levels, results, notifications, retesting, remediation, and validation.
6 | Water heaters / storage tanks | Clean and inspect water heaters and storage tanks. | Vd | Manufacturer O&M manuals; Facility PM Program; Facility WMP; ASHRAE Guideline 12-2023 | Annual cleaning/inspection of heaters and tanks; sediment removal, corrosion review, insulation/access check, valves, and temperature-control components.
7 | Recirculation system | Verify performance of recirculation system, including balancing, controls, and efficiency. | Vd | Domestic hot-water performance verification procedures; controls contractor documentation; Facility WMP | Annual recirculation performance review: balancing, return temperatures, pump schedules, alarms, controls, efficiency, and distal-fixture results.
INFRASTRUCTURE & STAGNATION RISK
8 | Corrosion / scaling / material degradation | Inspect overall system for corrosion, scaling, or material degradation. | Vd | Facility asset management program; corrosion monitoring guidance; treatment provider reports; AWWA guidance | Annual review for corrosion, scaling, material degradation, discoloration sources, leaks, deposits, and capital renewal needs.
9 | System sizing / usage patterns | Review system sizing and usage patterns to identify opportunities to reduce stagnation. | Vd | Facility operational review; occupancy and usage trend analysis; CDC Toolkit; Facility WMP | Review fixture usage, vacant/low-use areas, sizing versus demand, water age, low-flow branches, and stagnation-reduction opportunities.
Type Codes: | V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)

## 6. Multi-Year & As-Required
Water Quality Preventive Maintenance — Multi-Year & As-Required
Multi-year and event-driven tasks that require deeper assessment, recommissioning, response procedures, or specialized water quality review.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
EVERY 2–3 YEARS
1 | Pipe condition assessment | Assess representative piping for corrosion, scaling, erosion, tuberculation, discoloration sources, or biofilm concerns when age or symptoms indicate risk. | Vd | Facility assessment program; treatment provider guidance; asset management records; AWWA corrosion/scale guidance | Deeper condition assessment for corrosion, scaling, erosion, tuberculation, biofilm concerns, discoloration sources, and capital planning.
2 | Control sequence review | Review domestic hot-water generation, recirculation, mixing, and treatment control sequences. | Vd | Controls contractor documentation; Facility WMP; manufacturer O&M; commissioning / recommissioning procedures | Review hot-water generation, recirculation, mixing, treatment controls, alarms, trend logs, setpoint stability, and sequences of operation.
AS REQUIRED / EVENT-DRIVEN
3 | Long-term sampling plan review | Reevaluate sampling locations, frequency, and parameters based on building changes and trend data. | V | Facility WMP; CDC Toolkit; ASHRAE Standard 188-2021 | ASHRAE 188-2021 §5 and Guideline 12 — reassess system risk following renovations, piping modifications, or operational changes.
4 | Positive Legionella or microbial result | Follow written response plan for notification, retesting, remediation, and documentation. | Vd | Facility WMP; ASHRAE Guideline 12-2023; local health department guidance; treatment provider guidance | Follow written response plan for positive Legionella/microbial results, including notification, risk assessment, remediation, retesting, and documentation.
5 | Major renovation or recommissioning | Flush, clean, disinfect, and document systems affected by construction, outage, or recommissioning. | Vd | CDC Toolkit; Facility WMP; commissioning / closeout procedures; local utility guidance | Return-to-service procedures after renovation, shutdown, outage, or recommissioning: flush, clean, disinfect, verify residuals, and document.
6 | Water service interruption | Implement restart, flushing, and testing procedures after loss of water service or pressure. | Vd | Facility WMP; local utility guidance; public health guidance; water treatment provider guidance | Restart after loss of service/pressure: flushing, residual verification, temperature checks, sampling if required, and corrective-action documentation.
Type Codes: | V = Verify (visual inspection / BAS data, no calibrated tools) ¦ Vd = Validate (calibrated tools, qualified technician)

## 7. Observations Log
Additional Water Quality Observations & Corrective Action Log
Use this log to record water-quality concerns, testing results, abnormal readings, complaints, field observations, corrective actions, and follow-up items discovered outside the routine checklist tasks.
Date | Time | Location / Room | Equipment / System | Observation / Concern | Level of Concern | Tested? | Measurement / Reading | Source / Reference | Action Taken / Next Steps | Owner | Closed Date

## 8. Common Observations
Common Observations and Path Forward
This indicates some common issues that can be observed and the potential path forward towards resolution. Please know that this information is captured in the proactive checklists and will be checked accordingly.
Common Negative Observations | Technical Description | Metric(s) | Considerations | Next Steps / Remediation
Water temp is inconsistent | Hot Water delivery / temp control issues - increases pathogen risk | °F (delivery temp), time to temperature, temperature stability | System design (recirculation vs. dead legs), pipe lengths, pipe sizing, insulation, fixture type, control strategy | Evaluate recirculation design and balancing, verify setpoints, insulate piping, assess controls and mixing valves
Hot water is not hot enough or takes a long time to get hot | Temperature control and distribution issues increasing pathogen risk | Hot water temp (°F), time to temperature (sec), stability | Recirculation imbalance, long pipe runs, mixing valves, insulation | Maintain hot water ≥120°F (or per program), balance recirculation, verify mixing valves and controls
Water feels warmer than expected from cold tap | Cold water temperature too high, supporting microbial growth | Cold water temp (°F) | Ambient heat gain, pipe routing, low flow conditions | Maintain cold water ≤77°F, improve insulation, increase turnover
Water has an unusual taste, odor, or color | Chemical or biological degradation of water quality | pH, turbidity (NTU), iron/manganese (ppm), disinfectant residual | Source water variability, corrosion, biofilm, stagnation | Test water quality, flush system, evaluate corrosion control or treatment
Water tastes or smells strongly like chlorine | Elevated or noticeable disinfectant residual in potable water | Free chlorine (mg/L), total chlorine (mg/L) | Recent flushing, proximity to water main, low water age, temperature, occupant sensitivity, source water variability | Test chlorine levels at point of use and compare to acceptable ranges, confirm levels are within utility and health guidelines, adjust flushing practices if needed, consider point-of-use filtration where appropriate
Water appears rusty (brown, red, or orange color) | Particulate, corrosion byproducts, or entrained air | Turbidity (NTU), iron (ppm), particulate presence | Pipe condition, recent disturbances, water chemistry | Flush system, inspect piping, evaluate need for filtration or treatment
Water looks milky or cloudy | Entrained air or elevated turbidity affecting water clarity | Turbidity (NTU), visual observation (clears from bottom up vs. persists), dissolved gases | Recent maintenance or pressure changes, temperature differences, plumbing disturbances, source water conditions | Observe if water clears after standing (indicates air), measure turbidity at point of use, flush system if needed, investigate source or filtration if cloudiness persists
Water pressure seems inconsistent or weak | System imbalance or potential stagnation zones | Flow rate (gpm), pressure (psi) | Fixture demand, system design, partial blockages, low use areas | Evaluate system hydraulics, inspect for obstructions, improve circulation
Musty or sewer-like smells near sinks or drains | Trap seal loss or biological growth in drainage system | Trap seal depth, presence of biofilm, odor complaints | Dry traps, poor venting, infrequent use | Maintain trap seals, add trap primers, clean drains, improve venting
Concerns about “unsafe water” or health risk (especially in healthcare or high-risk settings) | Potential elevated microbial risk (e.g., Legionella) | Legionella testing (CFU/L), HPC | High-risk populations, aerosol-generating systems, water temperature, biofilm | Implement/verify water management plan per ASHRAE 188 and Guideline 12, perform testing and corrective actions

## 9. Standards Crosswalk
Water Quality Source & Standards Crosswalk
This crosswalk maps the requirements of ASHRAE Standard 188, ASHRAE Guideline 12, CDC guidance, IPC requirements, water treatment best practices, WELL Water concepts, and LEED v5 alignment items to the tabs in this workbook so a reviewer can confirm coverage.
Standard / Guidance | Section / Credit | Title / Topic | Frequency | Where in this Workbook
ASHRAE STANDARD 188-2021 — LEGIONELLOSIS RISK MANAGEMENT FOR BUILDING WATER SYSTEMS
ASHRAE 188-2021 | §5 | Applicability to building water systems | Ongoing | 5. Annual
ASHRAE 188-2021 | §6 | Building survey and hazard analysis | Annually | 5. Annual / 6. Multi-Year & As-Required
ASHRAE 188-2021 | §7 | Water Management Program (WMP) development and implementation | Ongoing / Annual | 2. Monthly / 3. Quarterly / 5. Annual
ASHRAE 188-2021 | §7.2 | Program team identification and responsibilities | Annually | 5. Annual
ASHRAE 188-2021 | §7.2.1 | Development / update of process flow diagrams | Annually | 5. Annual / 6. Multi-Year & As-Required
ASHRAE 188-2021 | §7.2.2 | Hazard analysis and control locations | Annually | 5. Annual / 6. Multi-Year & As-Required
ASHRAE 188-2021 | §7.2.3 | Control measures and monitoring procedures | Monthly / Ongoing | 2. Monthly / 3. Quarterly
ASHRAE 188-2021 | §7.2.4 | Corrective action procedures | As required | 5. Annual / 6. Multi-Year & As-Required
ASHRAE 188-2021 | §7.2.5 | Verification and validation procedures | Annually / As required | 5. Annual / 6. Multi-Year & As-Required
ASHRAE 188-2021 | §7.2.6 | Documentation and recordkeeping | Ongoing | All frequency tabs
ASHRAE 188-2021 | §7.3 | Building water system monitoring | Monthly / Quarterly | 2. Monthly / 3. Quarterly
ASHRAE 188-2021 | §7.4 | Response procedures for excursions and positive results | Event-driven | 5. Annual / 6. Multi-Year & As-Required
ASHRAE 188-2021 | §8 | Program review following changes to building use or system operation | Event-driven / Annual | 5. Annual / 6. Multi-Year & As-Required
ASHRAE GUIDELINE 12-2023 — MANAGING THE RISK OF LEGIONELLOSIS ASSOCIATED WITH BUILDING WATER SYSTEMS
ASHRAE Guideline 12-2023 | Potable water systems guidance | Domestic hot and cold water system management | Monthly / Annual | 2. Monthly / 4. Semi-Annual / 5. Annual
ASHRAE Guideline 12-2023 | Cooling tower and evaporative condenser guidance | Cooling tower inspection, cleaning, treatment, and aerosol control | Daily / Monthly / Semi-Annual | 2. Monthly / 3. Quarterly
ASHRAE Guideline 12-2023 | Temperature and operational control guidance | Water temperature management | Monthly / Annual | 2. Monthly / 5. Annual
ASHRAE Guideline 12-2023 | Water age / stagnation guidance | Water age and stagnation management | Monthly / Semi-Annual / Annual | 2. Monthly / 4. Semi-Annual / 5. Annual
ASHRAE Guideline 12-2023 | Corrective action and remediation guidance | Corrective action and remediation procedures | As required | 6. Multi-Year & As-Required
ASHRAE Guideline 12-2023 | Legionella testing and response guidance | Legionella testing and response | Annual / As required | 5. Annual / 6. Multi-Year & As-Required
CDC — DEVELOPING A WATER MANAGEMENT PROGRAM TOOLKIT
CDC Toolkit | Step 1 | Establish a WMP team | Annual | 5. Annual
CDC Toolkit | Step 2 | Describe building water systems using text and process flow diagrams | Annual | 5. Annual
CDC Toolkit | Step 3 | Identify areas where Legionella could grow and spread | Annual | 5. Annual / 6. Multi-Year & As-Required
CDC Toolkit | Step 4 | Decide where control measures should be applied and how to monitor them | Ongoing | 2. Monthly / 3. Quarterly
CDC Toolkit | Step 5 | Establish interventions when control limits are not met | Ongoing / As required | 6. Multi-Year & As-Required
CDC Toolkit | Step 6 | Ensure the program runs as designed and is effective | Annual / Ongoing | 5. Annual / 6. Multi-Year & As-Required
CDC Toolkit | Step 7 | Document and communicate all activities | Ongoing | All frequency tabs
CDC Toolkit | Flushing guidance | Low-use fixture flushing and water age management | Monthly | 2. Monthly / 4. Semi-Annual
CDC Toolkit | Building reopening / reduced occupancy guidance | Restart procedures after shutdown, reduced occupancy, or water-service interruption | Event-driven | 6. Multi-Year & As-Required
EPA / DRINKING WATER QUALITY GUIDANCE
EPA Drinking Water Regulations | Primary Drinking Water Standards | Regulated contaminant limits | Annual / As required | 5. Annual
EPA Secondary Drinking Water Standards | Secondary standards / aesthetic parameters | Aesthetic water quality guidance (taste, odor, color, staining, turbidity, iron, manganese) | Monthly / Semi-Annual / As required | 2. Monthly / 4. Semi-Annual
EPA Guidance | Disinfectant residual monitoring | Residual monitoring and distribution-system quality | Monthly | 2. Monthly / 3. Quarterly
EPA Guidance | Lead and copper rule considerations | Lead and copper management where applicable | Annual / As required | 5. Annual
EPA Guidance | Microbial monitoring considerations | Microbial monitoring where required or appropriate | Annual / As required | 5. Annual / 6. Multi-Year & As-Required
INTERNATIONAL PLUMBING CODE (IPC)
IPC 2024 | Chapter 4 | Fixture requirements and protection | Ongoing | 2. Monthly
IPC 2024 | Chapter 5 | Water heaters and hot water systems | Monthly / Annual | 2. Monthly / 5. Annual
IPC 2024 | Chapter 6 | Water supply and distribution systems | Ongoing | 2. Monthly / 3. Quarterly / 4. Semi-Annual / 5. Annual
IPC 2024 | Chapter 6 | Backflow prevention and cross-connection control | Quarterly / Semi-Annual / Annual | 3. Quarterly / 4. Semi-Annual / 5. Annual
IPC 2024 | Chapter 10 | Traps, interceptors, and trap seal protection | Monthly | 2. Monthly
IPC 2024 | Chapter 13 / Non-Potable provisions where adopted | Non-Potable water systems if applicable | Annual / As required | 5. Annual / 6. Multi-Year & As-Required
ANSI/ASHRAE/ACCA STANDARD 180-2018 — COMMERCIAL HVAC INSPECTION AND MAINTENANCE
ASHRAE 180-2018 | HVAC water treatment components | Treatment verification and maintenance | Monthly / Semi-Annual | 2. Monthly / 4. Semi-Annual
ASHRAE 180-2018 | Drain pans and condensate systems | Inspection and cleaning | Semi-Annual / As required | 4. Semi-Annual
ASHRAE 180-2018 | Cooling towers | Inspection, cleaning, and biological growth prevention | Monthly / Semi-Annual | 2. Monthly / 4. Semi-Annual
ASHRAE 180-2018 | Heat exchangers | Fouling, scaling, and operational inspection | Semi-Annual / Annual | 4. Semi-Annual / 5. Annual
ASHRAE 180-2018 | Sensors and controls | Functional verification and calibration | Quarterly / Annual | 3. Quarterly / 5. Annual
AWWA / WATER TREATMENT GUIDANCE
AWWA / Treatment Provider Guidance | Water quality testing procedures | Water quality profile testing and trend review | Semi-Annual / Annual | 4. Semi-Annual / 5. Annual
AWWA / Treatment Provider Guidance | Corrosion and scale management | Corrosion, scaling, and material degradation review | Annual | 5. Annual / 6. Multi-Year & As-Required
AWWA / Treatment Provider Guidance | Water storage tank inspection and cleaning | Storage tank sediment, corrosion, and cleaning review | Semi-Annual / Annual | 4. Semi-Annual / 5. Annual
AWWA / Treatment Provider Guidance | Treatment chemistry review | Chemical treatment, filtration, softening, and inhibitor review | Quarterly / Semi-Annual | 3. Quarterly / 4. Semi-Annual
WELL BUILDING STANDARD — WATER CONCEPT
WELL Water | Water Quality Indicators | Monitoring contaminants and aesthetic quality | Annual / Ongoing | 2. Monthly / 4. Semi-Annual / 5. Annual
WELL Water | Drinking Water Promotion | Access to clean drinking water and hydration support | Ongoing | 2. Monthly
WELL Water | Water Management | Building water management policies and procedures | Annual | 5. Annual
WELL Water | Moisture Management | Moisture and microbial growth prevention | Ongoing | 4. Semi-Annual / 5. Annual
WELL Water | Performance Verification | Testing, documentation, and ongoing performance verification | Annual / Multi-Year | 5. Annual / 6. Multi-Year & As-Required
LEED v5 — WATER EFFICIENCY / HEALTH & WELLNESS RELATED STRATEGIES
LEED v5 | Water Efficiency / water management policy alignment | Water management, metering, and performance-oriented operations | Ongoing / Annual | 5. Annual
LEED v5 | Enhanced Building Operations alignment | Preventive maintenance documentation and verification | Ongoing | All frequency tabs
LEED v5 | Occupant Health & Wellness alignment | Water quality and occupant comfort support | Ongoing | 2. Monthly / 5. Annual
FACILITY WATER MANAGEMENT PROGRAM (WMP)
Facility WMP | Temperature control procedures | Monthly monitoring and documentation | Monthly | 2. Monthly / 3. Quarterly / 5. Annual
Facility WMP | Flushing procedures | Water age management | Monthly | 2. Monthly / 4. Semi-Annual
Facility WMP | Corrective action tracking | Excursion response and closure documentation | Ongoing | 6. Multi-Year & As-Required
Facility WMP | Treatment program review | Chemical treatment and monitoring review | Quarterly / Semi-Annual | 3. Quarterly / 4. Semi-Annual
Facility WMP | Annual review | Program update and management review | Annual | 5. Annual
Facility WMP | Event response procedures | Shutdowns, outages, positive tests, recommissioning | Event-driven | 6. Multi-Year & As-Required

## 8. Cooling Tower (hidden)
Water Quality Preventive Maintenance - Cooling Tower
Operations and maintenance tasks for open water systems, cooling towers, treatment controls, cleaning, and microbial risk management.
Building / Site: |  |  |  | Inspector: |  |  | Period:
# | Topic / Equipment | Inspection / Maintenance Task | Type | Source / Reference | Standard Section / Clause | Status | Date Completed | Performed By (Initials) | Findings / Corrective Action
DAILY / EACH OPERATOR ROUND
1 | Tower operation | Verify tower is operating as intended with no unusual noise, drift, overflow, or visible fouling. | V | ASHRAE Standard 188-2021; ASHRAE Guideline 12-2023; manufacturer O&M; Facility WMP | Routine visible-condition check for drift, aerosols, overflow, unusual noise, fouling, and abnormal operation.
2 | Treatment controller | Check controller status, conductivity, pH / ORP if applicable, and alarms. | Vd | Treatment program; controller manufacturer O&M; Facility WMP; water treatment provider guidance | Verify conductivity, pH/ORP where used, feed status, alarms, blowdown, and control limits against treatment program.
3 | Chemical inventory | Verify chemicals are available, labeled, contained, and being fed as intended. | V | Treatment program; SDS; Facility safety procedures; chemical supplier guidance | Verify treatment chemicals are available, labeled, contained, compatible, safely stored, and feeding as intended.
ASHRAE 188-2021 §5.2 / CTI guidance — inspect cooling tower condition, basin cleanliness, drift eliminators, and treatment program performance.
4 | Basin and strainers | Inspect basin, strainers, fill, drift eliminators, and visible biological growth. | V | ASHRAE Standard 188-2021; ASHRAE Guideline 12-2023; CTI guidance; manufacturer O&M | Inspect basin, strainers, fill, drift eliminators, and visible biological growth; document cleaning needs and treatment deviations.
QUARTERLY
SEMI-ANNUAL / ANNUAL
5 | Treatment levels | Verify treatment levels and review service report recommendations. | Vd | Water treatment provider guidance; Facility WMP; ASHRAE Guideline 12-2023 | Review treatment levels, service recommendations, control limits, blowdown settings, corrective actions, and trend data.
6 | Microbiological results | Review microbiological testing results and corrective actions, if included in the program. | Vd | Facility WMP; ASHRAE Guideline 12-2023; treatment provider guidance; local health department guidance when applicable | Review microbiological results where included in program; action levels, response, retesting, remediation, and closure documentation.
7 | Cleaning and disinfection | Perform scheduled tower cleaning and disinfection. | Vd | ASHRAE Guideline 12-2023; treatment provider procedures; manufacturer O&M; Facility WMP | Scheduled cleaning and disinfection, including startup/shutdown procedures, basin cleaning, and post-service documentation.
8 | Drift eliminators / fill / distribution | Inspect distribution system, fill, drift eliminators, louvers, and access components for damage or fouling. | V | ASHRAE Guideline 12-2023; CTI guidance; manufacturer O&M | Inspect distribution system, fill, drift eliminators, louvers, and access components for fouling/damage impacting drift and aerosol control.
Note on A10: Original text: MONTHLY