## Main Compliance Page
Quick Links | Compliance Worksheet Instructions |  |  | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0) | [8 empty] | Select Version > | 2019 | 2019 | 5 | FALSE | 90.1-2010
| Throughout this form Fill in all YELLOW cells |  |  | Project Name:
Address:
| Click on the links below to go to each step/section |  |  | City: |  |  |  | State / Province: |  |  |  | ZIP:
[6 empty] | Name |  | Email Address |  |  |  | Telephone
|  |  |  | Designer: | [14 empty] | www.ashrae.org
|  | 90.1-2019 |  | Project Contact: | [14 empty] | www.ies.org
ALTERATIONS
Interior lighting alterations are determined on either step 6 - Building Area Method (9.5.1) page or step 7 - Space by Space Method (9.6.1) pages. Exterior lighting alterations are determined on step 9.
|  |  | No | Is this lighting installation an alteration (Yes/No)?
[16 empty] | Spaces must comply with Space by Space Method (Steps a, b, c & d) | Spaces must comply with 9.1.2 Alteration requirements
|  |  | No |  |  |  |  | By using the 9.1.2 Exceptions, step 8 - Space by Space Method must be used. See "SpxSp Compliance Details" for detailed compliance.
[16 empty] | Spaces must comply with Space by Space Method (Steps a, b, c & d) | Spaces must comply with 9.1.2 Alteration requirements
INTERIOR LIGHTING
[6 empty] | Space by Space |  | ◄ Select Compliance Method | [11 empty] | Interior Room and Exterior Area Schedule
0
[6 empty] | Total Lighting Power Allowance | Total Designed Lighting Power | Wattage Compliant? | Exit Sign Compliant? | Controls Compliant? |  | Alterations | Overall Compliance? |  |  | 9.1.2 Lighting Alterations For the alteration of any lighting system in an interior space, that space shall comply with the lighting power density (LPD) allowances of Section 9.5.1 or 9.6.1 and the control requirements of Section 9.4.1.1 (a), (b), (c), (d), (g), (h), and (i), as applicable to that space. Exception to 9.1.2 1. Alterations that involve 20% or less of the connected lighting load... 2. Lighting alterations that only involve replacement of lamps plus ballasts/drivers or only involve one-for-one luminaire replacement... 3. Routine maintenance or repair situations.
Building Area Not Used
|  |  | 9.6 Space by Space (SpxSp) |  |  | 0 | 0 | Not Used | Compliant | Not Used |  |  | Compliant
|  |  |  | 9.6.2a Decorative Lighting |  | 0 | 0 | Not Used |  | Not Used
|  |  |  | 9.6.2b Retail Lighting |  | 0 | 0 | Not Used |  | Not Used
|  |  |  | 9.6.3 Nonmandatory Controls |  | 0
EXTERIOR LIGHTING
[6 empty] | Total Lighting Power Allowance | Base allocated | Total Designed Lighting Power | Wattage Compliant? | Controls Compliant? |  | Alterations | Overall Compliance?
|  |  |  | Lighting Zone Base Allowance |  | 0 | [6 empty] | Not Used
|  |  |  | Tradable |  | 0 | 0 | 0 | Not Used | Not Used |  | Not Used
| Link to this tool on ASHRAE.com |  |  | Non Tradable |  | 0 | 0 | 0 | Not Used | Not Used |  | Not Used
|  |  |  | Lighting Zone |  | #N/A
Section 9.3 (only available using 2019 version)
[7 empty] | Total Lighting Power Allowance | Total Designed Lighting Power | Wattage Compliant? | Controls Compliant? |  | Alterations selected "Yes" above | Overall Compliance?
|  |  | Building Type > | 0
|  |  | Building Square footage > | 0 |  | Building | #VALUE! | 0 |  |  |  |  | #VALUE!
|  |  | Parking Garage Square footage > | 0 |  | Garage | #VALUE! | 0
[6 empty] | Interior Totals | #VALUE! | 0 | #VALUE! | Compliant
|  |  | Lighting Zone | 0 |  |  | Total Lighting Power Allowance | Total Designed Lighting Power | Wattage Compliant? | Controls Compliant? |  | Alterations selected "Yes" above | Overall Compliance?
|  |  |  | LPA |  | Base Used
|  |  | Base Allowance | 0
|  |  | Exterior | 0 |  | 0 | 0 | 0 | Not Compliant | Compliant |  |  | Not Compliant
|  |  | Façade | 0 |  | 0 | 0 | 0 | Not Compliant
POST INSTALLATION COMPLIANCE REQUIREMENTS
[6 empty] | Has 9.4.4 Functional Testing been completed? | No |  |  |  |  | Have 9.7 Submittals Requirements been met? | No
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! |  | #REF! | #REF! | Control Requirements
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | #REF! |  |  | #REF! |  |  |  | #REF! | #REF! | #REF! |  | #REF! | #REF!
ASHRAE/IES 90.1-2010 Lighting Compliance Documentation
| ASHRAE/IES 90.1-2016 Lighting Compliance Documentation | [16 empty] | #REF!
#REF!
#REF!
2
Note on A17: Click link to go to the Project information section (Name, Address and Contact information)
Note on A19: Click the link to select if the project is a building Alteration or New Construction
Note on A21: Click the link to go to the selection of Building Method Method or Space by Space Method for the interior lighting of this project
Note on A23: Click on this link to go to the Luminaire Schedule and enter the lights used on this project.
Note on A25: Click on this link to go to the Interior Room Schedule to enter the spaces on this project.
Note on A27: Click this link to go to the installed Interior Lighting page when using the Building Area Method and enter all of the planned lighting.
Note on A29: Click one of the links below to go to the Space by Space Method steps to enter all of the planned lighting.
Note on A31: Click this link to go to the Space by Space Method (step-a) which is for calculating the LPA and specifying RCR, spaces that have Retail or Decorative Lighting.
Note on A33: Click this link to go to the Space by Space Method (step-b) which is for specifying spaces and the luminaires in each room along with the required controls.
Note on A35: Click this link to go to the Space by Space Method (step-c) which is for specifying Decorative lighting.
Note on A37: Click this link to go to the Space by Space Method (step-d) which is for specifying Retail lighting.
Note on A41: Click on this link to go to the Exterior Room Schedule to enter the spaces on this project.
Note on A43: Click one of the links below to go to the installed Exterior Lighting pages and enter all of the planned lighting.
Top of Page
1 - Project Information
3 - Choose Interior Compliance Method
Building Area Method
Space-by Space Method
5 - Fill in Interior Room Schedule
4 - Fill in the Luminaire Schedule
6 - Building Area Method
2 - Alteration (yes/no)
8 - Fill in Exterior Area Schedule
7 - Space by Space Method
9 - Installed Exterior Lighting
2016 version
2019 version
SpxSp (step-a) - LPA
SpxSp (step-b) - Space/Control
SpxSp (step-c) - Decorative
SpxSp (step-d) - Retail
Tradable Exterior
Nontradable Exterior
SpxSp Compliance Details
Exterior Compliance Detials
10 - 9.3 Simplified Method (Interior)
11 - 9.3 Simplified Method (Exterior)
9.3 Simplified Details
10 - 9.3 Simplified Method (Interior)
11 - 9.3 Simplified Method (Exterior)

## SpxSp Compliance Details
| ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0) | [13 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
| 9.6 Space by Space Method Compliance Details | [53 empty] | FALSE
LPA Project Level
TRUE
[36 empty] | ALTERATION |  | Exceptions
| 9.6.1 |  |  | 9.6.2a Decorative |  |  | 9.6.2b Retail | [7 empty] | 8: 0; 10: 0; 11: 0; 13: 0; 14: 0; 16: 0; 17: 0; 19: Space Level; 22: FALSE; 24: FALSE; 32: 0; 33: 0
90.1-2019 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[17 empty] | 7 |  | 12 | 8 | [12 empty] | LPA |  |  | Exception #1 |  |  |  |  | Exception #2 |  |  |  |  | Exception pass | [8 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
Space Name | Allowed Watts | Watts Installed | Complies? | Allowed Watts | Watts Installed | Complies? | Allowed Watts | Watts Installed | Base Watts Used | Complies? | Control Requirements | What's Installed |  |  | Space Name | 90.1 Space Type | Square Feet |  | Allowed Watts | Allowed LPA |  | True Allowed Watts |  | "New" Watts | "BLANK" Watts | Quantity "New" and "BLANK" | Existing "Remains" watts | Existing "Removed" Watts | Quantity "Removed" | Existing Total | TOTAL "Installed" |  | Designed LPD | LPA Pass/ Fail |  | 20% | 20% Pass/ Fail | Wattage same or lower | Overall |  | 1 for 1 | LPA | Overall |  | Exception Pass/ Fail | Watts Designed | True Allowed Watts |  | Complies? |  | Control Requirements | 0 |  | What's Installed | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75
[14 empty] | 1 | [37 empty] | 0 | 1 | [51 empty] | a b c d
[14 empty] | 2 | [37 empty] | 0 | 2 | [51 empty] | a b c d
[14 empty] | 3 | [37 empty] | 0 | 3 | [51 empty] | a b c d
[14 empty] | 4 | [37 empty] | 0 | 4 | [51 empty] | a b c d
[14 empty] | 5 | [37 empty] | 0 | 5 | [51 empty] | a b c d
[14 empty] | 6 | [37 empty] | 0 | 6 | [51 empty] | a b c d
[14 empty] | 7 | [37 empty] | 0 | 7 | [51 empty] | a b c d
[14 empty] | 8 | [37 empty] | 0 | 8 | [51 empty] | a b c d
[14 empty] | 9 | [37 empty] | 0 | 9 | [51 empty] | a b c d
[14 empty] | 10 | [37 empty] | 0 | 10 | [51 empty] | a b c d
[14 empty] | 11 | [37 empty] | 0 | 11 | [51 empty] | a b c d
[14 empty] | 12 | [37 empty] | 0 | 12 | [51 empty] | a b c d
[14 empty] | 13 | [37 empty] | 0 | 13 | [51 empty] | a b c d
[14 empty] | 14 | [37 empty] | 0 | 14 | [51 empty] | a b c d
[14 empty] | 15 | [37 empty] | 0 | 15 | [51 empty] | a b c d
[14 empty] | 16 | [37 empty] | 0 | 16 | [51 empty] | a b c d
[14 empty] | 17 | [37 empty] | 0 | 17 | [51 empty] | a b c d
[14 empty] | 18 | [37 empty] | 0 | 18 | [51 empty] | a b c d
[14 empty] | 19 | [37 empty] | 0 | 19 | [51 empty] | a b c d
[14 empty] | 20 | [37 empty] | 0 | 20 | [51 empty] | a b c d
[14 empty] | 21 | [37 empty] | 0 | 21 | [51 empty] | a b c d
[14 empty] | 22 | [37 empty] | 0 | 22 | [51 empty] | a b c d
[14 empty] | 23 | [37 empty] | 0 | 23 | [51 empty] | a b c d
[14 empty] | 24 | [37 empty] | 0 | 24 | [51 empty] | a b c d
[14 empty] | 25 | [37 empty] | 0 | 25 | [51 empty] | a b c d
[14 empty] | 26 | [37 empty] | 0 | 26 | [51 empty] | a b c d
[14 empty] | 27 | [37 empty] | 0 | 27 | [51 empty] | a b c d
[14 empty] | 28 | [37 empty] | 0 | 28 | [51 empty] | a b c d
[14 empty] | 29 | [37 empty] | 0 | 29 | [51 empty] | a b c d
[14 empty] | 30 | [37 empty] | 0 | 30 | [51 empty] | a b c d
[14 empty] | 31 | [37 empty] | 0 | 31 | [51 empty] | a b c d
[14 empty] | 32 | [37 empty] | 0 | 32 | [51 empty] | a b c d
[14 empty] | 33 | [37 empty] | 0 | 33 | [51 empty] | a b c d
[14 empty] | 34 | [37 empty] | 0 | 34 | [51 empty] | a b c d
[14 empty] | 35 | [37 empty] | 0 | 35 | [51 empty] | a b c d
[14 empty] | 36 | [37 empty] | 0 | 36 | [51 empty] | a b c d
[14 empty] | 37 | [37 empty] | 0 | 37 | [51 empty] | a b c d
[14 empty] | 38 | [37 empty] | 0 | 38 | [51 empty] | a b c d
[14 empty] | 39 | [37 empty] | 0 | 39 | [51 empty] | a b c d
[14 empty] | 40 | [37 empty] | 0 | 40 | [51 empty] | a b c d
[14 empty] | 41 | [37 empty] | 0 | 41 | [51 empty] | a b c d
[14 empty] | 42 | [37 empty] | 0 | 42 | [51 empty] | a b c d
[14 empty] | 43 | [37 empty] | 0 | 43 | [51 empty] | a b c d
[14 empty] | 44 | [37 empty] | 0 | 44 | [51 empty] | a b c d
[14 empty] | 45 | [37 empty] | 0 | 45 | [51 empty] | a b c d
[14 empty] | 46 | [37 empty] | 0 | 46 | [51 empty] | a b c d
[14 empty] | 47 | [37 empty] | 0 | 47 | [51 empty] | a b c d
[14 empty] | 48 | [37 empty] | 0 | 48 | [51 empty] | a b c d
[14 empty] | 49 | [37 empty] | 0 | 49 | [51 empty] | a b c d
[14 empty] | 50 | [37 empty] | 0 | 50 | [51 empty] | a b c d
[13 empty] | Decorative | [32 empty] | 9.6.3 Nonmandatory Controls | 0 | [7 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
[55 empty] | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67
[53 empty] | 1 | [51 empty] | a b
[53 empty] | 2 | [51 empty] | a b
[53 empty] | 3 | [51 empty] | a b
[53 empty] | 4 | [51 empty] | a b
[53 empty] | 5 | [51 empty] | a b
[53 empty] | 6 | [51 empty] | a b
[53 empty] | 7 | [51 empty] | a b
[53 empty] | 8 | [51 empty] | a b
[53 empty] | 9 | [51 empty] | a b
[53 empty] | 10 | [51 empty] | a b
[53 empty] | 11 | [51 empty] | a b
[53 empty] | 12 | [51 empty] | a b
[53 empty] | 13 | [51 empty] | a b
[53 empty] | 14 | [51 empty] | a b
[53 empty] | 15 | [51 empty] | a b
[53 empty] | 16 | [51 empty] | a b
[53 empty] | 17 | [51 empty] | a b
[53 empty] | 18 | [51 empty] | a b
[53 empty] | 19 | [51 empty] | a b
[53 empty] | 20 | [51 empty] | a b
[53 empty] | 21 | [51 empty] | a b
[53 empty] | 22 | [51 empty] | a b
[53 empty] | 23 | [51 empty] | a b
[53 empty] | 24 | [51 empty] | a b
[53 empty] | 25 | [51 empty] | a b
[53 empty] | 26 | [51 empty] | a b
[53 empty] | 27 | [51 empty] | a b
[53 empty] | 28 | [51 empty] | a b
[53 empty] | 29 | [51 empty] | a b
[53 empty] | 30 | [51 empty] | a b
[53 empty] | 31 | [51 empty] | a b
[53 empty] | 32 | [51 empty] | a b
[53 empty] | 33 | [51 empty] | a b
[53 empty] | 34 | [51 empty] | a b
[53 empty] | 35 | [51 empty] | a b
[53 empty] | 36 | [51 empty] | a b
[53 empty] | 37 | [51 empty] | a b
[53 empty] | 38 | [51 empty] | a b
[53 empty] | 39 | [51 empty] | a b
[53 empty] | 40 | [51 empty] | a b
[53 empty] | 41 | [51 empty] | a b
[53 empty] | 42 | [51 empty] | a b
[53 empty] | 43 | [51 empty] | a b
[53 empty] | 44 | [51 empty] | a b
[53 empty] | 45 | [51 empty] | a b
[53 empty] | 46 | [51 empty] | a b
[53 empty] | 47 | [51 empty] | a b
[53 empty] | 48 | [51 empty] | a b
[53 empty] | 49 | [51 empty] | a b
[53 empty] | 50 | [51 empty] | a b
[13 empty] | Retail | [41 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
[55 empty] | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67
[53 empty] | 1 | [51 empty] | a b
[53 empty] | 2 | [51 empty] | a b
[53 empty] | 3 | [51 empty] | a b
[53 empty] | 4 | [51 empty] | a b
[53 empty] | 5 | [51 empty] | a b
[53 empty] | 6 | [51 empty] | a b
[53 empty] | 7 | [51 empty] | a b
[53 empty] | 8 | [51 empty] | a b
[53 empty] | 9 | [51 empty] | a b
[53 empty] | 10 | [51 empty] | a b
[53 empty] | 11 | [51 empty] | a b
[53 empty] | 12 | [51 empty] | a b
[53 empty] | 13 | [51 empty] | a b
[53 empty] | 14 | [51 empty] | a b
[53 empty] | 15 | [51 empty] | a b
[53 empty] | 16 | [51 empty] | a b
[53 empty] | 17 | [51 empty] | a b
[53 empty] | 18 | [51 empty] | a b
[53 empty] | 19 | [51 empty] | a b
[53 empty] | 20 | [51 empty] | a b
[53 empty] | 21 | [51 empty] | a b
[53 empty] | 22 | [51 empty] | a b
[53 empty] | 23 | [51 empty] | a b
[53 empty] | 24 | [51 empty] | a b
[53 empty] | 25 | [51 empty] | a b
[53 empty] | 26 | [51 empty] | a b
[53 empty] | 27 | [51 empty] | a b
[53 empty] | 28 | [51 empty] | a b
[53 empty] | 29 | [51 empty] | a b
[53 empty] | 30 | [51 empty] | a b
[53 empty] | 31 | [51 empty] | a b
[53 empty] | 32 | [51 empty] | a b
[53 empty] | 33 | [51 empty] | a b
[53 empty] | 34 | [51 empty] | a b
[53 empty] | 35 | [51 empty] | a b
[53 empty] | 36 | [51 empty] | a b
[53 empty] | 37 | [51 empty] | a b
[53 empty] | 38 | [51 empty] | a b
[53 empty] | 39 | [51 empty] | a b
[53 empty] | 40 | [51 empty] | a b
[53 empty] | 41 | [51 empty] | a b
[53 empty] | 42 | [51 empty] | a b
[53 empty] | 43 | [51 empty] | a b
[53 empty] | 44 | [51 empty] | a b
[53 empty] | 45 | [51 empty] | a b
[53 empty] | 46 | [51 empty] | a b
[53 empty] | 47 | [51 empty] | a b
[53 empty] | 48 | [51 empty] | a b
[53 empty] | 49 | [51 empty] | a b
[53 empty] | 50 | [51 empty] | a b
Compliance Main Page
Top of Page
Step 8a
Step 8c
Step 8d
Step 8b
Note on BE14: Michael lane: If Exception is used then the watts don't count towards the overall LPA compliance.

## Exterior Compliance Details
ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0)
9.4.2 Exterior Lighting Compliance Details
| 9.4.2 |  |  |  | #N/A
90.1-2019 | 0 | 0 | 0
Space Name | Allowed Watts | Watts Installed | Base Allocated | Complies? | Control Requirements | What's Installed
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
a b c d
Decorative
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
Retail
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
a b
Compliance Main Page
Top of Page
Tradable Exterior
Nontradable Exterior

## Luminaire Schedule
|  | Quick Links | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0) | [9 empty] | 30 |  |  | 0.8
Luminaire Schedule
[12 empty] | Line Voltage Track systems (fill in all yellow cells below for Line Voltage Track) | [8 empty] | Low Voltage Track (fill in yellow cells below for Low Voltage Track)
Exit Signs. Internally illuminated exit signs shall not exceed 5 W per face.
[6 empty] | Yes |  | Compliant
[12 empty] | specified luminaires and track length |  |  | system’s circuit breaker |  | Optional current-limiting device(s) |  |  | OR
|  |  |  | Type ID (enter a unique luminaire name) | Description (select from drop down list or enter your own) | Source |  | Watts per Luminaire (calculate track at right) |  | Total System Wattage | Track Type Calculated | TOTAL Installed Watts | TOTAL Track Length | Watts at 30W/ft min. | System Volts | TOTAL Breaker Amps | Current Limiter installed? | System Volts | TOTAL Limiter(s) Amps |  | TOTAL Transformer(s) Wattage
90.1-2019
[7 empty] | If using track lighting select from the dropdown list | [16 empty] | Installed Wattage | 30W/ft | Line Voltage Max | Circuit | current | Low Voltage |  |  | 0 | [8 empty] | New / Existing / Retrofit | Type ID | Description | Source | Watts per Luminaire |  | Total System Wattage
[9 empty] | 1 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Luminaire Schedule Instructions | [8 empty] | 2 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Throughout this form | [8 empty] | 3 |  |  | 120 | 8 |  | 120 | 15 | No |  |  |  |  | 0 | 0 | 120 | 240 | 240 | 1440 | 0 | 0 | 240 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fill in all yellow cells | [8 empty] | 4 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Missing infromation cells | [8 empty] | 5 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
White cells are calculated | [8 empty] | 6 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leave Blank | [8 empty] | 7 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 8 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 9 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 10 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Step 1: | [8 empty] | 11 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| The first step is to verify that all Exit Signs meet the < 5 watts per face requirement. Click on the hyperlink above to go directly to the Exit Sign checkoff. | [7 empty] | 12 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 13 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 14 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 15 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 16 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Fixture Types | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Step 2: | [8 empty] | 17 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Troffer (1x4) | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| The second step is to create your Luminaire Schedule. Click on the hyperlink below to go directly to the Luminaire Schedule. Once there fill in all YELLOW cells. | [7 empty] | 18 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Troffer (2x2) | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 19 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Troffer (2x4) | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 20 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | High Bay | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 21 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Low Bay | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 22 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Downlight (lensed) | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 23 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Downlight (open) | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 24 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Downlight (wall washer) | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 25 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pendant (direct / indirect) | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 26 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pendant (direct) | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 27 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pendant (indirect) | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 28 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Linear Industrial | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 29 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Strip | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 30 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Track | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 31 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wall Sconce | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 32 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Chandelier | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 33 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cove | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 34 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Task | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 35 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Parking Shoebox | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 36 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Façade Uplight | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 37 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Landscape | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 38 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wall Pack | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 39 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 40 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Track Types | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 41 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line Voltage (30W/lf) | 1 | < Enter Calculated Wattage | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 42 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line Voltage (circuit breaker) | 2 | < Enter Calculated Wattage | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 43 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line Voltage (current limiter) | 3 | < Enter Calculated Wattage | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 44 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Low Voltage (transformer wattage) | 4 | < Enter Calculated Wattage | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 45 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 46 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 47 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 48 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 49 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 50 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 51 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 52 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 53 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 54 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 55 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 56 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 57 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 58 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 59 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 60 | [7 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
[31 empty] | 1 | 0
[31 empty] | 2 | 0
[31 empty] | 3 | 0
[31 empty] | 4 | 0
[31 empty] | 5 | 0
[31 empty] | 6 | 0
[31 empty] | 7 | 0
[31 empty] | 8 | 0
[31 empty] | 9 | 0
[31 empty] | 10 | 0
[31 empty] | 11 | 0
[31 empty] | 12 | 0
[31 empty] | 13 | 0
[31 empty] | 14 | 0
[31 empty] | 15 | 0
[31 empty] | 16 | 0
[31 empty] | 17 | 0
[31 empty] | 18 | 0
[31 empty] | 19 | 0
[31 empty] | 20 | 0
[31 empty] | 21 | 0
[31 empty] | 22 | 0
[31 empty] | 23 | 0
[31 empty] | 24 | 0
[31 empty] | 25 | 0
[31 empty] | 26 | 0
[31 empty] | 27 | 0
[31 empty] | 28 | 0
[31 empty] | 29 | 0
[31 empty] | 30 | 0
[31 empty] | 31 | 0
[31 empty] | 32 | 0
[31 empty] | 33 | 0
[31 empty] | 34 | 0
[31 empty] | 35 | 0
[31 empty] | 36 | 0
[31 empty] | 37 | 0
[31 empty] | 38 | 0
[31 empty] | 39 | 0
[31 empty] | 40 | 0
[31 empty] | 41 | 0
[31 empty] | 42 | 0
[31 empty] | 43 | 0
[31 empty] | 44 | 0
[31 empty] | 45 | 0
[31 empty] | 46 | 0
[31 empty] | 47 | 0
[31 empty] | 48 | 0
[31 empty] | 49 | 0
[31 empty] | 50 | 0
[31 empty] | 51 | 0
[31 empty] | 52 | 0
[31 empty] | 53 | 0
[31 empty] | 54 | 0
[31 empty] | 55 | 0
[31 empty] | 56 | 0
[31 empty] | 57 | 0
[31 empty] | 58 | 0
[31 empty] | 59 | 0
[31 empty] | 60 | 0
Exit Sign
Create Luminaire Schedule
Compliance Main Page
Top of Page
Exit Sign
Luminaire
Exterior Room Schedule
Interior Room Schedule
Note on M15: If you are using track lighting it must comply with 9.1.4. Select the track type from the drop down and enter the wattage per 9.1.4. If using 9.1.4.c1, enter 30 in the Watts column. If using 9.1.4.c2, enter the VA rating of the circuit breaker and remember to use a quantity of 1 on the Compliance Worksheet. If using 9.1.4.c3, enter the VA rating of the current limiter and remember to use a quantity of 1 on the Compliance Worksheet. If using 9.1.4.d, enter the maximum transformer wattage and remember to use a quantity of 1 on the Compliance Worksheet.

## Int Room Schedule
| Quick Links | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0) | [25 empty] | HIDE | HIDE | HIDE | HIDE
Interior Room Schedule
[16 empty] | OFFSET('Interior Room Schedule'!$AD$10:$AG$59,0,1,'Interior Room Schedule'!$AD$8,1) | [7 empty] | OFFSET('Interior Room Schedule'!$AR$10:$AV$15,0,1,'Interior Room Schedule'!$AR$8,1) |  |  |  | Atrium LPA calculation
ALL LPA
|  | Use this table for the 2019 9.5.1 Building Area Method | [5 empty] | Use this table for the 2019 9.6.1 Space by Space Method
[28 empty] | 0.03 | 0.03 | 0.39 | <20'
[28 empty] | 0.03 | 0.03 | 0.48 | >=20' and <=40'
|  |  | FALSE | FALSE | Total Sq.ft. |  | Total LPA |  |  |  | Total Sq.ft. |  |  | Total LPA |  |  | 2 | 3 | 4 | 5 | [7 empty] | 0.02 | 0.02 | 0.6 | >40'
90.1-2019 |  |  |  |  | 0 |  | 0 |  |  |  | 0 |  |  | 0 | [14 empty] | 0.4 |  | base LPA
|  | Area ID | 9.5.1 Building Area Method "Building Type" |  | Enter Building Area (sq.ft) | W/sf.ft. Allowance | Watts Allowed | Space ID | 9.6.1 Space by Space Method "Space Type" | Optional Space Name | Enter Space Area (sq.ft) | Atrium Height (ft) | W/sf.ft. Allowance | Base LPA | 0 |  |  |  | SF | LPD |  |  | 0 | Space | Square feet | Allowed LPA | Allowed Watts | 2010 | 2016 | 2019
|  | 1 |  |  |  |  | 0 | 1 | [12 empty] | 1 | 1 | [5 empty] | 0 | 0 | 0
Room Schedule Instructions |  | 2 |  |  |  |  | 0 | 2 | [12 empty] | 2 | 2 | [5 empty] | 0 | 0 | 0
Throughout this form |  | 3 |  |  |  |  | 0 | 3 | [12 empty] | 3 | 3 | [5 empty] | 0 | 0 | 0
Fill in all yellow cells |  | 4 |  |  |  |  | 0 | 4 | [12 empty] | 4 | 4 | [5 empty] | 0 | 0 | 0
White cells are calculated |  | 5 |  |  |  |  | 0 | 5 | [12 empty] | 5 | 5 | [5 empty] | 0 | 0 | 0
|  | 6 |  |  |  |  | 0 | 6 | [12 empty] | 6 | 6 | [5 empty] | 0 | 0 | 0
[8 empty] | 7 | [12 empty] | 7 | [6 empty] | 0 | 0 | 0
[8 empty] | 8 | [12 empty] | 8 | [6 empty] | 0 | 0 | 0
If you are using the Building Area Method to comply with the Interior Power Allowance, select from the drop down your 9.5 Building Area type(s). Also fill in the square footage of each Building Area. | [7 empty] | 9 | [12 empty] | 9 | [6 empty] | 0 | 0 | 0
[8 empty] | 10 | [12 empty] | 10 | [6 empty] | 0 | 0 | 0
[8 empty] | 11 | [12 empty] | 11 | [6 empty] | 0 | 0 | 0
[8 empty] | 12 | [12 empty] | 12 | [6 empty] | 0 | 0 | 0
[8 empty] | 13 | [12 empty] | 13 | [6 empty] | 0 | 0 | 0
[8 empty] | 14 | [12 empty] | 14 | [6 empty] | 0 | 0 | 0
[8 empty] | 15 | [12 empty] | 15 | [6 empty] | 0 | 0 | 0
[8 empty] | 16 | [12 empty] | 16 | [6 empty] | 0 | 0 | 0
If you are using the Space by Space Method to comply with the Interior Power Allowance, select from the drop down your 9.6.1 Space type(s). Also fill in the square footage of each Building Area. | [7 empty] | 17 | [12 empty] | 17 | [6 empty] | 0 | 0 | 0
[8 empty] | 18 | [12 empty] | 18 | [6 empty] | 0 | 0 | 0
[8 empty] | 19 | [12 empty] | 19 | [6 empty] | 0 | 0 | 0
[8 empty] | 20 | [12 empty] | 20 | [6 empty] | 0 | 0 | 0
[8 empty] | 21 | [12 empty] | 21 | [6 empty] | 0 | 0 | 0
[8 empty] | 22 | [12 empty] | 22 | [6 empty] | 0 | 0 | 0
[8 empty] | 23 | [12 empty] | 23 | [6 empty] | 0 | 0 | 0
[8 empty] | 24 | [12 empty] | 24 | [6 empty] | 0 | 0 | 0
[8 empty] | 25 | [12 empty] | 25 | [6 empty] | 0 | 0 | 0
[8 empty] | 26 | [12 empty] | 26 | [6 empty] | 0 | 0 | 0
[8 empty] | 27 | [12 empty] | 27 | [6 empty] | 0 | 0 | 0
[8 empty] | 28 | [12 empty] | 28 | [6 empty] | 0 | 0 | 0
[8 empty] | 29 | [12 empty] | 29 | [6 empty] | 0 | 0 | 0
[8 empty] | 30 | [12 empty] | 30 | [6 empty] | 0 | 0 | 0
[8 empty] | 31 | [12 empty] | 31 | [6 empty] | 0 | 0 | 0
[8 empty] | 32 | [12 empty] | 32 | [6 empty] | 0 | 0 | 0
[8 empty] | 33 | [12 empty] | 33 | [6 empty] | 0 | 0 | 0
[8 empty] | 34 | [12 empty] | 34 | [6 empty] | 0 | 0 | 0
[8 empty] | 35 | [12 empty] | 35 | [6 empty] | 0 | 0 | 0
[8 empty] | 36 | [12 empty] | 36 | [6 empty] | 0 | 0 | 0
[8 empty] | 37 | [12 empty] | 37 | [6 empty] | 0 | 0 | 0
[8 empty] | 38 | [12 empty] | 38 | [6 empty] | 0 | 0 | 0
[8 empty] | 39 | [12 empty] | 39 | [6 empty] | 0 | 0 | 0
[8 empty] | 40 | [12 empty] | 40 | [6 empty] | 0 | 0 | 0
[8 empty] | 41 | [12 empty] | 41 | [6 empty] | 0 | 0 | 0
[8 empty] | 42 | [12 empty] | 42 | [6 empty] | 0 | 0 | 0
[8 empty] | 43 | [12 empty] | 43 | [6 empty] | 0 | 0 | 0
[8 empty] | 44 | [12 empty] | 44 | [6 empty] | 0 | 0 | 0
[8 empty] | 45 | [12 empty] | 45 | [6 empty] | 0 | 0 | 0
[8 empty] | 46 | [12 empty] | 46 | [6 empty] | 0 | 0 | 0
[8 empty] | 47 | [12 empty] | 47 | [6 empty] | 0 | 0 | 0
[8 empty] | 48 | [12 empty] | 48 | [6 empty] | 0 | 0 | 0
[8 empty] | 49 | [12 empty] | 49 | [6 empty] | 0 | 0 | 0
[8 empty] | 50 | [12 empty] | 50 | [6 empty] | 0 | 0 | 0
Building Area Method Installed Lighting
Create "Building Area Method" Interior Areas
Compliance Main Page
Create "Space by Space Method" Interior Spaces
Space by Space Method Installed Lighting
Link to "Building Area Method" Installed Lighting
Link to "Space by Space Method" Installed Lighting
Top of Page
Luminaire schedule
Note on J14: 'Select the 9.5.1 Building Area Method "Building Type" from the Drop Down list. Reference 90.1 Table 9.5.1.
Note on L14: Enter the square footage of each space in the cells below.
Note on R14: 'Select the 9.6.1 Space by Space Method "Space Type(s)" from the Drop Down list. Reference 90.1 Table 9.6.1.
Note on S14: Enter an optional room name. Eg: Classroom 102
Note on T14: Enter the square footage of each space in the cells below.
Note on U14: Enter the Atrium height in feet.

## Building Area Method
|  |  | Quick Links |  | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0) | [10 empty] | Complies?
[5 empty] | 9.5 Building Area Method for Interior Lighting | [5 empty] | No | Alteration
[11 empty] | 0 | Shift Column
[13 empty] | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  |  | Count |  | 9.4.1.1a Local Control | 9.4.1.1b Restricted to Manual ON | 9.4.1.1c Restricted to Partial Automatic ON | 9.4.1.1d Bilevel Lighting Control | 9.4.1.1e Automatic Daylight Controls for Sidelighting | 9.4.1.1f Automatic Daylight Controls for Toplighting | 9.4.1.1g Automatic Partial OFF | 9.4.1.1h Automatic Full OFF | 9.4.1.1i Scheduled Shutoff | 9.4.1.2b Garage | SUM
| 90.1-2019 | [6 empty] | Allowed Watts: | 0 |  |  |  | Lighting Controls
[8 empty] | TOTAL designed watts complies with allowance! : | 0 |  |  |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Compliant
| Building Area |  |  |  | Luminaire Type | Quantity | Source Type | Watts | Total Watts |  |  |  | 9.4.1.1a Local Control |  | 9.4.1.1b Restricted to Manual ON |  | 9.4.1.1c Restricted to Partial Automatic ON |  | 9.4.1.1d Bilevel Lighting Control |  | 9.4.1.1e Automatic Daylight Controls for Sidelighting |  | 9.4.1.1f Automatic Daylight Controls for Toplighting |  | 9.4.1.1g Automatic Partial OFF |  | 9.4.1.1h Automatic Full OFF |  | 9.4.1.1i Scheduled Shutoff |  | 9.4.1.2b Garage |  | Are Controls Complete?
| Select the Building Type | Space Type (this narrows down control requirements) |  |  | Select the Luminaire | Enter the Number of Luminaires or Linear Feet |  | Per Luminaire or Linear Foot
1 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | [33 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[34 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ''Building Area Method" Building Type |  | Lighting Power Allowance (Watts) | LPD Allowance (watts per sq.ft) |  | Building Area (sq.ft) |  |  | 0
| 0 |  |  |  |  | 0 |  | 0 | 0 | 0
| 0 |  |  |  |  | 0 |  | 0 | 0 | 0
| 0 |  |  |  |  | 0 |  | 0 | 0 | 0
| 0 |  |  |  |  | 0 |  | 0 | 0 | 0
| 0 |  |  |  |  | 0 |  | 0 | 0 | 0
| 0 |  |  |  |  | 0 |  | 0 | 0 | 0
|  | TOTAL: | 0 | [15 empty] | 0.6 | 0.6
Link to 9.4.2
Exit Sign Requirements
Top of Page
Interior Room Schedule
Compliance Main Page
Installed Interior Lighting
Controls
Luminaire schedule

## SpxSp (step-a)
|  | Quick Links |  |  |  | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0) | [9 empty] | Retail Area 1 | = the floor area for all products not listed in Retail Areas 2, 3, or 4 | [31 empty] | 9.4.1.2b Parking Lighting Power Reduction
[6 empty] | 9.6 Space by Space Method for Interior Lighting (step-a) | [9 empty] | Retail Area 2 | = the floor area used for the sale of vehicles, sporting goods, and small electronics | [7 empty] | 2010 | 1
[6 empty] | Lighting Power Allowance | [9 empty] | Retail Area 3 | = the floor area used for the sale of furniture, clothing, cosmetics, and artwork | [7 empty] | 2016 | 0.75 | [22 empty] | Lighting Power Reduction
[16 empty] | Retail Area 4 | = the floor area used for the sale of jewelry, crystal, and china | [7 empty] | 2019 | 0.75
| 90.1-2019 | [13 empty] | 0.75
This is Space by Space (step 8a) - Calculates the Allowed Watts
[39 empty] | #1 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
[5 empty] | Base (General) Lighting | [7 empty] | 9.6.2a Decorative Lighting |  |  | 9.6.2b Retail Lighting | [22 empty] | #2 | NA | NA | NA | NA | NA | NA | NA |  |  | NA | NA | NA | NA
[19 empty] | 0 | [19 empty] | ALT |  |  |  |  | NA | NA |  |  |  | NA | NA | NA | NA
[6 empty] | 0 | [5 empty] | 0 |  |  | 0 |  | 0 |  | 0 | 0 | [19 empty] | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 14
| Space |  |  |  |  | Space Area (sq.ft) | LPD Allow. (watts per sq.ft) | RCR Threshold | Leave blank for standard RCR or Enter Claculated RCR | RCR / Corridor factor | Maximum Base Power (Watts) | Allowed Base Power (Watts) | Will Decorative Lighting be installed (Yes, No)? | Enter the Decorative Area of each space (sq.ft) | Possible Decorative Watts | Will Retail Display Lighting be installed? | Retail Display Area of each space (sq.ft) | Retail Area Type? | Retail Area Display Allowed Watts | 9.6.3 Control Watts (determined in step-b) |  |  | # of Spaces listed on step-b |  | 9.6.3 |  | Atrium Space Height (ft) | Space | Space | Decorative | 0 |  | Allowed | Installed |  | Retail | 0 |  |  | Does Control comply with 9.4.1.1a "Local Control"? | Does Control comply with 9.4.1.1b "Restricted to Manual on"? | Does Control comply with 9.4.1.1c "Restricted to partial automatic on"? | Does Control comply with 9.4.1.1d "Bi-level lighting control"? | Does Control comply with 9.4.1.1e "Automatic daylight responsive controls for Sidelighting"? | Does Control comply with 9.4.1.1f "Automatic daylight responsive controls for Toplighting"? | Does Control comply with 9.4.1.1g "Automatic partial off (full off complies)"? | Does Control comply with 9.4.1.1h "Automatic full off"? | Does Control comply with 9.4.1.1i "Scheduled shutoff"? | 9.4.1.2b Parking Lighting Power Reduction | 9.4.1.2b Parking Vehicle Entrances | 9.4.1.2b Parking Daylighting Power Reduction | 9.4.1.3b Lighting Guest Rooms
1 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
2 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
3 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
4 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
5 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
6 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
7 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
8 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
9 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
10 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
11 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
12 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
13 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
14 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
15 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
16 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
17 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
18 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
19 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
20 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
21 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
22 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
23 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
24 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
25 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
26 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
27 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
28 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
29 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
30 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
31 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
32 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
33 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
34 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
35 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
36 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
37 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
38 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
39 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
40 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
41 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
42 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
43 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
44 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
45 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
46 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
47 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
48 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
49 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
50 | [9 empty] | 1 | 0 | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | #NUM! |  |  | 0 |  |  | #NUM!
|  |  | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
Click for Space by Space (step-c)
Click for RCR Calculator
Click for Space by Space (step-d)
Compliance Main Page
Top of Page
SpxSp Compliance Details
SpxSp (step-c) - Decorative
SpxSp (step-d) - Retail
SpxSp (step-b) - Space/Control
Note on L20: To calculate the Actual RCR of a space click on RCR Calculator above for help. Enter width for corridors.
Note on P20: If Decorative Lighting will be installed in addition to general lighting it must meet 9.6.2 Additional Interior Lighting Power and control requirements?
Note on Q20: Decorative area must be equal to or less than the Space Area.
Note on R20: If Cell below says "sq.ft. ERROR" you have entered a larger square footage than the space square footage. Please revise!
Note on V20: If Cell below says "sq.ft. ERROR" you have entered a larger square footage than the space square footage. Please revise!

## RCR Calculator
ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0)
RCR Calculator
RCR = 2.5 × Room Cavity Height × room perimeter length/room area
90.1-2019
|  | Length of the Room Perimeter | Area of the Room | Room Cavity Height | RCR
Room Geometry Adjustment. When using the space by space method, an adjustment of the space LPD is allowed for individual spaces where the Room Cavity Ratio (RCR) calculated for the empty room is documented to be greater than the RCR threshold for that space type shown in Table 9.6.1. Adjustment is entered in SpxSp (step-a)
Enter these three values:
Example:
[6 empty] | Length: | 40
[6 empty] | Area: | 80
[6 empty] | Workplane Height: | 2.5' | desktop
[6 empty] | Luminaires mounted at: | 9.5'
[6 empty] | Room Cavity Height*: | 7
[6 empty] | RCR: | 8.75
Where:
*Room Cavity Height = Luminaire mounting height – Workplane height
Compliance Main Page
Top of Page
SpxSp (step-a) - LPA

## SpxSp (step-b)
|  | Quick Links | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0) | [29 empty] | 9.6.3 Nonmandatory Controls | 1 | Manual, continuous dimming control or Programmable multi-level dimming control
|  |  | 9.6 Space by Space Method for Interior Lighting | [30 empty] | 2 | Programmable multi-level dimming control using programmable time scheduling
|  |  | Installed Interior Lighting | [30 empty] | 3 | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off capabilities. | [9 empty] | Controls
[34 empty] | 4 | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off operation, in combination with personal continuous dimming control of downlight illumination by workstation occupant.
[5 empty] | Allowed Watts | 0 | 0 | [26 empty] | 5 | Automatic continuous daylight dimming in secondary sidelighted areas when sidelighting effective aperture is greater than 0.3
|  |  | This is Space by Space (step 8b) - Installed Luminaire and Control Requirements |  |  |  |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16
| 90.1-2019 |  |  |  | Total DESIGNED wattage | 0 | FALSE | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  |  | Compliant
| Space |  | Luminaire Type | Quantity | Watts | System Watts | Column not used | 9.4.1.1a Local Control |  | 9.4.1.1b Restricted to Manual ON |  | 9.4.1.1c Restricted to Partial Automatic ON |  | 9.4.1.1d Bilevel Lighting Control |  | 9.4.1.1e Automatic Daylight Controls for Sidelighting |  | 9.4.1.1f Automatic Daylight Controls for Toplighting |  | 9.4.1.1g Automatic Partial OFF |  | 9.4.1.1h Automatic Full OFF |  | 9.4.1.1i Scheduled Shutoff |  | 9.4.1.2b Garage |  | 9.4.1.2c Garage |  | 9.4.1.2d Garage |  | 9.4.1.3b.2 Guest Room |  | 9.6.3 Nonmandatory Control (OPTIONAL) | [12 empty] | 9.4.1.1a Local Control | 9.4.1.1b Restricted to Manual on | 9.4.1.1c Restricted to partial automatic on | 9.4.1.1d Bi-level lighting control | 9.4.1.1e Automatic daylight controls for Sidelighting | 9.4.1.1f Automatic daylight controls for Toplighting | 9.4.1.1g Automatic partial off (full off complies) | 9.4.1.1h Automatic full off | 9.4.1.1i Scheduled shutoff | 9.4.1.2 Parking Garage Lighting Control | 9.4.1.2 Parking Garage Lighting Control | 9.4.1.2 Parking Garage Lighting Control | 9.4.1.3 Guest Room Lighting Control |  | SUM
[36 empty] | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | Count
[7 empty] | Leave cells below blank |  |  | one of these two controls must be included if ADD1 is listed below | [11 empty] | one of these two controls must be included if ADD2 is listed below
|  |  | Select from Drop Down of Luminaire Schedule | Enter the # of Luminaires or Tracks | [30 empty] | Are Controls Complete?
[5 empty] | Per Luminaire or Track | [34 empty] | Space | Control factor | Additional Watts
[44 empty] | BC |  |  | O | Q | S | U | W | Y | AA | AC | AE | AG |  |  |  |  | 13 | Col# | Col Name | Row #
1 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1 | A | 26
2 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2 | B | 27
3 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 3 | C | 28
4 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 4 | D | 29
5 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 5 | E | 30
6 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 6 | F | 31
7 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 7 | G | 32
8 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 8 | H | 33
9 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 9 | I | 34
10 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 10 | J | 35
11 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 11 | K | 36
12 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 12 | l | 37
13 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 13 | M | 38
14 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 14 | N | 39
15 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 15 | O | 40
16 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 16 | P | 41
17 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 17 | Q | 42
18 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 18 | R | 43
19 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 19 | S | 44
20 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 20 | T | 45
21 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 21 | U | 46
22 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 22 | V | 47
23 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 23 | W | 48
24 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 24 | X | 49
25 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 25 | Y | 50
26 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 26 | Z | 51
27 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 27 | AA | 52
28 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 28 | AB | 53
29 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | AC | 54
30 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 30 | AD | 55
31 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 31 | AE | 56
32 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 32 | AF | 57
33 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 33 | AG | 58
34 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 34 | AH | 59
35 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 35 | AI | 60
36 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 36 | AJ | 61
37 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 37 | AK | 62
38 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 38 | Al | 63
39 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 39 | AM | 64
40 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 40 | AN | 65
41 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 41 | AO | 66
42 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 42 | AP | 67
43 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 43 | AQ | 68
44 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 44 | AR | 69
45 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 45 | AS | 70
46 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 46 | AT | 71
47 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 47 | AU | 72
48 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 48 | AV | 73
49 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 49 | AW | 74
50 | [35 empty] | New |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 50 | AX | 75
[26 empty] | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51 | AY
[9 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | O: IF(SUM(AY17:AY66)>=$AW67,$AW67,SUM(AY17:AY66)) | [5 empty] | 52 | AZ
[62 empty] | 53 | BA
[62 empty] | 54 | BB
[62 empty] | 55 | BC
[62 empty] | 56 | BD
[62 empty] | 57 | BE
[62 empty] | 58 | BF
[62 empty] | 59 | BG
[62 empty] | 60 | BH
[62 empty] | 61 | BI
[62 empty] | 62 | BJ
[62 empty] | 63 | BK
[62 empty] | 64 | Bl
[62 empty] | 65 | BM
[62 empty] | 66 | BN
[62 empty] | 67 | BO
[62 empty] | 68 | BP
[62 empty] | 69 | BQ
[62 empty] | 70 | BR
[62 empty] | 71 | BS
[62 empty] | 72 | BT
[62 empty] | 73 | BU
[62 empty] | 74 | BV
[62 empty] | 75 | BW
[62 empty] | 76 | BX
[62 empty] | 77 | BY
[62 empty] | 78 | BZ
Compliance Main Page
Top of Page
go to to Luminaire section
go to to Controls section
go to to Alterations section (if applicable)
SpxSp Compliance Details
SpxSp (step-a) - LPA
SpxSp (step-c) - Decorative
SpxSp (step-d) - Retail

## SpxSp (step-c)
|  | Quick Links | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0)
9.6 Space by Space Method for Interior Lighting
9.6.2a Additional Interior Lighting - Decorative Lighting
| 90.1-2019 |  |  |  |  | Total Watts | Wattage | Controls
|  |  | This is Space by Space (step 8c) - Decorative Lighting |  | TOTAL: | 0 | Compliant | Compliant | [8 empty] | Col# | Col Name | Row #
| Space ID |  | Allowed Decorative Watts | Number of Luminaires or Linear Feet | Watts Per Luminaire or Linear Foot | Total Watts | Wattage | automatically controlled, separately from the general lighting | Notes |  | Controls Compliant |  |  |  |  | AC
[17 empty] | 1 | A | 17
1 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 2 | B | 18
2 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 3 | C | 19
3 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 4 | D | 20
4 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 5 | E | 21
5 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 6 | F | 22
6 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 7 | G | 23
7 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 8 | H | 24
8 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 9 | I | 25
9 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 10 | J | 26
10 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 11 | K | 27
11 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 12 | l | 28
12 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 13 | M | 29
13 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 14 | N | 30
14 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 15 | O | 31
15 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 16 | P | 32
16 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 17 | Q | 33
17 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 18 | R | 34
18 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 19 | S | 35
19 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 20 | T | 36
20 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 21 | U | 37
21 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 22 | V | 38
22 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 23 | W | 39
23 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 24 | X | 40
24 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 25 | Y | 41
25 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 26 | Z | 42
26 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 27 | AA | 43
27 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 28 | AB | 44
28 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 29 | AC | 45
29 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 30 | AD | 46
30 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 31 | AE | 47
31 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 32 | AF | 48
32 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 33 | AG | 49
33 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 34 | AH | 50
34 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 35 | AI | 51
35 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 36 | AJ | 52
36 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 37 | AK | 53
37 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 38 | Al | 54
38 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 39 | AM | 55
39 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 40 | AN | 56
40 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 41 | AO | 57
41 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 42 | AP | 58
42 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 43 | AQ | 59
43 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 44 | AR | 60
44 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 45 | AS | 61
45 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 46 | AT | 62
46 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 47 | AU | 63
47 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 48 | AV | 64
48 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 49 | AW | 65
49 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 50 | AX | 66
50 | [9 empty] | 0 | 0 |  | 0 | #N/A | 0 |  | 51 | AY
[11 empty] | Compliant |  | Compliant |  |  |  | 52 | AZ
[11 empty] | 0 | Compliant | 0 |  |  |  | 53 | BA
[17 empty] | 54 | BB
[17 empty] | 55 | BC
[17 empty] | 56 | BD
[17 empty] | 57 | BE
[17 empty] | 58 | BF
[17 empty] | 59 | BG
[17 empty] | 60 | BH
[17 empty] | 61 | BI
[17 empty] | 62 | BJ
[17 empty] | 63 | BK
[17 empty] | 64 | Bl
[17 empty] | 65 | BM
[17 empty] | 66 | BN
[17 empty] | 67 | BO
[17 empty] | 68 | BP
[17 empty] | 69 | BQ
[17 empty] | 70 | BR
[17 empty] | 71 | BS
[17 empty] | 72 | BT
[17 empty] | 73 | BU
[17 empty] | 74 | BV
[17 empty] | 75 | BW
[17 empty] | 76 | BX
[17 empty] | 77 | BY
[17 empty] | 78 | BZ
Compliance Main Page
Top of Page (Step 8c)
Luminaire Type
From Luminaire Schedule
SpxSp (step-a) - LPA
SpxSp (step-d) - Retail
SpxSp (step-b) - Space/Control
SpxSp Compliance Details

## SpxSp (step-d)
|  | Quick Links | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0)
9.6 Space by Space Method for Interior Lighting
9.6.2b Additional Interior Lighting - Retail Lighting
| 90.1-2019 | [5 empty] | Total Watts | Base Watts | Wattage | Controls
|  |  | This is Space by Space (step 8d) - Additional Retail Lighting |  | TOTAL: |  | 0 | 0 | Compliant | Compliant |  |  | Col# | Col Name | Row #
| Space ID |  | Retail Area (sf) | Number of Luminaires or Linear Feet | Watts Per Luminaire or Linear Foot | Retail Area Display Allowed Watts | Total Watts | Base Wattage used | Wattage | automatically controlled, separately from the general lighting | Base Remaining | AD |  |  |  |  | Controls Compliant
[13 empty] | 1 | A | 17
1 | [12 empty] | 2 | B | 18 | 0 | 0 |  | 0 | #N/A
2 | [12 empty] | 3 | C | 19 | 0 | 0 |  | 0 | #N/A
3 | [12 empty] | 4 | D | 20 | 0 | 0 |  | 0 | #N/A
4 | [12 empty] | 5 | E | 21 | 0 | 0 |  | 0 | #N/A
5 | [12 empty] | 6 | F | 22 | 0 | 0 |  | 0 | #N/A
6 | [12 empty] | 7 | G | 23 | 0 | 0 |  | 0 | #N/A
7 | [12 empty] | 8 | H | 24 | 0 | 0 |  | 0 | #N/A
8 | [12 empty] | 9 | I | 25 | 0 | 0 |  | 0 | #N/A
9 | [12 empty] | 10 | J | 26 | 0 | 0 |  | 0 | #N/A
10 | [12 empty] | 11 | K | 27 | 0 | 0 |  | 0 | #N/A
11 | [12 empty] | 12 | l | 28 | 0 | 0 |  | 0 | #N/A
12 | [12 empty] | 13 | M | 29 | 0 | 0 |  | 0 | #N/A
13 | [12 empty] | 14 | N | 30 | 0 | 0 |  | 0 | #N/A
14 | [12 empty] | 15 | O | 31 | 0 | 0 |  | 0 | #N/A
15 | [12 empty] | 16 | P | 32 | 0 | 0 |  | 0 | #N/A
16 | [12 empty] | 17 | Q | 33 | 0 | 0 |  | 0 | #N/A
17 | [12 empty] | 18 | R | 34 | 0 | 0 |  | 0 | #N/A
18 | [12 empty] | 19 | S | 35 | 0 | 0 |  | 0 | #N/A
19 | [12 empty] | 20 | T | 36 | 0 | 0 |  | 0 | #N/A
20 | [12 empty] | 21 | U | 37 | 0 | 0 |  | 0 | #N/A
21 | [12 empty] | 22 | V | 38 | 0 | 0 |  | 0 | #N/A
22 | [12 empty] | 23 | W | 39 | 0 | 0 |  | 0 | #N/A
23 | [12 empty] | 24 | X | 40 | 0 | 0 |  | 0 | #N/A
24 | [12 empty] | 25 | Y | 41 | 0 | 0 |  | 0 | #N/A
25 | [12 empty] | 26 | Z | 42 | 0 | 0 |  | 0 | #N/A
26 | [12 empty] | 27 | AA | 43 | 0 | 0 |  | 0 | #N/A
27 | [12 empty] | 28 | AB | 44 | 0 | 0 |  | 0 | #N/A
28 | [12 empty] | 29 | AC | 45 | 0 | 0 |  | 0 | #N/A
29 | [12 empty] | 30 | AD | 46 | 0 | 0 |  | 0 | #N/A
30 | [12 empty] | 31 | AE | 47 | 0 | 0 |  | 0 | #N/A
31 | [12 empty] | 32 | AF | 48 | 0 | 0 |  | 0 | #N/A
32 | [12 empty] | 33 | AG | 49 | 0 | 0 |  | 0 | #N/A
33 | [12 empty] | 34 | AH | 50 | 0 | 0 |  | 0 | #N/A
34 | [12 empty] | 35 | AI | 51 | 0 | 0 |  | 0 | #N/A
35 | [12 empty] | 36 | AJ | 52 | 0 | 0 |  | 0 | #N/A
36 | [12 empty] | 37 | AK | 53 | 0 | 0 |  | 0 | #N/A
37 | [12 empty] | 38 | Al | 54 | 0 | 0 |  | 0 | #N/A
38 | [12 empty] | 39 | AM | 55 | 0 | 0 |  | 0 | #N/A
39 | [12 empty] | 40 | AN | 56 | 0 | 0 |  | 0 | #N/A
40 | [12 empty] | 41 | AO | 57 | 0 | 0 |  | 0 | #N/A
41 | [12 empty] | 42 | AP | 58 | 0 | 0 |  | 0 | #N/A
42 | [12 empty] | 43 | AQ | 59 | 0 | 0 |  | 0 | #N/A
43 | [12 empty] | 44 | AR | 60 | 0 | 0 |  | 0 | #N/A
44 | [12 empty] | 45 | AS | 61 | 0 | 0 |  | 0 | #N/A
45 | [12 empty] | 46 | AT | 62 | 0 | 0 |  | 0 | #N/A
46 | [12 empty] | 47 | AU | 63 | 0 | 0 |  | 0 | #N/A
47 | [12 empty] | 48 | AV | 64 | 0 | 0 |  | 0 | #N/A
48 | [12 empty] | 49 | AW | 65 | 0 | 0 |  | 0 | #N/A
49 | [12 empty] | 50 | AX | 66 | 0 | 0 |  | 0 | #N/A
50 | [12 empty] | 51 | AY |  | 0 | 0 |  | 0 | #N/A
[13 empty] | 52 | AZ |  |  | Compliant |  | Compliant
[13 empty] | 53 | BA |  |  | 0 | Compliant | 0
[13 empty] | 54 | BB
[13 empty] | 55 | BC
[13 empty] | 56 | BD
[13 empty] | 57 | BE
[13 empty] | 58 | BF
[13 empty] | 59 | BG
[13 empty] | 60 | BH
[13 empty] | 61 | BI
[13 empty] | 62 | BJ
[13 empty] | 63 | BK
[13 empty] | 64 | Bl
[13 empty] | 65 | BM
[13 empty] | 66 | BN
[13 empty] | 67 | BO
[13 empty] | 68 | BP
[13 empty] | 69 | BQ
[13 empty] | 70 | BR
[13 empty] | 71 | BS
[13 empty] | 72 | BT
[13 empty] | 73 | BU
[13 empty] | 74 | BV
[13 empty] | 75 | BW
[13 empty] | 76 | BX
[13 empty] | 77 | BY
[13 empty] | 78 | BZ
Luminaire Type
From Luminaire Schedule
Compliance Main Page
Top of Page (Step 8d)
SpxSp (step-a) - LPA
SpxSp (step-b) - Space/Control
SpxSp Compliance Details
SpxSp (step-c) - Decorative

## Ext Area Schedule
| Quick Links | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0) | [5 empty] | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction
|  | Exterior Area Schedule | [5 empty] | LZ1 - Developed areas of national parks, state parks, forest land, and rural areas
LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas
|  |  |  | Select Appropriate Lighting Zone: | Select |  |  | LZ3 - All other areas
|  |  |  | Base Allowance: | 0 |  |  | LZ4 - High-activity commercial districts in major metropolitan areas as designated by the local jurisdiction | [10 empty] | Watts allowed if space is used |  |  | #REF!
90.1-2019 |  | 2019 | Tradable Exterior Areas |  |  | 0 | 2019 | NonTradable Exterior Areas |  |  | 0
|  | Space ID | Enter your Exterior Area Name | Select a Building Area Type from the Drop Down list | Enter Area (sq.ft.) | Watts Allowed | Space ID | Enter your Exterior Area Name | Select Building/Area Type from the Drop Down list | Enter Allowed Quantity | Watts Allowed |  | 0 | 9.4.3 Table Name | SF | Watts |  | Select | 0 |  | 0 |  | Select |  | 0 |  |  | 0 | SF | LPD |  | 0 | Name | SF | LPD
|  | 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | Tradable |  |  | 52 |  |  |  | 1 |  | Int | 1 |  |  |  | Interior
Area Schedule Instructions |  | 2 |  |  |  |  | 2 |  |  |  |  | 2 |  |  |  |  | Tradable |  |  | 53 |  |  |  | 2 |  |  | 2 |  |  |  | Interior
Throughout this form |  | 3 |  |  |  |  | 3 |  |  |  |  | 3 |  |  |  |  | Tradable |  |  | 54 |  |  |  | 3 |  |  | 3 |  |  |  | Interior
Fill in all yellow cells |  | 4 |  |  |  |  | 4 |  |  |  |  | 4 |  |  |  |  | Tradable |  |  | 55 |  |  |  | 4 |  |  | 4 |  |  |  | Interior
White cells are calculated |  | 5 |  |  |  |  | 5 |  |  |  |  | 5 |  |  |  |  | Tradable |  |  | 56 |  |  |  | 5 |  |  | 5 |  |  |  | Interior
|  | 6 |  |  |  |  | 6 |  |  |  |  | 6 |  |  |  |  | Tradable |  |  | 57 |  |  |  | 6 |  |  | 6 |  |  |  | Interior
|  | 7 |  |  |  |  | 7 |  |  |  |  | 7 |  |  |  |  | Tradable |  |  | 58 |  |  |  | 7 |  |  | 7 |  |  |  | Interior
|  | 8 |  |  |  |  | 8 |  |  |  |  | 8 |  |  |  |  | Tradable |  |  | 59 |  |  |  | 8 |  |  | 8 |  |  |  | Interior
Select either LZ0, LZ1, LZ2, LZ3 or LZ4 |  | 9 |  |  |  |  | 9 |  |  |  |  | 9 |  |  |  |  | Tradable |  |  | 60 |  |  |  | 9 |  |  | 9 |  |  |  | Interior
|  | 10 |  |  |  |  | 10 |  |  |  |  | 10 |  |  |  |  | Tradable |  |  | 61 |  |  |  | 10 |  |  | 10 |  |  |  | Interior
|  | 11 |  |  |  |  | 11 |  |  |  |  | 11 |  |  |  |  | Tradable |  |  | 62 |  |  |  | 11 |  |  | 11 |  |  |  | Interior
|  | 12 |  |  |  |  | 12 |  |  |  |  | 12 |  |  |  |  | Tradable |  |  | 63 |  |  |  | 12 |  |  | 12 |  |  |  | Interior
Go to the Tradable Exterior Areas table and enter an area name in the first column. Select a Building Area from the drop down in the second column. Enter the square footage of the exterior area. |  | 13 |  |  |  |  | 13 |  |  |  |  | 13 |  |  |  |  | Tradable |  |  | 64 |  |  |  | 13 |  |  | 13 |  |  |  | Interior
|  | 14 |  |  |  |  | 14 |  |  |  |  | 14 |  |  |  |  | Tradable |  |  | 65 |  |  |  | 14 |  |  | 14 |  |  |  | Interior
|  | 15 |  |  |  |  | 15 |  |  |  |  | 15 |  |  |  |  | Tradable |  |  | 66 |  |  |  | 15 |  |  | 15 |  |  |  | Interior
|  | 16 |  |  |  |  | 16 |  |  |  |  | 16 |  |  |  |  | Tradable |  |  | 67 |  |  |  | 16 |  |  | 16 |  |  |  | Interior
|  | 17 |  |  |  |  | 17 |  |  |  |  | 17 |  |  |  |  | Tradable |  |  | 68 |  |  |  | 17 |  |  | 17 |  |  |  | Interior
Go to the NonTradable Exterior Areas table and enter an area name in the first column. Select a Building Area from the drop down in the second column. Enter the square footage of the exterior area. |  | 18 |  |  |  |  | 18 |  |  |  |  | 18 |  |  |  |  | Tradable |  |  | 69 |  |  |  | 18 |  |  | 18 |  |  |  | Interior
|  | 19 |  |  |  |  | 19 |  |  |  |  | 19 |  |  |  |  | Tradable |  |  | 70 |  |  |  | 19 |  |  | 19 |  |  |  | Interior
|  | 20 |  |  |  |  | 20 |  |  |  |  | 20 |  |  |  |  | Tradable |  |  | 71 |  |  |  | 20 |  |  | 20 |  |  |  | Interior
|  | 21 |  |  |  |  | 21 |  |  |  |  | 21 |  |  |  |  | Tradable |  |  | 72 |  |  |  | 21 |  |  | 21 |  |  |  | Interior
|  | 22 |  |  |  |  | 22 |  |  |  |  | 22 |  |  |  |  | Tradable |  |  | 73 |  |  |  | 22 |  |  | 22 |  |  |  | Interior
|  | 23 |  |  |  |  | 23 |  |  |  |  | 23 |  |  |  |  | Tradable |  |  | 74 |  |  |  | 23 |  |  | 23 |  |  |  | Interior
|  | 24 |  |  |  |  | 24 |  |  |  |  | 24 |  |  |  |  | Tradable |  |  | 75 |  |  |  | 24 |  |  | 24 |  |  |  | Interior
|  | 25 |  |  |  |  | 25 |  |  |  |  | 25 |  |  |  |  | Tradable |  |  | 76 |  |  |  | 25 |  |  | 25 |  |  |  | Interior
|  | 26 |  |  |  |  | 26 |  |  |  |  | 26 |  |  |  |  | Tradable |  |  | 77 |  |  |  | 26 |  |  | 26 |  |  |  | Interior
|  | 27 |  |  |  |  | 27 |  |  |  |  | 27 |  |  |  |  | Tradable |  |  | 78 |  |  |  | 27 |  |  | 27 |  |  |  | Interior
|  | 28 |  |  |  |  | 28 |  |  |  |  | 28 |  |  |  |  | Tradable |  |  | 79 |  |  |  | 28 |  |  | 28 |  |  |  | Interior
|  | 29 |  |  |  |  | 29 |  |  |  |  | 29 |  |  |  |  | Tradable |  |  | 80 |  |  |  | 29 |  |  | 29 |  |  |  | Interior
|  | 30 |  |  |  |  | 30 |  |  |  |  | 30 |  |  |  |  | Tradable |  |  | 81 |  |  |  | 30 |  |  | 30 |  |  |  | Interior
|  | 31 |  |  |  |  | 31 |  |  |  |  | 31 |  |  |  |  | Tradable |  |  | 82 |  |  |  | 31 |  |  | 31 |  |  |  | Interior
|  | 32 |  |  |  |  | 32 |  |  |  |  | 32 |  |  |  |  | Tradable |  |  | 83 |  |  |  | 32 |  |  | 32 |  |  |  | Interior
|  | 33 |  |  |  |  | 33 |  |  |  |  | 33 |  |  |  |  | Tradable |  |  | 84 |  |  |  | 33 |  |  | 33 |  |  |  | Interior
|  | 34 |  |  |  |  | 34 |  |  |  |  | 34 |  |  |  |  | Tradable |  |  | 85 |  |  |  | 34 |  |  | 34 |  |  |  | Interior
|  | 35 |  |  |  |  | 35 |  |  |  |  | 35 |  |  |  |  | Tradable |  |  | 86 |  |  |  | 35 |  |  | 35 |  |  |  | Interior
|  | 36 |  |  |  |  | 36 |  |  |  |  | 36 |  |  |  |  | Tradable |  |  | 87 |  |  |  | 36 |  |  | 36 |  |  |  | Interior
|  | 37 |  |  |  |  | 37 |  |  |  |  | 37 |  |  |  |  | Tradable |  |  | 88 |  |  |  | 37 |  |  | 37 |  |  |  | Interior
|  | 38 |  |  |  |  | 38 |  |  |  |  | 38 |  |  |  |  | Tradable |  |  | 89 |  |  |  | 38 |  |  | 38 |  |  |  | Interior
|  | 39 |  |  |  |  | 39 |  |  |  |  | 39 |  |  |  |  | Tradable |  |  | 90 |  |  |  | 39 |  |  | 39 |  |  |  | Interior
|  | 40 |  |  |  |  | 40 |  |  |  |  | 40 |  |  |  |  | Tradable |  |  | 91 |  |  |  | 40 |  |  | 40 |  |  |  | Interior
|  | 41 |  |  |  |  | 41 |  |  |  |  | 41 |  |  |  |  | Tradable |  |  | 92 |  |  |  | 41 |  |  | 41 |  |  |  | Interior
|  | 42 |  |  |  |  | 42 |  |  |  |  | 42 |  |  |  |  | Tradable |  |  | 93 |  |  |  | 42 |  |  | 42 |  |  |  | Interior
|  | 43 |  |  |  |  | 43 |  |  |  |  | 43 |  |  |  |  | Tradable |  |  | 94 |  |  |  | 43 |  |  | 43 |  |  |  | Interior
|  | 44 |  |  |  |  | 44 |  |  |  |  | 44 |  |  |  |  | Tradable |  |  | 95 |  |  |  | 44 |  |  | 44 |  |  |  | Interior
|  | 45 |  |  |  |  | 45 |  |  |  |  | 45 |  |  |  |  | Tradable |  |  | 96 |  |  |  | 45 |  |  | 45 |  |  |  | Interior
|  | 46 |  |  |  |  | 46 |  |  |  |  | 46 |  |  |  |  | Tradable |  |  | 97 |  |  |  | 46 |  |  | 46 |  |  |  | Interior
|  | 47 |  |  |  |  | 47 |  |  |  |  | 47 |  |  |  |  | Tradable |  |  | 98 |  |  |  | 47 |  |  | 47 |  |  |  | Interior
|  | 48 |  |  |  |  | 48 |  |  |  |  | 48 |  |  |  |  | Tradable |  |  | 99 |  |  |  | 48 |  |  | 48 |  |  |  | Interior
|  | 49 |  |  |  |  | 49 |  |  |  |  | 49 |  |  |  |  | Tradable |  |  | 100 |  |  |  | 49 |  |  | 49 |  |  |  | Interior
|  | 50 |  |  |  |  | 50 |  |  |  |  | 50 |  |  |  |  | Tradable |  |  | 101 |  |  |  | 50 |  |  | 50 |  |  |  | Interior
[12 empty] | 51 | [11 empty] | 51 |  | Ext | 51 |  |  |  | Exterior
[12 empty] | 52 |  |  |  |  | Nontradable | [6 empty] | 52 |  |  | 52 |  |  |  | Exterior
[12 empty] | 53 |  |  |  |  | Nontradable | [6 empty] | 53 |  |  | 53 |  |  |  | Exterior
[12 empty] | 54 |  |  |  |  | Nontradable | [6 empty] | 54 |  |  | 54 |  |  |  | Exterior
[12 empty] | 55 |  |  |  |  | Nontradable | [6 empty] | 55 |  |  | 55 |  |  |  | Exterior
[12 empty] | 56 |  |  |  |  | Nontradable | [6 empty] | 56 |  |  | 56 |  |  |  | Exterior
[12 empty] | 57 |  |  |  |  | Nontradable | [6 empty] | 57 |  |  | 57 |  |  |  | Exterior
[12 empty] | 58 |  |  |  |  | Nontradable | [6 empty] | 58 |  |  | 58 |  |  |  | Exterior
[12 empty] | 59 |  |  |  |  | Nontradable | [6 empty] | 59 |  |  | 59 |  |  |  | Exterior
[12 empty] | 60 |  |  |  |  | Nontradable | [6 empty] | 60 |  |  | 60 |  |  |  | Exterior
[12 empty] | 61 |  |  |  |  | Nontradable | [6 empty] | 61 |  |  | 61 |  |  |  | Exterior
[12 empty] | 62 |  |  |  |  | Nontradable | [6 empty] | 62 |  |  | 62 |  |  |  | Exterior
[12 empty] | 63 |  |  |  |  | Nontradable | [6 empty] | 63 |  |  | 63 |  |  |  | Exterior
[12 empty] | 64 |  |  |  |  | Nontradable | [6 empty] | 64 |  |  | 64 |  |  |  | Exterior
[12 empty] | 65 |  |  |  |  | Nontradable | [6 empty] | 65 |  |  | 65 |  |  |  | Exterior
[12 empty] | 66 |  |  |  |  | Nontradable | [6 empty] | 66 |  |  | 66 |  |  |  | Exterior
[12 empty] | 67 |  |  |  |  | Nontradable | [6 empty] | 67 |  |  | 67 |  |  |  | Exterior
[12 empty] | 68 |  |  |  |  | Nontradable | [6 empty] | 68 |  |  | 68 |  |  |  | Exterior
[12 empty] | 69 |  |  |  |  | Nontradable | [6 empty] | 69 |  |  | 69 |  |  |  | Exterior
[12 empty] | 70 |  |  |  |  | Nontradable | [6 empty] | 70 |  |  | 70 |  |  |  | Exterior
[12 empty] | 71 |  |  |  |  | Nontradable | [6 empty] | 71 |  |  | 71 |  |  |  | Exterior
[12 empty] | 72 |  |  |  |  | Nontradable | [6 empty] | 72 |  |  | 72 |  |  |  | Exterior
[12 empty] | 73 |  |  |  |  | Nontradable | [6 empty] | 73 |  |  | 73 |  |  |  | Exterior
[12 empty] | 74 |  |  |  |  | Nontradable | [6 empty] | 74 |  |  | 74 |  |  |  | Exterior
[12 empty] | 75 |  |  |  |  | Nontradable | [6 empty] | 75 |  |  | 75 |  |  |  | Exterior
[12 empty] | 76 |  |  |  |  | Nontradable | [6 empty] | 76 |  |  | 76 |  |  |  | Exterior
[12 empty] | 77 |  |  |  |  | Nontradable | [6 empty] | 77 |  |  | 77 |  |  |  | Exterior
[12 empty] | 78 |  |  |  |  | Nontradable | [6 empty] | 78 |  |  | 78 |  |  |  | Exterior
[12 empty] | 79 |  |  |  |  | Nontradable | [6 empty] | 79 |  |  | 79 |  |  |  | Exterior
[12 empty] | 80 |  |  |  |  | Nontradable | [6 empty] | 80 |  |  | 80 |  |  |  | Exterior
[12 empty] | 81 |  |  |  |  | Nontradable | [6 empty] | 81 |  |  | 81 |  |  |  | Exterior
[12 empty] | 82 |  |  |  |  | Nontradable | [6 empty] | 82 |  |  | 82 |  |  |  | Exterior
[12 empty] | 83 |  |  |  |  | Nontradable | [6 empty] | 83 |  |  | 83 |  |  |  | Exterior
[12 empty] | 84 |  |  |  |  | Nontradable | [6 empty] | 84 |  |  | 84 |  |  |  | Exterior
[12 empty] | 85 |  |  |  |  | Nontradable | [6 empty] | 85 |  |  | 85 |  |  |  | Exterior
[12 empty] | 86 |  |  |  |  | Nontradable | [6 empty] | 86 |  |  | 86 |  |  |  | Exterior
[12 empty] | 87 |  |  |  |  | Nontradable | [6 empty] | 87 |  |  | 87 |  |  |  | Exterior
[12 empty] | 88 |  |  |  |  | Nontradable | [6 empty] | 88 |  |  | 88 |  |  |  | Exterior
[12 empty] | 89 |  |  |  |  | Nontradable | [6 empty] | 89 |  |  | 89 |  |  |  | Exterior
[12 empty] | 90 |  |  |  |  | Nontradable | [6 empty] | 90 |  |  | 90 |  |  |  | Exterior
[12 empty] | 91 |  |  |  |  | Nontradable | [6 empty] | 91 |  |  | 91 |  |  |  | Exterior
[12 empty] | 92 |  |  |  |  | Nontradable | [6 empty] | 92 |  |  | 92 |  |  |  | Exterior
[12 empty] | 93 |  |  |  |  | Nontradable | [6 empty] | 93 |  |  | 93 |  |  |  | Exterior
[12 empty] | 94 |  |  |  |  | Nontradable | [6 empty] | 94 |  |  | 94 |  |  |  | Exterior
[12 empty] | 95 |  |  |  |  | Nontradable | [6 empty] | 95 |  |  | 95 |  |  |  | Exterior
[12 empty] | 96 |  |  |  |  | Nontradable | [6 empty] | 96 |  |  | 96 |  |  |  | Exterior
[12 empty] | 97 |  |  |  |  | Nontradable | [6 empty] | 97 |  |  | 97 |  |  |  | Exterior
[12 empty] | 98 |  |  |  |  | Nontradable | [6 empty] | 98 |  |  | 98 |  |  |  | Exterior
[12 empty] | 99 |  |  |  |  | Nontradable | [6 empty] | 99 |  |  | 99 |  |  |  | Exterior
[12 empty] | 100 |  |  |  |  | Nontradable | [6 empty] | 100 |  |  | 100 |  |  |  | Exterior
[12 empty] | 101 |  |  |  |  | Nontradable | [9 empty] | 101 |  |  |  | Exterior
[27 empty] | 102 |  |  |  | Exterior
[27 empty] | 103 |  |  |  | Exterior
[27 empty] | 104 |  |  |  | Exterior
[27 empty] | 105 |  |  |  | Exterior
[27 empty] | 106 |  |  |  | Exterior
[27 empty] | 107 |  |  |  | Exterior
[27 empty] | 108 |  |  |  | Exterior
[27 empty] | 109 |  |  |  | Exterior
[27 empty] | 110 |  |  |  | Exterior
[27 empty] | 111 |  |  |  | Exterior
[27 empty] | 112 |  |  |  | Exterior
[27 empty] | 113 |  |  |  | Exterior
[27 empty] | 114 |  |  |  | Exterior
[27 empty] | 115 |  |  |  | Exterior
[27 empty] | 116 |  |  |  | Exterior
[27 empty] | 117 |  |  |  | Exterior
[27 empty] | 118 |  |  |  | Exterior
[27 empty] | 119 |  |  |  | Exterior
[27 empty] | 120 |  |  |  | Exterior
[27 empty] | 121 |  |  |  | Exterior
[27 empty] | 122 |  |  |  | Exterior
[27 empty] | 123 |  |  |  | Exterior
[27 empty] | 124 |  |  |  | Exterior
[27 empty] | 125 |  |  |  | Exterior
[27 empty] | 126 |  |  |  | Exterior
[27 empty] | 127 |  |  |  | Exterior
[27 empty] | 128 |  |  |  | Exterior
[27 empty] | 129 |  |  |  | Exterior
[27 empty] | 130 |  |  |  | Exterior
[27 empty] | 131 |  |  |  | Exterior
[27 empty] | 132 |  |  |  | Exterior
[27 empty] | 133 |  |  |  | Exterior
[27 empty] | 134 |  |  |  | Exterior
[27 empty] | 135 |  |  |  | Exterior
[27 empty] | 136 |  |  |  | Exterior
[27 empty] | 137 |  |  |  | Exterior
[27 empty] | 138 |  |  |  | Exterior
[27 empty] | 139 |  |  |  | Exterior
[27 empty] | 140 |  |  |  | Exterior
[27 empty] | 141 |  |  |  | Exterior
[27 empty] | 142 |  |  |  | Exterior
[27 empty] | 143 |  |  |  | Exterior
[27 empty] | 144 |  |  |  | Exterior
[27 empty] | 145 |  |  |  | Exterior
[27 empty] | 146 |  |  |  | Exterior
[27 empty] | 147 |  |  |  | Exterior
[27 empty] | 148 |  |  |  | Exterior
[27 empty] | 149 |  |  |  | Exterior
[27 empty] | 150 |  |  |  | Exterior
Create Tradable Exterior Areas
Create NonTradable Exterior Areas
Top of Page
Compliance Main Page
Tradable Areas
NonTradable Areas
Select Appropriate Lighting Zone
Luminaire schedule
Note on I14: Enter your Exterior Area name
Note on J14: Select the Building Space Type for the drop down list. Building/Space Type (C = Common Space Types) (S = Building Specific Space Types)
Note on K14: Enter the square footage of each space in the cells below. Enter length of walkways when using "Walkways < 10' wide (by length)"
Note on O14: Enter your Exterior Area name
Note on P14: Select the Building Space Type for the drop down list. Building/Space Type (C = Common Space Types) (S = Building Specific Space Types)
Note on Q14: Enter the square footage, Linear footage or Number of areas in the cells below.

## Ext Tradable
|  | Quick Links | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0)
|  |  | Exterior Lighting Power - Tradable Areas | [10 empty] | Step 9a: Tradable Areas | Not Used
[14 empty] | Step 9b: NonTradable Areas | Not Used
[6 empty] | Tradable Watts | Compliant
|  |  |  | Calculated | 0 | Base | 0
|  |  |  | Allowed | 0 | Used | 0
| 90.1-2019 |  |  | Tradable deficit before base | 0 | Remaning | 0 | FALSE
| Step 9a: Installed Exterior Lighting Power (Tradable) see NonTradable below also |  | Luminaire Type | Source Type | Number of Luminaires or Linear Feet | Watts Per Luminaire or Linear Foot | Watts | Column not used. | 9.4.1.4.a Daylight hours OFF | 9.4.1.4.b Façade automatic shutoff | 9.4.1.4.c 50% reduction | 9.4.1.4.d Parking 50% reduction | 9.4.2 Controlled separately |  | Exterior Controls compliant? | System Watts | "NEW" Watts | Count of Measures | 9.4.1.4.a Daylight hours OFF | 9.4.1.4.b Façade automatic shutoff | 9.4.1.4.c 50% reduction | 9.4.1.4.d Parking 50% reduction | 9.4.2 Controlled separately | Sum of Compliant (Compliant = 5)
Leave cells blank.
[25 empty] | AS | Col# | Col Name
1 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | A
2 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | B
3 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | C
4 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | D
5 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | E
6 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | F
7 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | G
8 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | H
9 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | I
10 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | J
11 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | K
12 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | l
13 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | M
14 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | N
15 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | O
16 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | P
17 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | Q
18 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | R
19 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | S
20 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | T
[16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 21 | U
[26 empty] | 22 | V
[26 empty] | 23 | W
[26 empty] | 24 | X
[26 empty] | 25 | Y
[26 empty] | 26 | Z
[26 empty] | 27 | AA
[26 empty] | 28 | AB
[26 empty] | 29 | AC
[26 empty] | 30 | AD
[26 empty] | 31 | AE
[26 empty] | 32 | AF
[26 empty] | 33 | AG
[26 empty] | 34 | AH
[26 empty] | 35 | AI
[26 empty] | 36 | AJ
[26 empty] | 37 | AK
1 | [25 empty] | 38 | Al
[26 empty] | 39 | AM
[26 empty] | 40 | AN
[26 empty] | 41 | AO
[26 empty] | 42 | AP
[26 empty] | 43 | AQ
[26 empty] | 44 | AR
[26 empty] | 45 | AS
[26 empty] | 46 | AT
[26 empty] | 47 | AU
[26 empty] | 48 | AV
[26 empty] | 49 | AW
[26 empty] | 50 | AX
[26 empty] | 51 | AY
[26 empty] | 52 | AZ
[26 empty] | 53 | BA
[26 empty] | 54 | BB
[26 empty] | 55 | BC
[26 empty] | 56 | BD
[26 empty] | 57 | BE
[26 empty] | 58 | BF
[26 empty] | 59 | BG
[26 empty] | 60 | BH
[26 empty] | 61 | BI
[26 empty] | 62 | BJ
[26 empty] | 63 | BK
[26 empty] | 64 | Bl
[26 empty] | 65 | BM
[26 empty] | 66 | BN
[26 empty] | 67 | BO
[26 empty] | 68 | BP
[26 empty] | 69 | BQ
[26 empty] | 70 | BR
[26 empty] | 71 | BS
[26 empty] | 72 | BT
[26 empty] | 73 | BU
[26 empty] | 74 | BV
[26 empty] | 75 | BW
[26 empty] | 76 | BX
[26 empty] | 77 | BY
[26 empty] | 78 | BZ
Top of Page
Compliance Main Page
go to to Luminaire section
go to to Controls section
go to to Alterations section (if applicable)
NonTradable Areas
Ext Area Schedule
Exterior Compliance Detials

## ExteriorTradableData (hidden)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43
FALSE
[18 empty] | Base | [14 empty] | LPA Project Level
[18 empty] | 0 | [15 empty] | TRUE
[23 empty] | ALTERATION |  | Exceptions
[8 empty] | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 |  | Area Level |  |  | FALSE |  | FALSE |  |  | NOT available for Exterior? |  |  |  |  | 0 | 0 |  |  |  |  | Compliant
|  |  | 7 |  | 12 | 8 | [13 empty] | LPA |  |  | Exception #1 |  |  |  |  | Exception #2 |  |  |  |  | Exception pass | [5 empty] | Pass=0 |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
| Space Name | 90.1 Space Type | Square Feet |  | Allowed Watts | Allowed LPA |  | True Allowed Watts |  | "New" Watts | "BLANK" Watts | Quantity "New" and "BLANK" | Existing "Remains" watts | Existing "Removed" Watts | Quantity "Removed" | Existing Total | TOTAL "Installed" | Base Allocated | Base Remaining | Designed LPD | LPA Pass/ Fail |  | 20% | 20% Pass/ Fail | Wattage same or lower | Overall |  | 1 for 1 | LPA | Overall |  | Exception Pass/ Fail | Watts Designed | True Allowed Watts |  |  |  |  | 0 |  |  |  |  | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75
1 | [7 empty] | 0 | [25 empty] | 0 | IF(OR(R10=0,B10=""),"",IF(Y$6=FALSE,"",IF(OR(Z10="Pass",AD10="Pass"),"Pass","Fail"))) |  |  |  | 0 |  |  | 1 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
2 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 2 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
3 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 3 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
4 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 4 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
5 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 5 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
6 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 6 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
7 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 7 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
8 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 8 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
9 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 9 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
10 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 10 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
11 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 11 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
12 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 12 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
13 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 13 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
14 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 14 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
15 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 15 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
16 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 16 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
17 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 17 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
18 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 18 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
19 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 19 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
20 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 20 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
21 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 21 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
22 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 22 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
23 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 23 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
24 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 24 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
25 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 25 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
26 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 26 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
27 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 27 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
28 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 28 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
29 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 29 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
30 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 30 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
31 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 31 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
32 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 32 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
33 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 33 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
34 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 34 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
35 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 35 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
36 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 36 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
37 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 37 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
38 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 38 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
39 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 39 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
40 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 40 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
41 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 41 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
42 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 42 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
43 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 43 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
44 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 44 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
45 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 45 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
46 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 46 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
47 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 47 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
48 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 48 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
49 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 49 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
50 | [7 empty] | 0 | [25 empty] | 0 |  |  |  |  | 0 |  |  | 50 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
Note on AH8: Michael lane: If Exception is used then the watts don't count towards the overall LPA compliance.

## Ext Nontradable
|  | Quick Links | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0)
|  |  | Exterior Lighting Power - Nontradable Areas | [16 empty] | Step 9a: Tradable Areas | Not Used
[20 empty] | Step 9b: NonTradable Areas | Not Used
[10 empty] | Nontradable Watts |  |  | Compliant
[10 empty] | Base remaining from Tradable Areas |  |  | 0
[10 empty] | Used below |  |  | 0
| 90.1-2019 | [8 empty] | Remaning |  |  | 0 | FALSE
| Step 9b: Installed Exterior Lighting Power (Nontradable) see NonTradable below also |  | Luminaire Type | Source Type | Number of Luminaires or Linear Feet | Watts Per Luminaire or Linear Foot | Watts | [6 empty] | Column not used. | 9.4.1.4.a Daylight hours OFF | 9.4.1.4.b Façade automatic shutoff | 9.4.1.4.c 50% reduction | 9.4.1.4.d Parking 50% reduction | 9.4.2 Controlled separately |  | Exterior Controls compliant? |  | System Watts | "NEW" Watts | Count of Measures | 9.4.1.4.a Daylight hours OFF | 9.4.1.4.b Façade automatic shutoff | 9.4.1.4.c 50% reduction | 9.4.1.4.d Parking 50% reduction | 9.4.2 Controlled separately | Sum of Compliant (Compliant = 5)
Leave cells blank.
[7 empty] | Designed | Allowed | HIDE column | Base required | HIDE Base remaining | HIDE Base remaining | Compliant?
[32 empty] | AZ | Col# | Col Name
1 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | A
2 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | B
3 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | C
4 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | D
5 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | E
6 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | F
7 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | G
8 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | H
9 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | I
10 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | J
11 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | K
12 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | l
13 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | M
14 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | N
15 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | O
16 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | P
17 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | Q
18 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | R
19 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | S
20 | [10 empty] | 0 | [10 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | T
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 21 | U
[33 empty] | 22 | V
[33 empty] | 23 | W
[33 empty] | 24 | X
[33 empty] | 25 | Y
[33 empty] | 26 | Z
[33 empty] | 27 | AA
[33 empty] | 28 | AB
[33 empty] | 29 | AC
[33 empty] | 30 | AD
[33 empty] | 31 | AE
[33 empty] | 32 | AF
[33 empty] | 33 | AG
[33 empty] | 34 | AH
[33 empty] | 35 | AI
[33 empty] | 36 | AJ
[33 empty] | 37 | AK
[33 empty] | 38 | Al
[33 empty] | 39 | AM
[33 empty] | 40 | AN
[33 empty] | 41 | AO
[33 empty] | 42 | AP
[33 empty] | 43 | AQ
[33 empty] | 44 | AR
[33 empty] | 45 | AS
[33 empty] | 46 | AT
[33 empty] | 47 | AU
[33 empty] | 48 | AV
[33 empty] | 49 | AW
[33 empty] | 50 | AX
[33 empty] | 51 | AY
[33 empty] | 52 | AZ
[33 empty] | 53 | BA
[33 empty] | 54 | BB
[33 empty] | 55 | BC
[33 empty] | 56 | BD
[33 empty] | 57 | BE
[33 empty] | 58 | BF
[33 empty] | 59 | BG
[33 empty] | 60 | BH
[33 empty] | 61 | BI
1 | [32 empty] | 62 | BJ
[33 empty] | 63 | BK
[33 empty] | 64 | Bl
[33 empty] | 65 | BM
[33 empty] | 66 | BN
[33 empty] | 67 | BO
[33 empty] | 68 | BP
[33 empty] | 69 | BQ
[33 empty] | 70 | BR
[33 empty] | 71 | BS
[33 empty] | 72 | BT
[33 empty] | 73 | BU
[33 empty] | 74 | BV
[33 empty] | 75 | BW
[33 empty] | 76 | BX
[33 empty] | 77 | BY
[33 empty] | 78 | BZ
Top of Page
Compliance Main Page
go to to Luminaire section
go to to Controls section
go to to Alterations section (if applicable)
Tradable Areas
Ext Area Schedule
Exterior Compliance Detials

## ExteriorNontradableData (hidden)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41
FALSE
[20 empty] | Base | [13 empty] | LPA Project Level
[19 empty] | from Tradable > | 0 | [14 empty] | TRUE
[19 empty] | Alocated > | 0 |  |  |  | ALTERATION |  | Exceptions
[8 empty] | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | Remaining > | 0 | Area Level |  |  | FALSE |  | FALSE |  |  | NOT available for Exterior? |  |  |  |  | 0 | 0 |  |  |  |  | Compliant
|  |  | 7 |  | 12 | 8 | [14 empty] | LPA |  |  | Exception #1 |  |  |  |  | Exception #2 |  |  |  |  | Exception pass | [5 empty] | Pass=0 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
| Space Name | 90.1 Space Type | Square Feet |  | Allowed Watts | Allowed LPA |  | True Allowed Watts |  | "New" Watts | "BLANK" Watts | Quantity "New" and "BLANK" | Existing "Remains" watts | Existing "Removed" Watts | Quantity "Removed" | Existing Total | TOTAL "Installed" | watts over under | Base Remaining | Allocated base | Allowed Watts (w/base) | Watts Pass/ Fail |  | 20% | 20% Pass/ Fail | Wattage same or lower | Overall |  | 1 for 1 | LPA | Overall |  | Exception Pass/ Fail | Watts Designed | True Allowed Watts |  |  |  |  | 0 |  |  | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75
1 | [17 empty] | 0 | 0 | 0 | [15 empty] | IF(OR(R10=0,B10=""),"",IF(Y$6=FALSE,"",IF(OR(Z10="Pass",AD10="Pass"),"Pass","Fail"))) |  |  |  | 0 |  | 1 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
2 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 2 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
3 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 3 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
4 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 4 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
5 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 5 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
6 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 6 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
7 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 7 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
8 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 8 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
9 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 9 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
10 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 10 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
11 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 11 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
12 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 12 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
13 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 13 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
14 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 14 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
15 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 15 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
16 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 16 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
17 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 17 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
18 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 18 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
19 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 19 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
20 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 20 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
21 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 21 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
22 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 22 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
23 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 23 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
24 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 24 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
25 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 25 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
26 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 26 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
27 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 27 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
28 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 28 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
29 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 29 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
30 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 30 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
31 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 31 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
32 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 32 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
33 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 33 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
34 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 34 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
35 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 35 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
36 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 36 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
37 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 37 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
38 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 38 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
39 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 39 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
40 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 40 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
41 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 41 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
42 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 42 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
43 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 43 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
44 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 44 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
45 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 45 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
46 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 46 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
47 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 47 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
48 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 48 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
49 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 49 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
50 | [17 empty] | 0 | 0 | 0 | [19 empty] | 0 |  | 50 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 000000000000000000000000000000
Note on AI8: Michael lane: If Exception is used then the watts don't count towards the overall LPA compliance.

## 9.3 Int Simplified
|  |  | Quick Links |  | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0) | [9 empty] | Complies?
[5 empty] | 9.3 Simplified Method for Interior Lighting | [6 empty] | No | Alteration
[12 empty] | 0 | Shift Column
[6 empty] | Building Type > |  |  | Designed | Allowed
[6 empty] | Building Square footage > |  |  | 0 |  | FALSE
[6 empty] | Parking Garage Square footage > |  |  | 0 |  |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  |  | Count |  | automatic off when building is unoccupied | manual reduction by at least 50% within 20 minutes | manual-ON occupant sensors | manual-ON or auto-ON occupant sensors | occupant sensor reduction by at least 50% within 20 minutes | reduce the general lighting by 75% during nonbusiness hours | turn off all non-general lighting during non-business hours | Top lighting daylight dimming | SUM
| 90.1-2019 | [10 empty] | Lighting Controls
[8 empty] | TOTAL designed watts complies with allowance! : | 0 |  |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Complete |  | Compliant
| Building Area |  |  |  | Luminaire Type | Quantity | Source Type | Watts | Total Watts | W/sf | Column not used. | automatic off when building is unoccupied |  | manual reduction by at least 50% within 20 minutes |  | manual-ON occupant sensors |  | manual-ON or auto-ON occupant sensors |  | occupant sensor reduction by at least 50% within 20 minutes |  | reduce the general lighting by 75% during nonbusiness hours |  | turn off all non-general lighting during non-business hours |  | Top lighting daylight dimming |  | Are Controls Complete? | [11 empty] | Alterations
|  | Space Type |  |  | Select the Luminaire | Enter the Number of Luminaires or Linear Feet |  | Per Luminaire or Linear Foot |  | LPA | Leave cells blank.
0
[10 empty] | LPA | [29 empty] | Existing Luminaire | Qty | Source | Watts | Total | % reduction | threshold | 0=yes, 1=no
1 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | LED | 0
2 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Fluorescent | 20
3 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | High Pressure Sodium | 45
4 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Metal Halide | 45
5 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Mercury Vapor | 45
6 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Low Pressure Sodium | 45
7 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Incandescent | 75
8 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Induction | 45
9 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Plasma | 45
10 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Other | 45
11 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
12 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
13 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
14 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
15 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
16 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
17 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
18 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
19 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
20 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
21 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
22 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
23 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
24 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
25 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[29 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ''Building Area Method" Building Type |  | Lighting Power Allowance (Watts) | LPD Allowance (watts per sq.ft) |  | Building Area (sq.ft) |  |  | 0
| 0 |  |  |  |  | 0 |  | 0 | 0
| 0 |  |  |  |  | 0 |  | 0 | 0
| 0 |  |  |  |  | 0 |  | 0 | 0
| 0 |  |  |  |  | 0 |  | 0 | 0
| 0 |  |  |  |  | 0 |  | 0 | 0
| 0 |  |  |  |  | 0 |  | 0 | 0
|  | TOTAL: | 0 | [14 empty] | 0.6 | 0.6
Top of Page
Compliance Main Page
Installed Interior Lighting
Controls
Luminaire schedule
9.3 Ext Simplified

## 9.3 Ext Simplified
|  |  | Quick Links |  |  | ASHRAE/IES 90.1-2019 Lighting Compliance Documentation (v4.0) | [10 empty] | Complies?
[6 empty] | 9.3 Simplified Method for Interior Lighting | [7 empty] | No | Alteration
[14 empty] | 0 | Shift Column
[8 empty] | Allowed Watts | Designed Watts | Base Wattage Needed | Base Remaining
< Building Type
[6 empty] | < Lighting Zone | Exterior | 0 | 0 | 0 | 0 | Not Compliant | FALSE | [7 empty] | Count |  | Auto off during daylight hours | power reduced by a minimum of 75% during nonoperating hours | Luminaires mounted 25 ft or less above grade shall be controlled to reduce the power by at least 50% when no activity is detected for not longer than 15 minutes. | SUM
| 90.1-2019 |  |  |  | 0 | Base Allowance | Façade | 0 | 0 | 0 | 0 | Not Compliant |  | Lighting Controls
[14 empty] | Complete |  | Complete |  | Complete |  | Compliant
[14 empty] | 4 |  | 5 |  | 6
| Building Area |  |  |  | Area illuminated | Luminaire Type | Quantity | Source Type | Watts | Designed Watts | W/sf | Allowed Watts | Column not used. | Auto off during daylight hours |  | power reduced by a minimum of 75% during nonoperating hours |  | Luminaires mounted 25 ft or less above grade shall be controlled to reduce the power by at least 50% when no activity is detected for not longer than 15 minutes. |  | Are Controls Complete? | [6 empty] | Alterations
|  | Space Type |  |  | Per Square Foot (or Linear Foot for doors) | Select the Luminaire | Enter the Number of Luminaires or Linear Feet |  | Per Luminaire or Linear Foot |  | LPA |  | Leave cells blank.
0
[11 empty] | LPA | [15 empty] | Existing Luminaire | Qty | Source | Watts | Total | % reduction | threshold | 0=yes, 1=no
1 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | LED | 0
2 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Fluorescent | 20
3 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | High Pressure Sodium | 45
4 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Metal Halide | 45
5 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Mercury Vapor | 45
6 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Low Pressure Sodium | 45
7 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Incandescent | 75
8 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Induction | 45
9 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Plasma | 45
10 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | Other | 45
11 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
12 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
13 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
14 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
15 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
16 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
17 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
18 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
19 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
20 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
21 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
22 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
23 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
24 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
25 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[21 empty] | 0 | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ''Building Area Method" Building Type |  | Lighting Power Allowance (Watts) | LPD Allowance (watts per sq.ft) |  |  | Building Area (sq.ft) |  |  | 0
| 0 | [5 empty] | 0 |  | 0 | 0
| 0 | [5 empty] | 0 |  | 0 | 0
| 0 | [5 empty] | 0 |  | 0 | 0
| 0 | [5 empty] | 0 |  | 0 | 0
| 0 | [5 empty] | 0 |  | 0 | 0
| 0 | [5 empty] | 0 |  | 0 | 0
|  | TOTAL: | 0
0
Top of Page
Compliance Main Page
Installed Interior Lighting
Controls
Luminaire schedule
9.3 Int Simplified

## 9.4.3 Tables
2019 TABLE 9.4.2-1 Exterior Lighting Zones
[15 empty] | Ext Area List | Exterior Table area
Lighting Zone
LZ0 | 0 | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction | [11 empty] | 2010 | Ext_Tradable_Areas_2010 | Ext_Tradable_Table_2010
LZ1 | 350 | LZ1 - Developed areas of national parks, state parks, forest land, and rural areas | [11 empty] | 2016 | Ext_Tradable_Areas_2016 | Ext_Tradable_Table_2016
LZ2 | 400 | LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas | [11 empty] | 2019 | Ext_Tradable_Areas_2019 | Ext_Tradable_Table_2019
LZ3 | 500 | LZ3 - All other areas
LZ4 | 900 | LZ4 - High-activity commercial districts in major metropolitan areas as designated by the local jurisdiction | [11 empty] | 2019 | Ext_Tradable_Areas_2019 | Ext_Tradable_Table_2019
2019 TABLE 9.4.2-2 Individual Lighting Power Allowances for Building Exteriors
[8 empty] | 9.4.1.4.a Daylight hours OFF | 9.4.1.4.b Façade automatic shutoff | 9.4.1.4.c 50% reduction | 9.4.1.4.d Parking 50% reduction | 9.4.2 Controlled separately |  | 2010 | Ext_Nontradable_Areas_2010 | Ext_Nontradable_Table_2010
| LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | Units | [7 empty] | 2016 | Ext_Nontradable_Areas_2016 | Ext_Nontradable_Table_2016
Base Allowance | 0 | 350 | 400 | 500 | 900 | watts | [7 empty] | 2019 | Ext_Nontradable_Areas_2019 | Ext_Nontradable_Table_2019
2019 Base Allowance TRADABLE SURFACES
Uncovered parking areas and drives | 0 | 0.03 | 0.04 | 0.06 | 0.08 | sq.ft. |  | REQ | NA | REQ | REQ | REQ | Meet control requirements of Section 9.4.1.4 a, c, d & 9.4.2 | 2019 | Ext_Nontradable_Areas_2019 | Ext_Nontradable_Table_2019
Walkways < 10' wide (by length) | 0 | 0.5 | 0.5 | 0.6 | 0.7 | Linear ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Walkways ≥ 10' wide OR plaza (by area) | 0 | 0.1 | 0.1 | 0.11 | 0.14 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Dining Areas | 0 | 0.65 | 0.65 | 0.75 | 0.95 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Stairways | 0 | 0.6 | 0.7 | 0.7 | 0.7 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Pedestrian tunnels | 0 | 0.12 | 0.12 | 0.14 | 0.21 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Landscaping | 0 | 0.03 | 0.04 | 0.04 | 0.04 | sq.ft. |  | REQ | REQ | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, b, & 9.4.2
Pedestrian and vehicular entry/exit | 0 | 14 | 14 | 21 | 21 | Linear ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Entry canopies | 0 | 0.2 | 0.2 | 0.2 | 0.2 | Linear ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Loading Docks | 0 | 0.35 | 0.35 | 0.35 | 0.35 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Sales canopies | 0 | 0.4 | 0.4 | 0.6 | 0.7 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Outdoor Sales - Open areas (including vehicle sales lots) | 0 | 0.2 | 0.2 | 0.2 | 0.2 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Street frontage for vehicle sales lots | 0 | 0 | 7 | 7 | 21 | Linear ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
2019 NONTRADABLE SURFACES
Building facades (by area) | 0 | 0 | 0.1 | 0.15 | 0.2 | sq.ft |  | REQ | REQ | NA | NA | REQ | Meet control requirements of Section 9.4.1.4 a, b, & 9.4.2
Building facades (by length) | 0 | 0 | 2.5 | 3.75 | 5 | Linear ft |  | REQ | REQ | NA | NA | REQ | Meet control requirements of Section 9.4.1.4 a, b, & 9.4.2
ATMs & night depository location | 0 | 135 | 135 | 135 | 135 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Additional ATMs | 0 | 45 | 45 | 45 | 45 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Uncovered entrances & gatehouse inspection facilities at guarded facilities | 0 | 0.5 | 0.5 | 0.5 | 0.5 | sq.ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Uncovered loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | 0 | 0.35 | 0.35 | 0.35 | 0.35 | sq.ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Drive-through windows/doors (per drive through) | 0 | 200 | 200 | 200 | 200 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Parking near 24-hour retail entrances | 0 | 400 | 400 | 400 | 400 | Number of |  | REQ | NA | REQ | REQ | REQ | Meet control requirements of Section 9.4.1.4 a, c, d & 9.4.2
Roadway/parking entry, trail head, and toilet facility, or other locations approved by the authority having jurisdiction. | 25 | 0 | 0 | 0 | 0 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
2010 TABLE 9.4.2-1 Exterior Lighting Zones
Lighting Zone
LZ0 | 0 | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction
LZ1 | 500 | LZ1 - Developed areas of national parks, state parks, forest land, and rural areas
LZ2 | 600 | LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas
LZ3 | 750 | LZ3 - All other areas
LZ4 | 1300 | LZ4 - High-activity commercial districts in major metropolitan areas as designated by the local jurisdiction
TABLE 9.4.2-2 Individual Lighting Power Allowances for Building Exteriors
[8 empty] | 9.4.1.7.a Daylight hours OFF | 9.4.1.7.b Façade automatic shutoff | 9.4.1.7.c 30% reduction | 9.4.3 Controlled separately
| LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | Units
Base Allowance | 0 | 500 | 600 | 750 | 1300 | watts
TRADABLE SURFACES
Uncovered parking areas and drives | 0 | 0.04 | 0.06 | 0.1 | 0.13 | sq.ft. |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Walkways < 10' wide (by length) | 0 | 0.7 | 0.7 | 0.8 | 1 | Linear ft |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Walkways ≥ 10' wide OR plaza (by area) | 0 | 0.14 | 0.14 | 0.16 | 0.2 | sq.ft. |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
[8 empty] | NA | NA | NA | NA | NA
Stairways | 0 | 0.75 | 1 | 1 | 1 | sq.ft. |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Pedestrian tunnels | 0 | 0.15 | 0.15 | 0.2 | 0.3 | sq.ft. |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Landscaping | 0 | 0.04 | 0.05 | 0.05 | 0.05 | sq.ft. |  | REQ | REQ | NA | REQ | NA | Meet control requirements of Section 9.4.1.7 a, b & 9.4.3
Main entries | 0 | 20 | 20 | 30 | 30 | Linear ft |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Other doors | 0 | 20 | 20 | 20 | 20 | Linear ft |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Entry canopies | 0 | 0.25 | 0.25 | 0.4 | 0.4 | sq.ft. |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Sales canopies | 0 | 0.6 | 0.6 | 0.8 | 1 | sq.ft. |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Open sales areas | 0 | 0.25 | 0.25 | 0.5 | 0.7 | sq.ft. |  | REQ | NA | REQ | REQ | NA
Street frontage | 0 | 0 | 10 | 10 | 30 | Linear ft |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
NONTRADABLE SURFACES
Building facades (by area) | 0 | 0 | 0.1 | 0.15 | 0.2 | sq.ft |  | REQ | REQ | NA | REQ | NA | Meet control requirements of Section 9.4.1.7 a, b & 9.4.3
Building facades (by length) | 0 | 0 | 2.5 | 3.75 | 5 | Linear ft |  | REQ | REQ | NA | REQ | NA | Meet control requirements of Section 9.4.1.7 a, b & 9.4.3
ATMs & night depository location | 0 | 270 | 270 | 270 | 270 | Number of |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Additional ATMs | 0 | 90 | 90 | 90 | 90 | Number of |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Uncovered entrances & gatehouse inspection facilities at guarded facilities | 0 | 0.75 | 0.75 | 0.75 | 0.75 | sq.ft |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Uncovered loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | 0 | 0.5 | 0.5 | 0.5 | 0.5 | sq.ft |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Drive-through windows/doors (per drive through) | 0 | 400 | 400 | 400 | 400 | Number of |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Parking near 24-hour retail entrances | 0 | 800 | 800 | 800 | 800 | Number of |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
Roadway/parking entry, trail head, and toilet facility, or other locations approved by the authority having jurisdiction. | 60 | 0 | 0 | 0 | 0 | Number of |  | REQ | NA | REQ | REQ | NA | Meet control requirements of Section 9.4.1.7 a, c & 9.4.3
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
2016 TABLE 9.4.2-1 Exterior Lighting Zones
Lighting Zone
LZ0 | 0 | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction
LZ1 | 350 | LZ1 - Developed areas of national parks, state parks, forest land, and rural areas
LZ2 | 400 | LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas
LZ3 | 500 | LZ3 - All other areas
LZ4 | 900 | LZ4 - High-activity commercial districts in major metropolitan areas as designated by the local jurisdiction
TABLE 9.4.2-2 Individual Lighting Power Allowances for Building Exteriors
[8 empty] | 9.4.1.4.a Daylight hours OFF | 9.4.1.4.b Façade automatic shutoff | 9.4.1.4.c 50% reduction | 9.4.1.4.d Parking 50% reduction | 9.4.2 Controlled separately
| LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | Units
Base Allowance | 0 | 350 | 400 | 500 | 900 | watts
TRADABLE SURFACES
Uncovered parking areas and drives | 0 | 0.03 | 0.04 | 0.06 | 0.08 | sq.ft. |  | REQ | NA | REQ | REQ | REQ | Meet control requirements of Section 9.4.1.4 a, c, d & 9.4.2
Walkways < 10' wide (by length) | 0 | 0.5 | 0.5 | 0.6 | 0.7 | Linear ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Walkways ≥ 10' wide OR plaza (by area) | 0 | 0.1 | 0.1 | 0.11 | 0.14 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Dining Areas | 0 | 0.65 | 0.65 | 0.75 | 0.95 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Stairways | 0 | 0.6 | 0.7 | 0.7 | 0.7 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Pedestrian tunnels | 0 | 0.12 | 0.12 | 0.14 | 0.21 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Landscaping | 0 | 0.03 | 0.04 | 0.04 | 0.04 | sq.ft. |  | REQ | REQ | NA | NA | REQ | Meet control requirements of Section 9.4.1.4 a, b, & 9.4.2
Pedestrian and vehicular entry/exit | 0 | 14 | 14 | 21 | 21 | Linear ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Entry canopies | 0 | 0.2 | 0.25 | 0.4 | 0.4 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Loading Docks | 0 | 0.35 | 0.35 | 0.35 | 0.35 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Sales canopies | 0 | 0.4 | 0.4 | 0.6 | 0.7 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Outdoor Sales - Open areas (including vehicle sales lots) | 0 | 0.2 | 0.2 | 0.35 | 0.5 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Street frontage for vehicle sales lots | 0 | 0 | 7 | 7 | 21 | Linear ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
NONTRADABLE SURFACES
Building facades (by area) | 0 | 0 | 0.1 | 0.15 | 0.2 | sq.ft |  | REQ | REQ | NA | NA | REQ | Meet control requirements of Section 9.4.1.4 a, b, & 9.4.2
Building facades (by length) | 0 | 0 | 2.5 | 3.75 | 5 | Linear ft |  | REQ | REQ | NA | NA | REQ | Meet control requirements of Section 9.4.1.4 a, b, & 9.4.2
ATMs & night depository location | 0 | 270 | 270 | 270 | 270 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Additional ATMs | 0 | 90 | 90 | 90 | 90 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Uncovered entrances & gatehouse inspection facilities at guarded facilities | 0 | 0.75 | 0.75 | 0.75 | 0.75 | sq.ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Uncovered loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | 0 | 0.5 | 0.5 | 0.5 | 0.5 | sq.ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Drive-through windows/doors (per drive through) | 0 | 400 | 400 | 400 | 400 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Parking near 24-hour retail entrances | 0 | 800 | 800 | 800 | 800 | Number of |  | REQ | NA | REQ | REQ | REQ | Meet control requirements of Section 9.4.1.4 a, c, d & 9.4.2
Roadway/parking entry, trail head, and toilet facility, or other locations approved by the authority having jurisdiction. | 60 | 0 | 0 | 0 | 0 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
2019 TABLE 9.4.2-1 Exterior Lighting Zones
Lighting Zone
LZ0 | 0 | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction
LZ1 | 350 | LZ1 - Developed areas of national parks, state parks, forest land, and rural areas
LZ2 | 400 | LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas
LZ3 | 500 | LZ3 - All other areas
LZ4 | 900 | LZ4 - High-activity commercial districts in major metropolitan areas as designated by the local jurisdiction
TABLE 9.4.2-2 Individual Lighting Power Allowances for Building Exteriors
[8 empty] | 9.4.1.4.a Daylight hours OFF | 9.4.1.4.b Façade automatic shutoff | 9.4.1.4.c 50% reduction | 9.4.1.4.d Parking 50% reduction | 9.4.2 Controlled separately
| LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | Units
Base Allowance | 0 | 350 | 400 | 500 | 900 | watts
TRADABLE SURFACES
Uncovered parking areas and drives | 0 | 0.03 | 0.04 | 0.06 | 0.08 | sq.ft. |  | REQ | NA | REQ | REQ | REQ | Meet control requirements of Section 9.4.1.4 a, c, d & 9.4.2
Walkways < 10' wide (by length) | 0 | 0.5 | 0.5 | 0.6 | 0.7 | Linear ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Walkways ≥ 10' wide OR plaza (by area) | 0 | 0.1 | 0.1 | 0.11 | 0.14 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Dining Areas | 0 | 0.65 | 0.65 | 0.75 | 0.95 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Stairways | 0 | 0.6 | 0.7 | 0.7 | 0.7 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Pedestrian tunnels | 0 | 0.12 | 0.12 | 0.14 | 0.21 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Landscaping | 0 | 0.03 | 0.04 | 0.04 | 0.04 | sq.ft. |  | REQ | REQ | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, b, & 9.4.2
Pedestrian and vehicular entry/exit | 0 | 14 | 14 | 21 | 21 | Linear ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Entry canopies | 0 | 0.2 | 0.2 | 0.2 | 0.2 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Loading Docks | 0 | 0.35 | 0.35 | 0.35 | 0.35 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Sales canopies | 0 | 0.4 | 0.4 | 0.6 | 0.7 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Outdoor Sales - Open areas (including vehicle sales lots) | 0 | 0.2 | 0.2 | 0.2 | 0.2 | sq.ft. |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Street frontage for vehicle sales lots | 0 | 0 | 7 | 7 | 21 | Linear ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
NONTRADABLE SURFACES
Building facades (by area) | 0 | 0 | 0.1 | 0.15 | 0.2 | sq.ft |  | REQ | REQ | NA | NA | REQ | Meet control requirements of Section 9.4.1.4 a, b, & 9.4.2
Building facades (by length) | 0 | 0 | 2.5 | 3.75 | 5 | Linear ft |  | REQ | REQ | NA | NA | REQ | Meet control requirements of Section 9.4.1.4 a, b, & 9.4.2
ATMs & night depository location | 0 | 135 | 135 | 135 | 135 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Additional ATMs | 0 | 45 | 45 | 45 | 45 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Uncovered entrances & gatehouse inspection facilities at guarded facilities | 0 | 0.5 | 0.5 | 0.5 | 0.5 | sq.ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Uncovered loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | 0 | 0.35 | 0.35 | 0.35 | 0.35 | sq.ft |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Drive-through windows/doors (per drive through) | 0 | 200 | 200 | 200 | 200 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2
Parking near 24-hour retail entrances | 0 | 400 | 400 | 400 | 400 | Number of |  | REQ | NA | REQ | REQ | REQ | Meet control requirements of Section 9.4.1.4 a, c, d & 9.4.2
Roadway/parking entry, trail head, and toilet facility, or other locations approved by the authority having jurisdiction. | 25 | 0 | 0 | 0 | 0 | Number of |  | REQ | NA | REQ | NA | REQ | Meet control requirements of Section 9.4.1.4 a, c & 9.4.2

## 9.5 Table
Table 9.5.1 Lighting Power Density Allowances
| Using the Building Area Method | [6 empty] | Year | Col
5 | 2019 |  |  | 2010 | 2013 | 2016 | 2019 | 2010 | 2
| Building Area Type(a) | LPD, W/ft2 | Building Area Type(a) | LPD, W/ft2 | LPD, W/ft2 | LPD, W/ft2 | LPD, W/ft2 | 2013 | 3
| Automotive Facility | 0.76 | Automotive Facility | 0.82 |  | 0.71 | 0.76 | 2016 | 4
| Convention Center | 0.65 | Convention Center | 1.08 |  | 0.76 | 0.65 | 2019 | 5
| Courthouse | 0.8 | Courthouse | 1.05 |  | 0.9 | 0.8
| Dining: Bar lounge/leisure | 0.81 | Dining: Bar Lounge/Leisure | 0.99 |  | 0.9 | 0.81
| Dining: Cafeteria/fast food | 0.77 | Dining: Cafeteria/Fast Food | 0.9 |  | 0.79 | 0.77
| Dining: Family | 0.72 | Dining: Family | 0.89 |  | 0.78 | 0.72
| Dormitory | 0.54 | Dormitory | 0.61 |  | 0.61 | 0.54
| Exercise Center | 0.73 | Exercise Center | 0.88 |  | 0.65 | 0.73
| Fire Station | 0.57 | Fire Station | 0.71 |  | 0.53 | 0.57
| Gymnasium | 0.77 | Gymnasium | 1 |  | 0.68 | 0.77
| Health-care Clinic | 0.82 | Health-care Clinic | 0.87 |  | 0.82 | 0.82
| Hospital | 0.97 | Hospital | 1.21 |  | 1.05 | 0.97
| Hotel | 0.57 | Hotel | 1 |  | 0.75 | 0.57
| Library | 0.84 | Library | 1.18 |  | 0.78 | 0.84
| Manufacturing Facility | 0.83 | Manufacturing Facility | 1.11 |  | 0.9 | 0.83
| Motel | 0.57 | Motel | 0.88 |  | 0.75 | 0.57
| Motion Picture Theater | 0.45 | Motion Picture Theater | 0.83 |  | 0.83 | 0.45
| Multifamily | 0.46 | Multifamily | 0.6 |  | 0.68 | 0.46
| Museum | 0.56 | Museum | 1.06 |  | 1.06 | 0.56
| Office | 0.65 | Office | 0.9 |  | 0.79 | 0.65
| Parking Garage | 0.19 | Parking Garage | 0.25 |  | 0.15 | 0.19
| Penitentiary | 0.7 | Penitentiary | 0.97 |  | 0.75 | 0.7
| Performing Arts Theater | 0.84 | Performing Arts Theater | 1.39 |  | 1.18 | 0.84
| Police Station | 0.67 | Police Station | 0.96 |  | 0.8 | 0.67
| Post Office | 0.66 | Post Office | 0.87 |  | 0.67 | 0.66
| Religious Facility | 0.68 | Religious Facility | 1.05 |  | 0.94 | 0.68
| Retail | 0.85 | Retail | 1.4 |  | 1.06 | 0.85
| School/University | 0.73 | School/University | 0.99 |  | 0.81 | 0.73
| Sports Arena | 0.77 | Sports Arena | 0.78 |  | 0.87 | 0.77
| Town hall | 0.7 | Town Hall | 0.92 |  | 0.8 | 0.7
| Transportation | 0.51 | Transportation | 0.77 |  | 0.61 | 0.51
| Warehouse | 0.46 | Warehouse | 0.66 |  | 0.48 | 0.46
| Workshop | 0.92 | Workshop | 1.2 |  | 0.9 | 0.92
| a. In cases where both a general building area | [5 empty] | a. In cases where both a general building area type and a specific building area type are listed,
| type and a specific building area type are listed, | [5 empty] | the specific building area type shall apply.
the specific building area type shall apply.

## 9.6 Table
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34
2016 Spaces | 2016 LPD | 2016 RCR | 2016 Local Control (9.4.1.1[a]) | 2016 Restricted to Manual ON (9.4.1.1[b]) | 2016 Restricted to Partial Automatic ON (9.4.1.1[c]) | 2016 Bilevel Lighting Control (9.4.1.1[d]) | 2016 Automatic Daylight Responsive Controls for Sidelighting (9.4.1.1[e]6) | 2016 Automatic Daylight Responsive Controls for Toplighting (9.4.1.1[f]6) | 2016 Automatic Partial OFF (9.4.1.1[g] [Full Off complies]) | 2016 Automatic Full OFF (9.4.1.1[h]) | 2016 Scheduled Shutoff (9.4.1.1[i]) | Garage 9.4.1.2b | Garage 9.4.1.2c | Garage 9.4.1.2d | Guest Room 9.4.1.3b.2 | 2016 9.6.2c | Master | Alteration 9.4.1.1a Local Control | Alterations 9.4.1.1b Restricted to Manual ON | Alteration 9.4.1.1c Restricted to Partial Automatic ON | Alteration 9.4.1.1d Bilevel Lighting Control | Alteration 9.4.1.1e Automatic Daylight Controls for Sidelighting | Alteration 9.4.1.1f Automatic Daylight Controls for Toplighting | Alteration 9.4.1.1g Automatic Partial OFF | Alteration 9.4.1.1h Automatic Full OFF | Alteration 9.4.1.1i Scheduled Shutoff | Alteration 9.4.1.2b Garage | Alteration 9.4.1.2c Garage | Alteration 9.4.1.2d Garage | 9.4.1.3b.2 Guest Room
2016 Spaces | 2016 LPD | 2016 RCR | 9.4.1.1a Local Control | 9.4.1.1b Restricted to Manual ON | 9.4.1.1c Restricted to Partial Automatic ON | 9.4.1.1d Bilevel Lighting Control | 9.4.1.1e Automatic Daylight Controls for Sidelighting | 9.4.1.1f Automatic Daylight Controls for Toplighting | 9.4.1.1g Automatic Partial OFF | 9.4.1.1h Automatic Full OFF | 9.4.1.1i Scheduled Shutoff | 9.4.1.2b Garage | 9.4.1.2c Garage | 9.4.1.2d Garage | 9.4.1.3b.2 Guest Room | 2016 9.6.2c | 2016 Master | 9.4.1.1a Local Control | 9.4.1.1b Restricted to Manual ON | 9.4.1.1c Restricted to Partial Automatic ON | 9.4.1.1d Bilevel Lighting Control | 9.4.1.1e Automatic Daylight Controls for Sidelighting | 9.4.1.1f Automatic Daylight Controls for Toplighting | 9.4.1.1g Automatic Partial OFF | 9.4.1.1h Automatic Full OFF | 9.4.1.1i Scheduled Shutoff | 9.4.1.2b Garage | 9.4.1.2c Garage | 9.4.1.2d Garage | 9.4.1.3b.2 Guest Room
Atrium <20 ft in height | 0.03 | NA | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Atrium >=20 ft and <40 ft in height | 0.03 | NA | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Atrium >40 ft in height | 0.02 | NA | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - All other areas | 0.43 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Auditorium | 0.63 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Convention center | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Gymnasium | 0.65 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Motion picture theater | 1.14 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Penitentiary | 0.28 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Performing arts theater | 2.03 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Religious facility | 1.53 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Sports arena | 0.43 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Banking Activity Area | 0.86 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Chapel - Facility for the Visually Impaired (used primarily by residents) | 1.06 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Classroom/Lecture Hall/Training Room - All other classrooms/lecture halls/training rooms | 0.92 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | 3 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Classroom/Lecture Hall/Training Room - Penitentiary | 1.34 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | 3 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Computer Room | 1.33 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Conference/Meeting/Multipurpose Room | 1.07 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | 3 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Confinement Cells | 0.81 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Convention Center - Exhibit Space | 0.88 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Copy/Print Room | 0.56 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Corridor - All other | 0.66 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Corridor - Facility for the visually impaired not used primarily by the staff | 0.92 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Corridor - Hospital | 0.92 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | ADD2 | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | ADD2 | ADD2 | ADD2 | NA | NA | NA | NA
Corridor - Manufacturing facility | 0.29 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Courtroom | 1.39 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - All other dining areas | 0.63 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - Bar/lounge or leisure dining | 0.93 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - Cafeteria or fast food dining | 0.63 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - Facility for the visually impaired not used primarily by the staff | 2 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - Family dining | 0.71 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - Penitentiary | 0.96 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dormitory - Living Quarters | 0.54 | 8 | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Electrical/Mechanical Room | 0.43 | 6 | REQ | NA | NA | NA | REQ | REQ | NA | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Emergency Vehicle Garage | 0.41 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Fire Station - Sleeping Quarters | 0.2 | 6 | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Food Preparation Area | 1.06 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Guest Room | 0.77 | 6 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | REQ | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | REQ
Gymnasium/Fitness Center - Exercise area | 0.5 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Gymnasium/Fitness Center - Playing area | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Exam/treatment room | 1.68 | 8 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Imaging room | 1.06 | 6 | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Medical supply room <50 ft2 | 0.97 | 6 | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Medical supply room >=50 ft2 | 0.46 | 6 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Healthcare Facility - Nurse’s station | 0.81 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Nursery | 1 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Operating room | 2.17 | 6 | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Patient room | 0.62 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Physical therapy room | 0.84 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Recovery room | 1.03 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Laboratory - All other laboratories | 1.45 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Laboratory - In or as a classroom | 1.2 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 3 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Laundry/Washing Area | 0.43 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Library - Reading area | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Library - Stacks | 1.2 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Loading Dock, Interior | 0.58 | 6 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - All other lobbies | 1 | 4 | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - Elevator | 0.69 | 6 | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - Facility for the visually impaired and not used primarily by the staff | 2.03 | 4 | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - Hotel | 1.06 | 4 | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - Motion picture theater | 0.45 | 4 | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - Performing arts theater | 1.7 | 6 | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Locker Room | 0.48 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Lounge/Breakroom - All other lounges/breakrooms | 0.62 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Lounge/Breakroom - Healthcare facility | 0.78 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Manufacturing Facility - Detailed manufacturing area | 0.93 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Manufacturing Facility - Equipment room | 0.65 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Manufacturing Facility - Extra high bay area (>50 ft floor-to-ceiling height) | 1.05 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Manufacturing Facility - High bay area (25 to 50 ft floor-to-ceiling height) | 0.75 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Manufacturing Facility - Low bay area (<25 ft floor-to-ceiling height) | 0.96 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Museum - General exhibition area | 1.05 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Museum - Restoration room | 0.85 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Office - Enclosed and <=250 ft2 | 0.93 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | 2 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Office - Enclosed and >250 ft2 | 0.93 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 2 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Office - Open plan | 0.81 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 1 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Parking Area, Interior | 0.14 | 4 | NA | NA | NA | NA | NA | NA | NA | NA | REQ | REQ | REQ | REQ | NA | 6 |  | NA | NA | NA | NA | NA | NA | NA | NA | REQ | REQ | REQ | REQ | NA
Performing Arts Theater - Dressing Room | 0.36 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Pharmacy Area | 1.34 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Post Office - Sorting Area | 0.68 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Recreation room/common living room - Facility for the Visually Impaired not used primarily by staff | 1.8 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Religious Facility - Fellowship hall | 0.55 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Religious Facility - Worship/pulpit/choir area | 1.53 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Restroom - All other restrooms | 0.85 | 8 | NA | NA | NA | NA | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Restroom - Facility for the visually impaired nd not used primarily by the staff | 0.96 | 8 | NA | NA | NA | NA | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Retail Facilities - Dressing/fitting room | 0.5 | 8 | REQ | ADD1 | ADD1 | REQ | NA | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Retail Facilities - Mall concourse | 0.9 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Sales Area | 1.22 | 6 | REQ | ADD1 | ADD1 | REQ | NA | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 4 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Seating Area, General | 0.42 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Sports Arena Playing Area - Class I facility | 2.47 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Sports Arena Playing Area - Class II facility | 1.96 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Sports Arena Playing Area - Class III facility | 1.7 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Sports Arena Playing Area - Class IV facility | 1.13 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Stairwell | 0.58 | 10 | NA | NA | NA | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | NA | NA | NA | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Storage Room <50 ft2 | 0.97 | 6 | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Storage Room >=50 ft2 | 0.46 | 6 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Transportation Facility - Airport concourse | 0.31 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Transportation Facility - Baggage/carousel area | 0.45 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Transportation Facility - Terminal ticket counter | 0.62 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Vehicular Maintenance Area | 0.56 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Warehouse Storage - Medium to bulky, palletized items | 0.35 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Warehouse Storage - Smaller, hand-carried items | 0.69 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Workshop | 1.14 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
[13 empty] | Year | _Space_X_Space_List
Table 9.6.1 Lighting Power Density Allowances Using the Space-by-Space Method and Minimum Control Requirements Using Either Method
|  | Informative Note: This table is divided into two sections; this first section covers space types that can be commonly found in multiple building types. The second part of this table covers space types that are typically found in a single building type. |  |  | The control functions below shall be implemented in accordance with the descriptions found in the referenced paragraphs within
Section 9.4.1.1. For each space type:
(1) All REQs shall be implemented.
(2) At least one ADD1 (when present) shall be implemented.
(3) At least one ADD2 (when present) shall be implemented.
0.40 + 0.02/ft total height |  |  |  |  | Local Control (See Section 9.4.1.1[a]) | Restricted to Manual ON (See Section 9.4.1.1[b]) | Restricted to Partial Automatic ON (See Section 9.4.1.1[c]) | Bilevel Lighting Control (See Section 9.4.1.1[d]) | Automatic Daylight Responsive Controls for Sidelighting (See Section 9.4.1.1[e]6) | Automatic Daylight Responsive Controls for Toplighting (See Section 9.4.1.1[f]6) | Automatic Partial OFF (See Section 9.4.1.1[g] [Full Off complies]) |  |  |  | Automatic Full OFF (See Section 9.4.1.1[h]) | Scheduled Shutoff (See Section 9.4.1.1[i])
|  | Space Types1 | LPD Allowances, W/ft2 | RCR Threshold | a | b | c | d | e | f | g |  |  |  | h | i | 9.6.2c
Atrium <20 ft in height | Atrium | <20 ft in height | 0.03 | NA | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Atrium >=20 ft and <=40 ft in height | Atrium | >=20 ft and <=40 ft in height | 0.03 | NA | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Atrium >40 ft in height | Atrium | >40 ft in height | 0.02 | NA | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Audience Seating Area in all other audience areas | Audience Seating Area in | all other audience areas | 0.43 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Auditorium | Audience Seating Area in | Auditorium | 0.63 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Convention center | Audience Seating Area in | Convention center | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Gymnasium | Audience Seating Area in | Gymnasium | 0.65 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Motion picture theater | Audience Seating Area in | Motion picture theater | 1.14 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Penitentiary | Audience Seating Area in | Penitentiary | 0.28 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Performing arts theater | Audience Seating Area in | Performing arts theater | 2.03 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Religious facility | Audience Seating Area in | Religious facility | 1.53 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Sports arena | Audience Seating Area in | Sports arena | 0.43 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Banking Activity Area - Bank/Office | Banking Activity Area - | Bank/Office | 0.86 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Chapel for the Visually Impaired (used primarily by residents) | Chapel | for the Visually Impaired (used primarily by residents) | 1.06 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Classroom - Laboratory in or as a classroom |  | Classroom - Laboratory in or as a classroom | 1.2 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Conference Room, Meeting Room, Classroom (Lecture/Training)
Classroom/ Lecture Hall/ Training Room in a Penitentiary |  | Classroom/ Lecture Hall/ Training Room in a Penitentiary | 1.34 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | REQ |  | Conference Room, Meeting Room, Classroom (Lecture/Training)
Classrooms/ lecture halls/ training rooms in all other areas |  | Classrooms/ lecture halls/ training rooms in all other areas | 0.92 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | REQ |  | Conference Room, Meeting Room, Classroom (Lecture/Training)
Computer Room |  | Computer Room | 1.33 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Conference/ Meeting/ Multipurpose Room |  | Conference/ Meeting/ Multipurpose Room | 1.07 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | REQ |  | Conference Room, Meeting Room, Classroom (Lecture/Training)
Confinement Cells |  | Confinement Cells | 0.81 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Convention Center - Exhibit Space |  | Convention Center - Exhibit Space | 0.88 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Copy/Print Room |  | Copy/Print Room | 0.56 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | REQ |  | NA
Corridor Facility for the visually impaired (and not used primarily by the staff) | Corridor | Facility for the visually impaired (and not used primarily by the staff) | 0.92 | width <8 ft | REQ |  |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Corridor in all other other areas | Corridor in | all other other areas | 0.66 | width <8 ft | REQ |  |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Corridor in a Hospital | Corridor in a | Hospital | 0.92 | width <8 ft | REQ |  |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Corridor in a Manufacturing facility | Corridor in a | Manufacturing facility | 0.29 | width <8 ft | REQ |  |  |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Courtroom |  | Courtroom | 1.39 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Dining Area in all other dining areas | Dining Area in | all other dining areas | 0.63 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area in a Bar/lounge or leisure dining | Dining Area in a | Bar/lounge or leisure dining | 0.93 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area in a Cafeteria or fast food dining | Dining Area in a | Cafeteria or fast food dining | 0.63 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area in a Facility for the visually impaired (and not u(and not used primarily by staff)sed primarily by the staff) | Dining Area in a | Facility for the visually impaired (and not u(and not used primarily by staff)sed primarily by the staff) | 2 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area in a Family dining area | Dining Area in a | Family dining area | 0.71 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area in a Penitentiary | Dining Area in a | Penitentiary | 0.96 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dormitory - Living Quarters |  | Dormitory - Living Quarters | 0.54 | 8 | REQ | [11 empty] | NA
Electrical/Mechanical Room |  | Electrical/Mechanical Room | 0.43 | 6 | REQ |  |  |  | REQ | REQ | [6 empty] | NA
Emergency Vehicle Garage |  | Emergency Vehicle Garage | 0.41 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Fire Station - Sleeping Quarters |  | Fire Station - Sleeping Quarters | 0.2 | 6 | REQ | [11 empty] | NA
Food Preparation Area |  | Food Preparation Area | 1.06 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Guest Room |  | Guest Room | 0.77 | 6 | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). |  |  |  | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | NA
Gymnasium/Fitness Center Exercise area | Gymnasium/Fitness Center | Exercise area | 0.5 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Gymnasium/Fitness Center Playing area | Gymnasium/Fitness Center | Playing area | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Healthcare Facility - Exam/treatment room | Healthcare Facility - | Exam/treatment room | 1.68 | 8 | REQ |  |  | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Healthcare Facility - Imaging room | Healthcare Facility - | Imaging room | 1.06 | 6 | REQ |  |  | REQ | [6 empty] | ADD2 | ADD2 | NA
Healthcare Facility - Medical supply room | Healthcare Facility - | Medical supply room | 0.54 | 6 | See “Storage Room” | See “Storage Room” | See “Storage Room” | See “Storage Room” | See “Storage Room” | See “Storage Room” | See “Storage Room” |  |  |  | See “Storage Room” | See “Storage Room” | NA
Healthcare Facility - Nurse’s station | Healthcare Facility - | Nurse’s station | 0.81 | 6 | REQ |  |  | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Healthcare Facility - Nursery | Healthcare Facility - | Nursery | 1 | 6 | REQ |  |  | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Healthcare Facility - Operating room | Healthcare Facility - | Operating room | 2.17 | 6 | REQ |  |  | REQ | [6 empty] | ADD2 | ADD2 | NA
Healthcare Facility - Patient room | Healthcare Facility - | Patient room | 0.62 | 6 | REQ |  |  | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Healthcare Facility - Physical therapy room | Healthcare Facility - | Physical therapy room | 0.84 | 6 | REQ |  |  | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Healthcare Facility - Recovery room | Healthcare Facility - | Recovery room | 1.03 | 6 | REQ |  |  | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Laboratories - not in or as a classroom |  | Laboratories - not in or as a classroom | 1.45 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Laundry/Washing Area |  | Laundry/Washing Area | 0.43 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Library - Reading area | Library - | Reading area | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Library - Stacks | Library - | Stacks | 1.2 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Loading Dock, Interior |  | Loading Dock, Interior | 0.58 | 6 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Lobby - All other lobbies | Lobby - | All other lobbies | 1 | 4 | REQ |  |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Elevator lobby | Lobby - | Elevator lobby | 0.69 | 6 | REQ |  |  |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby Facility for the visually impaired (and not used primarily by the staff) | Lobby | Facility for the visually impaired (and not used primarily by the staff) | 2.03 | 4 | REQ |  |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby in a Hotel | Lobby in a | Hotel | 1.06 | 4 | REQ |  |  |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby in a Motion picture theater | Lobby in a | Motion picture theater | 0.45 | 4 | REQ |  |  |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby in a Performing arts theater | Lobby in a | Performing arts theater | 1.7 | 6 | REQ |  |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Locker Room |  | Locker Room | 0.48 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Lounge/Breakroom in a Healthcare facility |  | Lounge/Breakroom in a Healthcare facility | 0.78 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Lounges/breakrooms - All other |  | Lounges/breakrooms - All other | 0.62 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - (<25 ft floor-to-ceiling height) | Manufacturing Facility - | (<25 ft floor-to-ceiling height) | 0.96 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - (>50 ft floor-to-ceiling height) | Manufacturing Facility - | (>50 ft floor-to-ceiling height) | 0.75 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - (25 to 50 ft floor-to-ceiling height) | Manufacturing Facility - | (25 to 50 ft floor-to-ceiling height) | 1.05 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - Detailed manufacturing area | Manufacturing Facility - | Detailed manufacturing area | 0.93 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - Equipment room | Manufacturing Facility - | Equipment room | 0.65 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - Extra high bay area | Manufacturing Facility - | Extra high bay area | 1.05 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - High bay area | Manufacturing Facility - | High bay area | 0.75 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - Low bay area | Manufacturing Facility - | Low bay area | 0.96 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Museum - General exhibition area | Museum - | General exhibition area | 1.05 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Museum - Restoration room | Museum - | Restoration room | 0.85 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Office - Enclosed and <=250 ft | Office - | Enclosed and <=250 ft | 0.93 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | REQ |  | Private Office
Office - Enclosed and >250 ft | Office - | Enclosed and >250 ft | 0.93 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Private Office
Office - Open plan | Office - | Open plan | 0.81 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Open Office
Parking Area - Garage |  | Parking Area - Garage | 0.14 | 4 | See Section 9.4.1.2. | See Section 9.4.1.2. | See Section 9.4.1.2. | See Section 9.4.1.2. | See Section 9.4.1.2. | See Section 9.4.1.2. | See Section 9.4.1.2. |  |  |  | See Section 9.4.1.2. | See Section 9.4.1.2. | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Performing Arts Theater - Dressing Room |  | Performing Arts Theater - Dressing Room | 0.36 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | REQ |  | NA
Pharmacy Area |  | Pharmacy Area | 1.34 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Post Office - Sorting Area |  | Post Office - Sorting Area | 0.68 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Recreation Room/ Common Living Room (and not used primarily by staff) for the Visually Impaired (used primarily by residents) | Recreation Room/ Common Living Room (and not used primarily by staff) | for the Visually Impaired (used primarily by residents) | 1.8 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Religious Facility - Fellowship hall | Religious Facility - | Fellowship hall | 0.55 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Religious Facility - Worship/pulpit/choir area | Religious Facility - | Worship/pulpit/choir area | 1.53 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Restroom in a facility for the visually impaired (and not used primarily by the staff)3 |  | Restroom in a facility for the visually impaired (and not used primarily by the staff)3 | 0.96 | 8 |  |  |  |  | REQ | REQ |  |  |  |  | REQ |  | NA
Restrooms - All other |  | Restrooms - All other | 0.85 | 8 |  |  |  |  | REQ | REQ |  |  |  |  | REQ |  | NA
Retail Facilities - Dressing/fitting room | Retail Facilities - | Dressing/fitting room | 0.5 | 8 | REQ | ADD1 | ADD1 | REQ |  | REQ |  |  |  |  | REQ |  | NA
Retail Facilities - Mall concourse | Retail Facilities - | Mall concourse | 0.9 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Sales Area |  | Sales Area | 1.22 | 6 | REQ | ADD1 | ADD1 | REQ |  | REQ |  |  |  |  | ADD2 | ADD2 | Retail Sales Area
Seating Area, General |  | Seating Area, General | 0.42 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Sports Arena - Playing Area Class I facility | Sports Arena - Playing Area | Class I facility | 2.47 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Sports Arena - Playing Area Class II facility | Sports Arena - Playing Area | Class II facility | 1.96 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Sports Arena - Playing Area Class III facility | Sports Arena - Playing Area | Class III facility | 1.7 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Sports Arena - Playing Area Class IV facility | Sports Arena - Playing Area | Class IV facility | 1.13 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Stairwell |  | Stairwell | 0.58 | 10 |  |  |  | REQ | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Storage Room <50 ft2 | Storage Room | <50 ft2 | 0.97 | 6 | REQ | [9 empty] | ADD2 | ADD2 | NA
Storage Room >=50 ft2 and <=1000 ft2 | Storage Room | >=50 ft2 and <=1000 ft2 | 0.46 | 6 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  |  | REQ |  | NA
Storage Room All other storage rooms | Storage Room | All other storage rooms | 0.46 | 6 | REQ | ADD1 | ADD1 |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Transportation Facility - Airport concourse | Transportation Facility - | Airport concourse | 0.31 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Transportation Facility - Baggage/carousel area | Transportation Facility - | Baggage/carousel area | 0.45 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Transportation Facility - Ticket counter | Transportation Facility - | Ticket counter | 0.62 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Vehicular Maintenance Area |  | Vehicular Maintenance Area | 0.56 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
Warehouse - Storage Area Medium to bulky, palletized items | Warehouse - Storage Area | Medium to bulky, palletized items | 0.35 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Warehouse - Storage Area Smaller, hand-carried items | Warehouse - Storage Area | Smaller, hand-carried items | 0.69 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Workshop |  | Workshop | 1.14 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  |  | ADD2 | ADD2 | NA
1. In cases where both a common space type and a building area specific space type are listed, the building area specific space type shall apply
2. In corridors, the extra lighting power density allowance is permitted when the width of the corridor is less than 8 ft and is not based on the RCR.
3. A “Facility for the Visually Impaired” is a facility that can be documented as being designed to comply with the light levels in ANSI/IES RP-28 and is licensed or will be licensed by local/state authorities for either senior long-term care, adult daycare, senior support and/or people with special visual needs.
4. For accent lighting, see Section 9.6.2(b).
5. Sometimes referred to as a “Picking Area.”
6. Automatic daylight responsive controls are mandatory only if the requirements of the specified sections are present.
7. An additional 0.52 W/ft2 shall be allowed, provided that the additional lighting is controlled separately from the base allowance of 0.43 W/ft2. The additional 0.52 W/ft2 allowance shall not be used for any other purpose.
8. Class of play as defined by IES RP-6.
2010
Space Types (SSpaceType3) |  |  | LPD | RCR | 9.4.1.1 Automatic Lighting Shutoff | 9.4.1.2 Space Control (a) Bi-Level | 9.4.1.2 Space Control (b) Occ | 9.4.1.2 Space Control (c) | 9.4.1.3 Parking Garage Lighting Control | 9.4.1.4 Automatic Daylighting Controls for Primary Sidelighted Areas | 9.4.1.5 Automatic Daylighting Controls for Toplighting |  |  |  | 9.4.1.6 Additional Control
Atrium - First 40 ft in height |  |  | 0.03 | na | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Atrium >40 ft in height |  |  | 0.02 | na | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Audience/Seating Area - Auditorium |  |  | 0.79 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Audience/Seating Area - Motion Picture Theater |  |  | 1.14 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Audience/Seating Area - Performing Arts Theater |  |  | 2.43 | 8 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Classroom/Lecture/Training |  |  | 1.24 | 4 | REQ | REQ | REQ | N/A | N/A | - | - |  |  |  | - | - | Conference Room, Meeting Room, Classroom (Lecture/Training)
Conference/Meeting/Multipurpose |  |  | 1.23 | 6 | REQ | REQ | REQ | N/A | N/A | - | - |  |  |  | - | - | Conference Room, Meeting Room, Classroom (Lecture/Training)
Corridor/Transition |  |  | 0.66 | 8' wide | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area |  |  | 0.65 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Bar Lounge/Leisure Dining |  |  | 1.31 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Family Dining |  |  | 0.89 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dressing/Fitting Room - Performing Arts Theater |  |  | 0.4 | 6 | REQ | REQ | REQ | N/A | N/A | - | - |  |  |  | - | - | NA
Electrical/Mechanical Room |  |  | 0.95 | 6 | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Food Preperation |  |  | 0.99 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Laboratory - Classroom |  |  | 1.28 | 6 | REQ | REQ | REQ | N/A | N/A | - | - |  |  |  | - | - | Conference Room, Meeting Room, Classroom (Lecture/Training)
Laboratory - Research |  |  | 1.81 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Lobby |  |  | 0.9 | 4 | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Elevator |  |  | 0.64 | 6 | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Motion Picture Theater |  |  | 0.52 | 4 | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Performing Arts Theater |  |  | 2 | 6 | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Locker Room |  |  | 0.75 | 6 | REQ | REQ | REQ | N/A | N/A | - | - |  |  |  | - | - | NA
Lounge/Recreation |  |  | 0.73 | 4 | REQ | REQ | REQ | N/A | N/A | - | - |  |  |  | - | - | NA
Office-Enclosed |  |  | 1.11 | 8 | REQ | REQ | REQ | N/A | N/A | - | - |  |  |  | - | - | Private Office
Office-Open |  |  | 0.98 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | Open Office
Restrooms |  |  | 0.98 | 8 | REQ | N/A | REQ | N/A | N/A | - | - |  |  |  | - | - | NA
Sales Area |  |  | 1.68 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | Retail Sales Area
Stairway |  |  | 0.69 | 10 | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Storage |  |  | 0.63 | 6 | REQ | N/A | REQ | N/A | N/A | - | - |  |  |  | - | - | NA
Workshop |  |  | 1.59 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Automotive - Service/Repair |  |  | 0.67 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Bank/Office - Banking Activity Area |  |  | 1.38 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Convention Center - Audience Seating |  |  | 0.82 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Convention Center - Exhibit Space |  |  | 1.45 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Confinement Cells |  |  | 1.1 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Courtroom |  |  | 1.72 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Judges' Chambers |  |  | 1.17 | 8 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating |  |  | 0.43 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Penitentiary Dining |  |  | 1.07 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Pentitentiary Classroom |  |  | 1.34 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Dormitory - Living Quarters |  |  | 0.38 | 8 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Fire Stations - Engine Room |  |  | 0.56 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Fire Stations - Sleeping Quarters |  |  | 0.25 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Gymnasium/Fitness Center - Fitness Area |  |  | 0.72 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Gymnasium/Fitness Center - Gymnasium - Audience Seating |  |  | 0.43 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Gymnasium/Fitness Center - Playing Area |  |  | 1.2 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Hospital - Corridor/Transition |  |  | 0.89 | 8' wide | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Emergency |  |  | 2.26 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Exam/Treatment |  |  | 1.66 | 8 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Laundry - Washing |  |  | 0.6 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Lounge/Recreation |  |  | 1.07 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Medical Supply |  |  | 1.27 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Nursery |  |  | 0.88 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Nurses' Station |  |  | 0.87 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Operating Room |  |  | 1.89 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Patient Room |  |  | 0.62 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Pharmacy |  |  | 1.14 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Physical Therapy |  |  | 0.91 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Radiology/Imaging |  |  | 1.32 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hospital - Recovery |  |  | 1.15 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hotel/Motel - Highway Lodging Dining |  |  | 0.88 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hotel/Motel - Highway Lodging Guest Room |  |  | 0.75 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hotel/Motel - Hotel Dining |  |  | 0.82 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hotel/Motel - Hotel Guest Rooms |  |  | 1.11 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Hotel/Motel - Hotel Lobby |  |  | 1.06 | 4 | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Library - Card File & Cataloging |  |  | 0.72 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Library - Reading Area |  |  | 0.93 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Library - Stacks |  |  | 1.71 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Manufacturing - Corridor/Transition |  |  | 0.41 | 8' wide | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Manufacturing - Detailed Manufacturing |  |  | 1.29 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Manufacturing - Equipment Room |  |  | 0.95 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Manufacturing - Extra High Bay (≥ 50') |  |  | 1.05 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Manufacturing - High Bay (≥ 25' & < 50') |  |  | 1.23 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Manufacturing - Low Bay (< 25') |  |  | 1.19 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Museum - General Exhibition |  |  | 1.05 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Museum - Restoration |  |  | 1.02 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Parking Garage - Garage Area |  |  | 0.19 | 4 | REQ | REQ | N/A | REQ | REQ | - | - |  |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Post Office - Sorting Area |  |  | 0.94 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Religious Buildings - Audience Seating |  |  | 1.53 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Religious Buildings - Fellowship Hall |  |  | 0.64 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Religious Buildings - Worship Pulpit, Choir |  |  | 1.53 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Retail - Dressing/Fitting Room |  |  | 0.87 | 8 | REQ | REQ | REQ | N/A | N/A | - | - |  |  |  | - | - | NA
Retail - Mall Concourse |  |  | 1.1 | 4 | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Retail - Sales Area |  |  | 1.68 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | Retail Sales Area
Sports Arena - Audience Seating |  |  | 0.43 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Sports Arena - Court Sports Area - Class 1 |  |  | 3.01 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Sports Arena - Court Sports Area - Class 2 |  |  | 1.92 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Sports Arena - Court Sports Area - Class 3 |  |  | 1.2 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Sports Arena - Court Sports Area - Class 4 |  |  | 0.72 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Sports Arena - Ring Sports Area |  |  | 2.68 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Transportation - Air/Train/Bus Baggage Area |  |  | 0.76 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Transportation - Airport Concourse |  |  | 0.36 | 4 | REQ | N/A | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Transportation - Audience Seating |  |  | 0.54 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Transportation - Terminal - Ticket Counter |  |  | 1.08 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Warehouse - Fine Material Storage |  |  | 0.95 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA
Warehouse - Medium/Bulky Material Storage |  |  | 0.58 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  |  | - | - | NA |  | Ext Area List | Exterior Table area
[6 empty] | 2019 | Courtroom |  |  | 1.2 |  |  | 2016 | __2016_Space_List | Table_9.6.1_2016 |  |  | 2010 | 2010 areas | 2010 Table
NA | 2010 | 2016 | 2019 | Notes | [8 empty] | 2019 | __2019_Space_List | Table_9.6.1_2019 |  |  | 2016 | 2016 areas | 2016 Table
9.6.2 Additional Interior Lighting Power | 2010 | 2016 | 2019 | Notes | [8 empty] | 2010 | __2010_Space_List | _Table_9.6.1_2010 |  |  | 2019 | 2019 areas | 2019 Table
Retail Area 1 | 0.6 | 0.45 | 0.45 | = the floor area for all products not listed in Retail Areas 2, 3, or 4
Retail Area 2 | 0.6 | 0.45 | 0.45 | = the floor area used for the sale of vehicles, sporting goods, and small electronics | [8 empty] | 2019 | __2019_Space_List | Table_9.6.1_2019 |  |  | 2019 | 2019 areas | 2019 Table
Retail Area 3 | 1.4 | 1.05 | 1.05 | = the floor area used for the sale of furniture, clothing, cosmetics, and artwork
Retail Area 4 | 2.5 | 1.88 | 1.88 | = the floor area used for the sale of jewelry, crystal, and china
Base | 1000 | 1000 | 1000 | = Base allowance |  | 1000
2019
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
2019 Spaces | 2019 LPD | 2019 RCR | 2019 Local Control (9.4.1.1[a]) | 2019 Restricted to Manual ON (9.4.1.1[b]) | 2019 Restricted to Partial Automatic ON (9.4.1.1[c]) | 2019 Bilevel Lighting Control (9.4.1.1[d]) | 2019 Automatic Daylight Responsive Controls for Sidelighting (9.4.1.1[e]6) | 2019 Automatic Daylight Responsive Controls for Toplighting (9.4.1.1[f]6) | 2019 Automatic Partial OFF (9.4.1.1[g] [Full Off complies]) | 2019 Automatic Full OFF (9.4.1.1[h]) | 2019 Scheduled Shutoff (9.4.1.1[i]) | Garage 9.4.1.2b | Garage 9.4.1.2c | Garage 9.4.1.2d | Guest Room 9.4.1.3b.2 | 2019 9.6.2c | Master | Alteration 9.4.1.1a Local Control | Alterations 9.4.1.1b Restricted to Manual ON | Alteration 9.4.1.1c Restricted to Partial Automatic ON | Alteration 9.4.1.1d Bilevel Lighting Control | Alteration 9.4.1.1e Automatic Daylight Controls for Sidelighting | Alteration 9.4.1.1f Automatic Daylight Controls for Toplighting | Alteration 9.4.1.1g Automatic Partial OFF | Alteration 9.4.1.1h Automatic Full OFF | Alteration 9.4.1.1i Scheduled Shutoff | Alteration 9.4.1.2b Garage | Alteration 9.4.1.2c Garage | Alteration 9.4.1.2d Garage | 9.4.1.3b.2 Guest Room
2019 Spaces | 2019 LPD | 2019 RCR | 9.4.1.1a Local Control | 9.4.1.1b Restricted to Manual ON | 9.4.1.1c Restricted to Partial Automatic ON | 9.4.1.1d Bilevel Lighting Control | 9.4.1.1e Automatic Daylight Controls for Sidelighting | 9.4.1.1f Automatic Daylight Controls for Toplighting | 9.4.1.1g Automatic Partial OFF | 9.4.1.1h Automatic Full OFF | 9.4.1.1i Scheduled Shutoff | 9.4.1.2b Garage | 9.4.1.2c Garage | 9.4.1.2d Garage | 9.4.1.3b.2 Guest Room | 9.6.2c | Master | 9.4.1.1a Local Control | 9.4.1.1b Restricted to Manual ON | 9.4.1.1c Restricted to Partial Automatic ON | 9.4.1.1d Bilevel Lighting Control | 9.4.1.1e Automatic Daylight Controls for Sidelighting | 9.4.1.1f Automatic Daylight Controls for Toplighting | 9.4.1.1g Automatic Partial OFF | 9.4.1.1h Automatic Full OFF | 9.4.1.1i Scheduled Shutoff | 9.4.1.2b Garage | 9.4.1.2c Garage | 9.4.1.2d Garage | 9.4.1.3b.2 Guest Room
Atrium <20 ft in height | 0.39 | NA | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Atrium >=20 ft and <40 ft in height | 0.48 | NA | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Atrium >40 ft in height | 0.6 | 11 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - All other areas | 0.23 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Auditorium | 0.61 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Gymnasium | 0.23 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Motion picture theater | 0.27 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Penitentiary | 0.67 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Performing arts theater | 1.16 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Religious facility | 0.72 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Audience Seating Area - Sports arena | 0.33 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Banking Activity Area | 0.61 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Chapel - Facility for the Visually Impaired (used primarily by residents) | 0.7 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Classroom/Lecture Hall/Training Room - All other classrooms/lecture halls/training rooms | 0.71 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | 3 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Classroom/Lecture Hall/Training Room - Penitentiary | 0.89 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | 3 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Computer Room | 0.94 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Conference/Meeting/Multipurpose Room | 0.97 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | 3 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Confinement Cells | 0.7 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Convention Center - Exhibit Space | 0.61 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Copy/Print Room | 0.31 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Corridor - All other | 0.41 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Corridor - Facility for the visually impaired not used primarily by the staff | 0.71 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Corridor - Hospital | 0.71 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | ADD2 | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | ADD2 | ADD2 | ADD2 | NA | NA | NA | NA
Courtroom | 1.2 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - All other dining areas | 0.43 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - Bar/lounge or leisure dining | 0.86 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - Cafeteria or fast food dining | 0.4 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - Facility for the visually impaired not used primarily by the staff | 1.27 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - Family dining | 0.6 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dining Area - Penitentiary | 0.42 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Dormitory - Living Quarters | 0.5 | 8 | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Electrical/Mechanical Room | 0.43 | 6 | REQ | NA | NA | NA | REQ | REQ | NA | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Emergency Vehicle Garage | 0.52 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Fire Station - Sleeping Quarters | 0.23 | 6 | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Food Preparation Area | 1.09 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Guest Room | 0.41 | 6 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | REQ | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | REQ
Gymnasium/Fitness Center - Exercise area | 0.9 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Gymnasium/Fitness Center - Playing area | 0.85 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Corridor | 0.71 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | ADD2 | ADD2 | ADD2 | NA | NA | NA | NA | 5 | Corridor - Hospital | REQ | NA | NA | NA | NA | NA | ADD2 | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Exam/treatment room | 1.4 | 8 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Imaging room | 0.94 | 6 | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare facility - Lounge/Breakroom | 0.42 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA | Lounge/Breakroom - Healthcare facility | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Healthcare Facility - Medical supply room <50 ft2 | 0.51 | 9 | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Medical supply room >=50 ft2 | 0.38 | 6 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Healthcare Facility - Nurse’s station | 1.17 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Nursery | 0.92 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Operating room | 2.26 | 6 | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Patient room | 0.68 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Physical therapy room | 0.91 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Healthcare Facility - Recovery room | 1.25 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Laboratory - All other laboratories | 1.33 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Laboratory - In or as a classroom | 1.11 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 3 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Laundry/Washing Area | 0.53 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Library - Reading area | 0.96 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Library - Stacks | 1.18 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Loading Dock, Interior | 0.88 | 6 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - All other lobbies | 0.84 | 4 | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - Elevator | 0.65 | 6 | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - Facility for the visually impaired and not used primarily by the staff | 1.69 | 4 | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - Hotel | 0.51 | 4 | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - Motion picture theater | 0.23 | 4 | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Lobby - Performing arts theater | 1.25 | 6 | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Locker Room | 0.52 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Lounge/Breakroom - All other lounges/breakrooms | 0.59 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Lounge/Breakroom - Healthcare facility | 0.42 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Manufacturing Facility - Detailed manufacturing area | 0.8 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Manufacturing Facility - Equipment room | 0.76 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Manufacturing Facility - Extra high bay area (>50 ft floor-to-ceiling height) | 1.42 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Manufacturing Facility - High bay area (25 to 50 ft floor-to-ceiling height) | 1.24 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Manufacturing Facility - Low bay area (<25 ft floor-to-ceiling height) | 0.86 | 3 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Motion picture theater - Audience Seating Area | 0.27 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA | Audience Seating Area - Motion picture theater | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Motion picture theater - Lobby | 0.23 | 4 | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA | Lobby - Motion picture theater | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Museum - General exhibition area | 0.31 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Museum - Restoration room | 1.1 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Office - Enclosed and <=250 ft2 | 0.74 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | 2 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Office - Enclosed and >250 ft2 | 0.66 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 2 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Office - Open plan | 0.61 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 1 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Parking Area, Interior | 0.15 | 4 | NA | NA | NA | NA | NA | NA | NA | NA | REQ | REQ | REQ | REQ | NA | 5 |  | NA | NA | NA | NA | NA | NA | NA | NA | REQ | REQ | REQ | REQ | NA
Penitentiary - Audience Seating Area | 0.67 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA | Audience Seating Area - Penitentiary | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Penitentiary - Classroom/Lecture Hall/Training Room | 0.89 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Penitentiary - Dining Area | 0.42 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 | Dining Area - Penitentiary | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Performing Arts theater - Audience Seating Area | 1.16 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA | Audience Seating Area - Performing arts theater | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Performing Arts Theater - Dressing Room | 0.41 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Performing Arts theater - Lobby | 1.25 | 6 | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 | Lobby - Performing arts theater | REQ | NA | NA | NA | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Pharmacy Area | 1.66 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Post Office - Sorting Area | 0.76 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Recreation room/common living room - Facility for the Visually Impaired not used primarily by staff | 1.77 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Religious facility - Audience Seating Area | 0.72 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA | Audience Seating Area - Religious facility | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Religious Facility - Fellowship hall | 0.54 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Religious Facility - Worship/pulpit/choir area | 0.85 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Restroom - All other restrooms | 0.63 | 8 | NA | NA | NA | NA | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Restroom - Facility for the visually impaired nd not used primarily by the staff | 1.26 | 8 | NA | NA | NA | NA | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Retail Facilities - Dressing/fitting room | 0.51 | 8 | REQ | ADD1 | ADD1 | REQ | NA | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Retail Facilities - Mall concourse | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Sales Area | 1.05 | 6 | REQ | ADD1 | ADD1 | REQ | NA | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | 4 |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Seating Area, General | 0.23 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Sports arena - Audience Seating Area | 0.33 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Sports Arena Playing Area - Class I facility | 2.94 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Sports Arena Playing Area - Class II facility | 2.01 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Sports Arena Playing Area - Class III facility | 1.3 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Sports Arena Playing Area - Class IV facility | 0.86 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Stairwell | 0.49 | 10 | NA | NA | NA | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | 5 |  | NA | NA | NA | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Storage Room <50 ft2 | 0.51 | 9 | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Storage Room >=50 ft2 | 0.38 | 6 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | REQ | NA | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | REQ | NA | NA | NA | NA | NA
Transportation Facility - Airport concourse | 0.25 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Transportation Facility - Baggage/carousel area | 0.39 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Transportation Facility - Terminal ticket counter | 0.51 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Vehicular Maintenance Area | 0.6 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
Warehouse Storage - Medium to bulky, palletized items | 0.33 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Warehouse Storage - Smaller, hand-carried items | 0.69 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | REQ | ADD2 | ADD2 | NA | NA | NA | NA
Workshop | 1.26 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | NA | NA | NA |  | REQ | ADD1 | ADD1 | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | NA | NA
[18 empty] | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
2010 Spaces | 2010 LPD | 2010 RCR | 9.4.1.1 Automatic Lighting Shutoff | 9.4.1.2 Space Control (a) Bi-Level | 9.4.1.2 Space Control (b) Occ | 9.4.1.2 Space Control (c) | 9.4.1.4 Automatic Daylighting Controls for Primary Sidelighted Areas | 9.4.1.5 Automatic Daylighting Controls for Toplighting | 9.4.1.6 Additional Control | Not Used | Not Used2 | 9.4.1.3.b Parking Garage Control | 9.4.1.3.c Parking Garage Control | 9.4.1.3.d Parking Garage Control | Guest Room 9.4.1.6c | Column2 | Master | 9.4.1.1 Automatic Lighting Shutoff2 | 9.4.1.2 Space Control (a) Bi-Level3 | 9.4.1.2 Space Control (b) Occ4 | 9.4.1.2 Space Control (c)5 | 9.4.1.4 Automatic Daylighting Controls for Primary Sidelighted Areas6 | 9.4.1.5 Automatic Daylighting Controls for Toplighting7 | 9.4.1.6 Additional Control8 | Not Used9 | Not Used210 | 9.4.1.3.b Parking Garage Control11 | 9.4.1.3.c Parking Garage Control12 | 9.4.1.3.d Parking Garage Control13 | Guest Room 9.4.1.6c14 |  |  | 2010 9.6.2c2
2010 Spaces | 2010 LPD | 2010 RCR | 9.4.1.1 Automatic Lighting Shutoff | 9.4.1.2 Space Control (a) Bi-Level | 9.4.1.2 Space Control (b) Occ | 9.4.1.2 Space Control (c) | 9.4.1.4 Daylighting Controls for Sidelighted Areas | 9.4.1.5 Daylighting Controls for Toplighting | 9.4.1.6 Additional Control | Not Used | Not Used | 9.4.1.3.b Parking Garage Control | 9.4.1.3.c Parking Garage Control | 9.4.1.3.d Parking Garage Control | Guest Room 9.4.1.6c | NA |  | 9.4.1.1 Automatic Lighting Shutoff | 9.4.1.2 Space Control (a) Bi-Level | 9.4.1.2 Space Control (b) Occ | 9.4.1.2 Space Control (c) | 9.4.1.4 Daylighting Controls for Primary Sidelighted Areas | 9.4.1.5 Automatic Daylighting Controls for Toplighting | 9.4.1.6 Additional Control | Not Used | Not Used | 9.4.1.3.b Parking Garage Control | 9.4.1.3.c Parking Garage Control | 9.4.1.3.d Parking Garage Control | Guest Room 9.4.1.6c |  |  | 2010 9.6.2c2
Atrium <20 ft in height | 0.03 | NA | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Atrium >=20 ft and <40 ft in height | 0.03 | NA | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Atrium >40 ft in height | 0.02 | NA | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Audience Seating Area - Auditorium | 0.79 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Audience Seating Area - Convention center | 0.82 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Audience Seating Area - Gymnasium | 0.43 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Audience Seating Area - Motion picture theater | 1.14 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Audience Seating Area - Penitentiary | 0.43 | 4 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Audience Seating Area - Performing arts theater | 2.43 | 8 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Audience Seating Area - Religious facility | 1.53 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Audience Seating Area - Sports arena | 0.43 | 4 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Audience Seating Area - Transportation | 0.54 | 4 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Banking Activity Area | 1.38 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Classroom/Lecture Hall/Training Room - All other classrooms/lecture halls/training rooms | 1.24 | 4 | REQ | REQ | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 3 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Conference Room, Meeting Room, Classroom (Lecture/Training)
Classroom/Lecture Hall/Training Room - Penitentiary | 1.34 | 4 | REQ | REQ | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 3 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Conference Room, Meeting Room, Classroom (Lecture/Training)
Conference/Meeting/Multipurpose Room | 1.23 | 6 | REQ | REQ | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 3 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Conference Room, Meeting Room, Classroom (Lecture/Training)
Confinement Cells | 1.1 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Convention Center - Exhibit Space | 1.45 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Corridor - All other | 0.66 | 8' wide | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Corridor - Hospital | 0.89 | 8' wide | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Corridor - Manufacturing facility | 0.41 | 8' wide | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Courtroom | 1.72 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Dining Area - All other dining areas | 0.65 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Bar/lounge or leisure dining | 1.31 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Family dining | 0.89 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Hotel | 0.82 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Highway Lodging | 0.88 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Penitentiary | 1.07 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dormitory - Living Quarters | 0.38 | 8 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Electrical/Mechanical Room | 0.95 | 6 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Fire Stations - Engine Room | 0.56 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Fire Station - Sleeping Quarters | 0.25 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Food Preparation Area | 0.99 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Guest Room - Hotel | 1.11 | 6 | REQ | REQ | NA | REQ | REQ | REQ | NA | NA | NA | NA | NA | NA | REQ | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | REQ
Guest Room - Highway Lodging | 0.75 | 6 | REQ | REQ | NA | REQ | REQ | REQ | NA | NA | NA | NA | NA | NA | REQ | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | REQ
Gymnasium/Fitness Center - Exercise area | 0.72 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Gymnasium/Fitness Center - Playing area | 1.2 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Heathcare Facility - Emergency | 2.26 | 6 | NA | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA | [11 empty] | NA | NA | NA | bar: 18 to 27
Healthcare Facility - Exam/treatment room | 1.66 | 8 | NA | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA | [11 empty] | NA | NA | NA |  |  | NA | bar: 18 to 27
Healthcare Facility - Imaging room | 1.32 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Healthcare Facility - Medical supply room <50 ft2 | 0.63 | 6 | REQ | NA | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Healthcare Facility - Medical supply room >=50 ft2 | 0.63 | 6 | REQ | NA | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Healthcare Facility - Nurse’s station | 0.87 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Healthcare Facility - Nursery | 0.88 | 6 | NA | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA | [11 empty] | NA | NA | NA |  |  | NA | bar: 18 to 27
Healthcare Facility - Operating room | 1.89 | 6 | NA | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA | [11 empty] | NA | NA | NA |  |  | NA | bar: 18 to 27
Healthcare Facility - Patient room | 0.62 | 6 | NA | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA | [11 empty] | NA | NA | NA |  |  | NA | bar: 18 to 27
Healthcare Facility - Physical therapy room | 0.91 | 6 | NA | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA | [11 empty] | NA | NA | NA |  |  | NA | bar: 18 to 27
Healthcare Facility - Recovery room | 1.15 | 6 | NA | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA | [11 empty] | NA | NA | NA |  |  | NA | bar: 18 to 27
Judges' Chambers | 1.17 | 8 | REQ | REQ | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 2 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Private Office
Laboratory - All other laboratories | 1.81 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Laboratory - In or as a classroom | 1.28 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 3 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Conference Room, Meeting Room, Classroom (Lecture/Training)
Laundry/Washing Area | 0.6 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Library - Card File and Cataloging | 0.72 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Library - Reading area | 0.93 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Library - Stacks | 1.71 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Lobby - All other lobbies | 0.9 | 4 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Elevator | 0.64 | 6 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Hotel | 1.06 | 4 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Motion picture theater | 0.52 | 4 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Performing arts theater | 2 | 6 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Locker Room | 0.75 | 6 | REQ | REQ | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Lounge/Breakroom - All other lounges/breakrooms | 0.73 | 4 | REQ | REQ | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Lounge/Breakroom - Healthcare facility | 1.07 | 6 | REQ | REQ | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Manufacturing Facility - Detailed manufacturing area | 1.29 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Manufacturing Facility - Equipment room | 0.95 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Manufacturing Facility - Extra high bay area (>50 ft floor-to-ceiling height) | 1.05 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Manufacturing Facility - High bay area (25 to 50 ft floor-to-ceiling height) | 1.23 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Manufacturing Facility - Low bay area (<25 ft floor-to-ceiling height) | 1.19 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Museum - General exhibition area | 1.05 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Museum - Restoration room | 1.02 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Office - Enclosed and <=250 ft2 | 1.11 | 8 | REQ | REQ | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 2 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Private Office
Office - Enclosed and >250 ft2 | 1.11 | 8 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 2 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Private Office
Office - Open plan | 0.98 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 1 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Open Office
Parking Area, Interior | 0.19 | 4 | REQ | NA | NA | NA | NA | NA | 9.4.1.6 | NA | NA | REQ | REQ | REQ | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | REQ | REQ | REQ | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Performing Arts Theater - Dressing Room | 0.4 | 6 | REQ | NA | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Pharmacy Area | 1.14 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Post Office - Sorting Area | 0.94 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Religious Facility - Fellowship hall | 0.64 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Religious Facility - Worship/pulpit/choir area | 1.53 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Restroom - All other restrooms | 0.98 | 8 | REQ | NA | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Retail Facilities - Dressing/fitting room | 0.87 | 8 | REQ | REQ | REQ | NA | NA | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Retail Facilities - Mall concourse | 1.1 | 4 | REQ | NA | NA | REQ | NA | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Sales Area | 1.68 | 6 | REQ | REQ | NA | REQ | NA | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | 4 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Retail Sales Area
Sports Arena Playing Area - Class I facility | 3.01 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Sports Arena Playing Area - Class II facility | 1.92 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Sports Arena Playing Area - Class III facility | 1.2 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Sports Arena Playing Area - Class IV facility | 0.72 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Stairwell | 0.69 | 10 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6g | NA | NA | NA | NA | NA | NA | 5 |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Storage Room <50 ft2 | 0.63 | 6 | REQ | NA | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Storage Room >=50 ft2 | 0.63 | 6 | REQ | NA | REQ | NA | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Transportation Facility - Airport concourse | 0.36 | 4 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Transportation Facility - Baggage/carousel area | 0.76 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Transportation Facility - Terminal ticket counter | 1.08 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Vehicular Maintenance Area | 0.67 | 4 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Warehouse Storage - Medium to bulky, palletized items | 0.58 | 4 | REQ | NA | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Warehouse Storage - Smaller, hand-carried items | 0.95 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
Workshop | 1.59 | 6 | REQ | REQ | NA | REQ | REQ | REQ | 9.4.1.6 | NA | NA | NA | NA | NA | NA | NA |  | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | NA
20
14
|  |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13
2010 | 2010 LPD | 2010 RCR | 2010 9.4.1.1 Automatic Lighting Shutoff | 9.4.1.2 Space Control (a) Bi-Level | 9.4.1.2 Space Control (b) Occ | 9.4.1.2 Space Control (c) | 9.4.1.4 Automatic Daylighting Controls for Primary Sidelighted Areas | 9.4.1.5 Automatic Daylighting Controls for Toplighting | 9.4.1.6 Additional Control | Not Used | Not Used | 9.4.1.3.b Parking Garage Lighting Control | 9.4.1.3.c Parking Garage Lighting Control | 9.4.1.3.d Parking Garage Lighting Control | Guest Room 9.4.1.3b.2 | 2016 9.6.2c | Master
2016 | 2016 LPD | 2016 RCR | 2016 Local Control (9.4.1.1[a]) | 2016 Restricted to Manual ON (9.4.1.1[b]) | 2016 Restricted to Partial Automatic ON (9.4.1.1[c]) | 2016 Bilevel Lighting Control (9.4.1.1[d]) | 2016 Automatic Daylight Responsive Controls for Sidelighting (9.4.1.1[e]6) | 2016 Automatic Daylight Responsive Controls for Toplighting (9.4.1.1[f]6) | 2016 Automatic Partial OFF (9.4.1.1[g] [Full Off complies]) | 2016 Automatic Full OFF (9.4.1.1[h]) | 2016 Scheduled Shutoff (9.4.1.1[i]) | Garage 9.4.1.2b | Garage 9.4.1.2c | Garage 9.4.1.2d | Guest Room 9.4.1.3b.2 | 2019 9.6.2c | Master
2019 | 2019 LPD | 2019 RCR | 2019 Local Control (9.4.1.1[a]) | 2019 Restricted to Manual ON (9.4.1.1[b]) | 2019 Restricted to Partial Automatic ON (9.4.1.1[c]) | 2019 Bilevel Lighting Control (9.4.1.1[d]) | 2019 Automatic Daylight Responsive Controls for Sidelighting (9.4.1.1[e]6) | 2019 Automatic Daylight Responsive Controls for Toplighting (9.4.1.1[f]6) | 2019 Automatic Partial OFF (9.4.1.1[g] [Full Off complies]) | 2019 Automatic Full OFF (9.4.1.1[h]) | 2019 Scheduled Shutoff (9.4.1.1[i]) | Garage 9.4.1.2b | Garage 9.4.1.2c | Garage 9.4.1.2d | Guest Room 9.4.1.3b.3

## 9.6.2c
Table 9.6.2 Control Factors in Calculating Additional Lighting Power Allowance
Method # | Description | Open Office | Private Office | Conference Room, Meeting Room, Classroom (Lecture/Training) | Retail Sales Area | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | NA
01 | Manual, continuous dimming control or Programmable multi-level dimming control | 0.05 | 0.05 | 0.1 | 0.1 | 0 | 0
02 | Programmable multi-level dimming control using programmable time scheduling | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0
03 | Multi-level occupancy sensors | 0.05 | 0.05 | 0.05 | 0 | 0 | 0
04 | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off capabilities. | 0.25 | 0 | 0 | 0 | 0 | 0
05 | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off operation, in combination with personal continuous dimming control of downlight illumination by workstation occupant. | 0.3 | 0 | 0 | 0 | 0 | 0
06 | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 | 0 | 0 | 0 | 0.1 | 0 | 0
07 | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
08 | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0
09 | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is greater than 250 sq.ft | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
10 | Automatic continuous daylight dimming in secondary sidelighted areas when sidelighting effective aperture is greater than 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
11 | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is less than 900 sq.ft and when skylight effective aperture is greater than 0.01 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0
12 | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is greater than 900 sq.ft and when skylight effective aperture is greater than 0.01 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
Footnotes
1 | These control factors may only be used if the requirements of section 9.4.1.2 are met using an occupancy sensor.
2 | Control factor is limited to the wattage of workstation-specific luminaires in partitioned single occupant workspaces contained within an open office environment (i.e. direct-indirect luminaires with separately controlled downlight and uplight components, with the downward component providing illumination to a single occupant in an open plan workstation). Within 30 minutes of the occupant leaving the space, the downward component shall continuously dim to off over a minimum of 2 minutes. Upon the occupant entering the space, the downward component shall turn on at the minimum level and continuously raise the illumination to a preset level over a minimum of 30 seconds. The uplight component of workstation specific luminaire shall comply with section 9.4.1.1 (automatic shutoff).
3 | In addition to the requirements described in footnote 2, the control shall allow the occupant to select their preferred light level via a personal computer, handheld device, or similarly accessible device located within the workstation.
4 | Control factors may not be used if controls are used to satisfy exceptions to Section 5.5.4.2.3
| Open Office | 1
| Private Office | 2
| Conference Room, Meeting Room, Classroom (Lecture/Training) | 3
| Retail Sales Area | 4
| Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | 5
| NA | 6
[8 empty] | Method # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
[8 empty] | Description | Manual, continuous dimming control or Programmable multi-level dimming control | Programmable multi-level dimming control using programmable time scheduling | Multi-level occupancy sensors | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off capabilities. | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off operation, in combination with personal continuous dimming control of downlight illumination by workstation occupant. | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is greater than 250 sq.ft | Automatic continuous daylight dimming in secondary sidelighted areas when sidelighting effective aperture is greater than 0.3 | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is less than 900 sq.ft and when skylight effective aperture is greater than 0.01 | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is greater than 900 sq.ft and when skylight effective aperture is greater than 0.01
[8 empty] | Open Office | 0.05 | 0.05 | 0.05 | 0.25 | 0.3 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[8 empty] | Private Office | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[8 empty] | Conference Room, Meeting Room, Classroom (Lecture/Training) | 0.1 | 0.1 | 0.05 | 0 | 0 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[8 empty] | Retail Sales Area | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[8 empty] | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | 0 | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
Note on F4: See footnote 1
Note on F5: These control factors may only be used if the requirements of section 9.4.1.2 are met using an occupancy sensor.
Note on C7: See footnote 2.
Note on C8: See footnote 3.
Note on C9: See footnote 4.
Note on W45: See footnote 2.
Note on X45: See footnote 3.
Note on Y45: See footnote 4.
Note on T48: See footnote 1
Note on U48: These control factors may only be used if the requirements of section 9.4.1.2 are met using an occupancy sensor.

## 9.6.3 Table
Table 9.63 Control Factors in Calculating Additional Lighting Power Allowance
Method # | Description | Open Office | Private Office | Conference Room, Meeting Room, Classroom (Lecture/Training) | Retail Sales Area | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | NA
|  | 1 | 2 | 3 | 4 | 5
1 | Manual, continuous dimming control or Programmable multi-level dimming control | 0.05 | 0.05 | 0.1 | 0.1 | 0 | 0 |  |  | 9.6.3 - Manual dimming
2 | Programmable multi-level dimming control using programmable time scheduling | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0 |  |  | 9.6.3 - Programmable multi-level dimming
3 | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off capabilities. | 0.25 | 0 | 0 | 0 | 0 | 0 | a |  | 9.6.3 - Manual dimming
4 | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off operation, in combination with personal continuous dimming control of downlight illumination by workstation occupant. | 0.3 | 0 | 0 | 0 | 0 | 0 | a | b | 9.6.3 - Manual dimming
5 | Automatic continuous daylight dimming in secondary sidelighted areas when sidelighting effective aperture is greater than 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | c |  | 9.6.3 - Manual dimming
Footnotes
a | Control factor is limited to the wattage of workstation-specific luminaires in partitioned single occupant workspaces contained within an open office environment (i.e. direct-indirect luminaires with separately controlled downlight and uplight components, with the downward component providing illumination to a single occupant in an open plan workstation). Within 30 minutes of the occupant leaving the space, the downward component shall continuously dim to off over a minimum of 2 minutes. Upon the occupant entering the space, the downward component shall turn on at the minimum level and continuously raise the illumination to a preset level over a minimum of 30 seconds. The uplight component of workstation specific luminaire shall comply with section 9.4.1.1 (automatic shutoff).
b | In addition to the requirements described in footnote 2, the control shall allow the occupant to select their preferred light level via a personal computer, handheld device, or similarly accessible device located within the workstation.
c | Control factors may not be used if controls are used to satisfy exceptions to Section 5.5.4.2.3
| Open Office | 1
| Private Office | 2
| Conference Room, Meeting Room, Classroom (Lecture/Training) | 3
| Retail Sales Area | 4
| Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | 5
| NA | 6
[11 empty] | Method # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
[11 empty] | Description | Manual, continuous dimming control or Programmable multi-level dimming control | Programmable multi-level dimming control using programmable time scheduling | Multi-level occupancy sensors | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off capabilities. | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off operation, in combination with personal continuous dimming control of downlight illumination by workstation occupant. | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is greater than 250 sq.ft | Automatic continuous daylight dimming in secondary sidelighted areas when sidelighting effective aperture is greater than 0.3 | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is less than 900 sq.ft and when skylight effective aperture is greater than 0.01 | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is greater than 900 sq.ft and when skylight effective aperture is greater than 0.01
[11 empty] | Open Office | 0.05 | 0.05 | 0.05 | 0.25 | 0.3 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[11 empty] | Private Office | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[11 empty] | Conference Room, Meeting Room, Classroom (Lecture/Training) | 0.1 | 0.1 | 0.05 | 0 | 0 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[11 empty] | Retail Sales Area | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[11 empty] | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | 0 | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
Note on C7: See footnote 2.
Note on C8: See footnote 3.
Note on W38: See footnote 2.
Note on X38: See footnote 3.
Note on Y38: See footnote 4.
Note on T41: See footnote 1
Note on U41: These control factors may only be used if the requirements of section 9.4.1.2 are met using an occupancy sensor.

## Simplified Tables
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 0 |  | automatic off when building is unoccupied | manual reduction by at least 50% within 20 minutes | manual-ON occupant sensors | manual-ON or auto-ON occupant sensors | occupant sensor reduction by at least 50% within 20 minutes | reduce the general lighting by 75% during nonbusiness hours | turn off all non-general lighting during non-business hours | Top lighting daylight dimming
Used in calculation | Table 9.3.1-2 Simplified Building Method for 0 Buildings
| Interior Space Type | Interior Lighting Power Allowance
|  |  | automatic off when building is unoccupied | manual control device reducing the lighting power by a minimum of 50% when no activity is detected for not longer than 20 minutes | manual-ON occupant sensors | manual-ON or auto-ON occupant sensors | occupant sensor reducing the lighting power by a minimum of 50% when no activity is detected for not longer than 20 minutes
a. All lights in the space shall be controlled.
Table 9.3.1-1 Simplified Building Method for Office Buildings
| Interior Space Type | Interior Lighting Power Allowance | [8 empty] | Controls (All lights in the space shall be controlled)
Office | Office spaces less than or equal to 250 ft2 | 0.7 | REQ | REQ | REQ | NA | NA | NA | NA | NA | These spaces shall also be controlled by manual-ON occupant sensors.
Office | Offices greater than 250 ft2 | 0.7 | REQ | REQ | NA | REQ | NA | NA | NA | NA | These spaces shall also be controlled by occupant sensors.
Office | classrooms and training rooms | 0.7 | REQ | REQ | REQ | NA | NA | NA | NA | NA | These spaces shall also be controlled by manual-ON occupant sensors.
Office | conference, meeting, and break rooms | 0.7 | REQ | REQ | REQ | NA | NA | NA | NA | NA | These spaces shall also be controlled by manual-ON occupant sensors.
Office | storage rooms | 0.7 | REQ | REQ | REQ | NA | NA | NA | NA | NA | These spaces shall also be controlled by manual-ON occupant sensors.
Office | Restrooms | 0.7 | REQ | REQ | NA | REQ | NA | NA | NA | NA | These spaces shall also be controlled by occupant sensors.
Office | Stairwells and corridors | 0.7 | REQ | NA | NA | NA | REQ | NA | NA | NA | These spaces shall also be controlled by occupant sensors.
Office | All other spaces | 0.7 | REQ | REQ | NA | NA | NA | NA | NA | NA | All lighting shall be automatically controlled to turn off when the building is either unoccupied or scheduled to be unoccupied. (Exception: Lighting load not exceeding 0.02 W/ft2 multiplied by the gross lighted area of the building shall be permitted to operate at all times.) Each space shall have a manual control device that allows the occupant to reduce lighting power by a minimum of 50% and to turn the lighting off.
Office | Stairwells and corridors in parking garages | 0.7 | REQ | NA | NA | NA | REQ | NA | NA | NA | These spaces shall also be controlled by occupant sensors.
Office | Parking Garages | 0.13 | REQ | NA | NA | NA | REQ | NA | NA | NA | All lighting shall be automatically controlled to turn off during garage nonoperating hours. Lighting shall also be controlled by occupant sensors. Controls shall reduce the power by a minimum of 50% when no activity is detected for not longer than 20 minutes. No device shall control more than 3600 ft2.
|  |  | automatic off when building is unoccupied | manual control device reducing the lighting power by a minimum of 50% when no activity is detected for not longer than 20 minutes | manual-ON occupant sensors | manual-ON or auto-ON occupant sensors | occupant sensor reducing the lighting power by a minimum of 50% when no activity is detected for not longer than 20 minutes | controls to reduce ethe general lighting power by 75% during nonbusiness hours | turn off all lighting other than general lighting during nonbusiness hours | Top lighting daylight dimming
a When the combined input power of the general lights completely or partially within the daylight areas is 150 watts or greater.
Table 9.3.1-2 Simplified Building Method for Retail Buildings
| Interior Space Type | Interior Lighting Power Allowance | [8 empty] | Controls (All lights in the space shall be controlled)
Retail | Sales area | 1 | REQ | NA | NA | NA | NA | REQ | REQ | REQ | These spaces shall also be controlled • to reduce the general lighting power by a minimum of 75% during nonbusiness hours, • to turn off all lighting other than general lighting during nonbusiness hours, and • by continuous daylight dimming controls b in spaces with toplighting.
Retail | Stock, dressing/fitting, locker, and restrooms | 1 | REQ | REQ | NA | REQ | NA | NA | NA | REQ | These spaces shall also be controlled by; auto-ON or manual-ON occupant sensors, and continuous daylight dimming controls b in spaces with toplighting.
Retail | Office spaces | 1 | REQ | REQ | REQ | NA | NA | NA | NA | REQ | These spaces shall also be controlled by; manual-ON occupant sensors, and continuous daylight dimming controls b in spaces with toplighting.
Retail | conference, meeting, training, and break rooms | 1 | REQ | REQ | REQ | NA | NA | NA | NA | REQ | These spaces shall also be controlled by; manual-ON occupant sensors, and continuous daylight dimming controls b in spaces with toplighting.
Retail | storage rooms and utility spaces | 1 | REQ | REQ | REQ | NA | NA | NA | NA | REQ | These spaces shall also be controlled by; manual-ON occupant sensors, and continuous daylight dimming controls b in spaces with toplighting.
Retail | Stairwells and corridors | 1 | REQ | NA | NA | NA | REQ | NA | NA | NA | These spaces shall also be controlled by occupant sensors that reduce the lighting power by a minimum of 50% when no activity is detected for not longer than 20 minutes and be controlled to turn off when the building is either unoccupied or scheduled to be unoccupied.
Retail | All other spaces | 1 | REQ | REQ | NA | NA | NA | NA | NA | NA | All lighting shall be automatically controlled to turn off when the building is either unoccupied or scheduled to be unoccupied. (Exception: Lighting load not exceeding 0.02 W/ft2 multiplied by the gross lighted area of the building shall be permitted to operate at all times.) Each space shall have a manual control device that allows the occupant to reduce lighting power by a minimum of 50% and to turn the lighting off.
Retail | Stairwells and corridors in parking garages | 1 | REQ | NA | NA | NA | REQ | NA | NA | NA | These spaces shall also be controlled by occupant sensors.
Retail | Parking Garages | 0.13 | REQ | NA | NA | NA | REQ | NA | NA | NA | All lighting shall be automatically controlled to turn off during garage nonoperating hours. Lighting shall also be controlled by occupant sensors. Controls shall reduce the power by a minimum of 50% when no activity is detected for not longer than 20 minutes. No device shall control more than 3600 ft2.
|  |  | NA | NA | NA | NA | NA | NA | NA | NA
|  |  | automatic off when building is unoccupied | manual control device reducing the lighting power by a minimum of 50% when no activity is detected for not longer than 20 minutes | manual-ON occupant sensors | manual-ON or auto-ON occupant sensors | occupant sensor reducing the lighting power by a minimum of 50% when no activity is detected for not longer than 20 minutes
Table 9.3.1-3 Simplified Building Method for School Buildings
| Interior Space Type | Interior Lighting Power Allowance | [8 empty] | Controls (All lights in the space shall be controlled)
School | Office spaces | 0.7 | REQ | REQ | NA | REQ | NA | NA | NA | NA | These spaces shall also be controlled by occupant sensors.
| Classrooms | 0.7 | REQ | REQ | NA | REQ | NA | NA | NA | NA | These spaces shall also be controlled by manual-ON occupant sensors.
| conference, meeting, and break rooms | 0.7 | REQ | REQ | NA | REQ | NA | NA | NA | NA | These spaces shall also be controlled by manual-ON occupant sensors.
| library and storage rooms | 0.7 | REQ | REQ | NA | REQ | NA | NA | NA | NA | These spaces shall also be controlled by manual-ON occupant sensors.
| Gymnasiums and cafeterias | 0.7 | REQ | REQ | NA | REQ | NA | NA | NA | NA | These spaces shall also be controlled by occupant sensors
| Restrooms | 0.7 | REQ | REQ | NA | REQ | NA | NA | NA | NA | These spaces shall also be controlled by occupant sensors
| Stairwells and corridors | 0.7 | REQ | NA | NA | NA | REQ | NA | NA | NA | These spaces shall also be controlled by occupant sensors that reduce the lighting power by a minimum of 50% when no activity is detected for not longer than 20 minutes and be controlled to turn off when the building is either unoccupied or scheduled to be unoccupied.
| All other spaces | 0.7 | REQ | REQ | NA | NA | NA | NA | NA | NA | All lighting shall be automatically controlled to turn off when the building is either unoccupied or scheduled to be unoccupied. (Exception: Lighting load not exceeding 0.02 W/ft2 multiplied by the gross lighted area of the building shall be permitted to operate at all times.) Each space shall have a manual control device that allows the occupant to reduce lighting power by a minimum of 50% and to turn the lighting off.
| Stairwells and corridors in parking garages | 0.7 | REQ | NA | NA | NA | REQ | NA | NA | NA | These spaces shall also be controlled by occupant sensors.
| Parking Garages | 0.13 | REQ | NA | NA | NA | REQ | NA | NA | NA | All lighting shall be automatically controlled to turn off during garage nonoperating hours. Lighting shall also be controlled by occupant sensors. Controls shall reduce the power by a minimum of 50% when no activity is detected for not longer than 20 minutes. No device shall control more than 3600 ft2.
|  |  |  | Auto off during daylight hours | power reduced by a minimum of 75% during nonoperating hours | Luminaires mounted 25 ft or less above grade shall be controlled to reduce the power by at least 50% when no activity is detected for not longer than 15 minutes.
0
Table 9.3.2 Simplified Building Method for Building Exteriors
| Exterior Area Type | Exterior Lighting Power Allowance a,b | Calculated for LZ | [7 empty] | Controls c
| Base allowance | 200 | 0 | REQ | REQ | NA | W |  |  |  | Luminaires shall be turned off or the power reduced by a minimum of 75% during nonoperating hours.
| Façade lighting | 0.1 | 0 | REQ | REQ | NA | W/ft2 |  |  |  | Luminaires shall be turned off or the power reduced by a minimum of 75% during nonoperating hours.
| Special feature areas | 0.1 | 0 | REQ | REQ | NA | W/ft2 |  |  |  | Luminaires shall be turned off or the power reduced by a minimum of 75% during nonoperating hours.
| walkways, plazas | 0.1 | 0 | REQ | REQ | NA | W/ft2 |  |  |  | Luminaires shall be turned off or the power reduced by a minimum of 75% during nonoperating hours.
| Landscape | 0.04 | 0 | REQ | REQ | NA | W/ft2 |  |  |  | Luminaires shall be turned off or the power reduced by a minimum of 75% during nonoperating hours.
| Entry doors (per linear foot) | 14 | 0 | REQ | REQ | NA | W/linear foot |  |  |  | Luminaires shall be turned off or the power reduced by a minimum of 75% during nonoperating hours.
| Stairs and ramps | 0.7 | 0 | REQ | NA | NA | W/ft2 |  |  |  | No additional controls required.
| Parking lots and drives | 0.05 | 0 | REQ | NA | REQ | W/ft2 |  |  |  | Luminaires mounted 25 ft or less above grade shall be controlled to reduce the power by at least 50% when no activity is detected for not longer than 15 minutes.
| All other areas not listed | 0.2 | 0 | REQ | REQ | NA | W/ft2 |  |  |  | Luminaires shall be turned off or the power reduced by a minimum of 75% during nonoperating hours.
a. To calculate the exterior allowance, multiply the space or area square footage by the allowed W/ft2 and sum the exterior allowances and the base allowance.
Façade lighting shall be calculated separately by multiplying the façade area by the allowed W/ft2. Façade allowance shall not be traded with other exterior areas
or between separate façade areas.
b. For buildings in Lighting Zone 2, as defined in Table 9.4.2-1, decrease exterior allowances by 20%. For buildings in Lighting Zone 4, as defined in Table 9.4.2-1,
increase exterior allowances by 25%.
c. All exterior lighting shall be automatically controlled by either a photocell or an astronomical time switch to shut off the lighting when daylight is available.

## LISTS (hidden)
Compliance Codes (ComCodes) |  |  | Building Types (BuildingType) | LPD |  | Space-by-Space Building Types (SBuildingType) | [14 empty] | Units | Current | LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | Units | 1 | Control Types
90.1-2001 |  |  | Automotive Facility | 0.82 |  | 1-Common Space Types | [5 empty] | Manual, continuous dimming control or Programmable multi-level dimming control | [7 empty] | Base Allowance |  | #N/A | 0 | 500 | 600 | 750 | 1300 | watts | 2 | Building Automation
[8 empty] | Yes |  |  |  | Programmable multi-level dimming control using programmable time scheduling | [7 empty] | TRADABLE SURFACES | [8 empty] | 3 | Daylight Continuous Dimming
90.1-2004 |  |  | Convention Center | 1.08 |  | 2-Automotive |  | No |  |  |  | Multi-level occupancy sensors | [7 empty] | Uncovered parking areas and drives | sq.ft | #N/A | 0 | 0.04 | 0.06 | 0.1 | 0.13 | w/sq.ft | 4 | Daylight Step Dimming
90.1-2007 |  |  | Courthouse | 1.05 |  | 2-Bank/Office |  | Exempt |  |  |  | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off capabilities. | [7 empty] | Walkways < 10' wide | lin.ft | #N/A | 0 | 0.7 | 0.7 | 0.8 | 1 | w/lin.ft | 5 | Occupancy Sensor
90.1-2010 |  |  | Dining: Bar Lounge/Leisure | 0.99 |  | 2-Convention Center |  | NA |  |  |  | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off operation, in combination with personal continuous dimming control of downlight illumination by workstation occupant. | [7 empty] | Walkways ≥ 10' wide OR plazas | sq.ft | #N/A | 0 | 0.14 | 0.14 | 0.16 | 0.2 | w/sq.ft | 6 | Occupancy & Daylight sensors
|  |  | Dining: Cafeteria/Fast Food | 0.9 |  | 2-Courthouse/Police Station/Penitentiary | [5 empty] | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 | [7 empty] | Stairways | sq.ft | #N/A | 0 | 0.75 | 1 | 1 | 1 | w/sq.ft | 7 | Timer Switch
Fixture Quantity Units (FQUnits) |  |  | Dining: Family | 0.89 |  | 2-Dormitory | [5 empty] | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | [7 empty] | Pedestrian tunnels | sq.ft | #N/A | 0 | 0.15 | 0.15 | 0.2 | 0.3 | w/sq.ft | 8 | Vacancy Sensor
EA | count |  | Dormitory | 0.61 |  | 2-Fire Stations | [5 empty] | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | [7 empty] | Landscaping | sq.ft | #N/A | 0 | 0.04 | 0.05 | 0.05 | 0.05 | w/sq.ft | 9 | Exterior Photocell
LF | linear feet |  | Exercise Center | 0.88 |  | 2-Gymnasium/Fitness Center | [5 empty] | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is greater than 250 sq.ft | [7 empty] | Main entries | lin.ft | #N/A | 0 | 20 | 20 | 30 | 30 | w/lin.ft | 10 | Astronomical Time Switch
|  |  | Fire Station | 0.71 |  | 2-Hospital | [5 empty] | Automatic continuous daylight dimming in secondary sidelighted areas when sidelighting effective aperture is greater than 0.3 | [7 empty] | Other doors | lin.ft | #N/A | 0 | 20 | 20 | 20 | 20 | w/lin.ft | 11 | Dimmer
YES/NO (YesNo) |  |  | Gymnasium | 1 |  | 2-Hotel/Motel | [5 empty] | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is less than 900 sq.ft and when skylight effective aperture is greater than 0.01 | [7 empty] | Entry canopies | sq.ft | #N/A | 0 | 0.25 | 0.25 | 0.4 | 0.4 | w/sq.ft | 12 | Multi-Scene Control
YES |  |  | Health-care Clinic | 0.87 |  | 2-Library | [5 empty] | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is greater than 900 sq.ft and when skylight effective aperture is greater than 0.01 | [7 empty] | Sales canopies | sq.ft | #N/A | 0 | 0.6 | 0.6 | 0.8 | 1 | w/sq.ft | 13 | 9.6.2c - Method 01
NO |  |  | Hospital | 1.21 |  | 2-Manufacturing | [13 empty] | Open sales areas | sq.ft | #N/A | 0 | 0.25 | 0.25 | 0.5 | 0.7 | w/sq.ft | 14 | 9.6.2c - Method 02
|  |  | Hotel | 1 |  | 2-Museum | [13 empty] | Street frontage | lin.ft | #N/A | 0 | 0 | 10 | 10 | 30 | w/lin.ft | 15 | 9.6.2c - Method 03
YES/NO/NA (YesNoNA) |  |  | Library | 1.18 |  | 2-Parking Garage | [13 empty] | NONTRADABLE SURFACES | [8 empty] | 16 | 9.6.2c - Method 04
YES |  |  | Manufacturing Facility | 1.11 |  | 2-Post Office | [13 empty] | Building facades by area | sq.ft | #N/A | 0 | 0 | 0.1 | 0.15 | 0.2 | w/sq.ft | 17 | 9.6.2c - Method 05
NO |  |  | Motel | 0.88 |  | 2-Religious Buildings | [13 empty] | Building facades by length | lin.ft | #N/A | 0 | 0 | 2.5 | 3.75 | 5 | w/lin.ft | 18 | 9.6.2c - Method 06
NA |  |  | Motion Picture Theater | 0.83 |  | 2-Retail | [13 empty] | ATMs & night depository location | locations | #N/A | 0 | 270 | 270 | 270 | 270 | watts | 19 | 9.6.2c - Method 07
|  |  | Multifamily | 0.6 |  | 2-Sports Arena | [13 empty] | Additional ATMs | additional ATMs | #N/A | 0 | 90 | 90 | 90 | 90 | watts | 20 | 9.6.2c - Method 08
|  |  | Museum | 1.06 |  | 2-Transportation | [13 empty] | Uncovered entrances & gatehouse inspection facilities at guarded facilities | sq.ft | #N/A | 0 | 0.75 | 0.75 | 0.75 | 0.75 | w/sq.ft | 21 | 9.6.2c - Method 09
Source Type (SourceType) |  |  | Office | 0.9 |  | 2-Warehouse | [13 empty] | Uncovered loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | sq.ft | #N/A | 0 | 0.5 | 0.5 | 0.5 | 0.5 | w/sq.ft | 22 | 9.6.2c - Method 10
|  |  | Parking Garage | 0.25 | [15 empty] | Drive-through windows/doors (per drive through) | drive-throughs | #N/A | 0 | 400 | 400 | 400 | 400 | watts | 23 | 9.6.2c - Method 11
|  |  | Penitentiary | 0.97 | [15 empty] | Parking near 24-hour retail entrances | entrances | #N/A | 0 | 800 | 800 | 800 | 800 | watts | 24 | 9.6.2c - Method 12
|  |  | Performing Arts Theater | 1.39 | [7 empty] | Space Types (SSpaceType3) | LPD | RCR | Bi-Level | Occ |  |  |  | Roadway/parking entry, trail head, and toilet facility, or other locations approved by the authority having jurisdiction. | locations | #N/A | 60 | 0 | 0 | 0 | 0 | watts | 25
|  |  | Police | 0.96 |  | Atrium (first 40' in height) | 0.03/foot in height
|  |  | Post Office | 0.87 |  | Atrium ( height above 40') | 0.02/foot in height |  | LED |  | Atrium | C-Atrium | .03/.02 | na | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
|  |  | Religious Building | 1.05 |  | Audience/Seating Area - Auditorium | 0.79 |  | Fluorescent |  | Audience/Seating Area - Auditorium | C-Audience/Seating Area - Auditorium | 0.79 | 6 | Yes | No | NA |  |  | TABLE 9.4.2-1 Exterior Lighting Zones
|  |  | Retail | 1.4 |  | Audience/Seating Area - Motion Picture Theater | 1.14 |  | High Pressure Sodium |  | Audience/Seating Area - Motion Picture Theater | C-Audience/Seating Area - Motion Picture Theater | 1.14 | 4 | Yes | No | NA |  |  | Lighting Zone | Description
|  |  | School/University | 0.99 |  | Audience/Seating Area - Performing Arts Theater | 2.43 |  | Metal Halide |  | Audience/Seating Area - Performing Arts Theater | C-Audience/Seating Area - Performing Arts Theater | 2.43 | 8 | Yes | No | NA |  |  | 0 | Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction
Retail Area Type (RetailType) |  |  | Sports Arena | 0.78 |  | Classroom/Lecture/Training | 1.24 |  | Mercury Vapor |  | Classroom/Lecture/Training | C-Classroom/Lecture/Training | 1.24 | 4 | Yes | Yes | Conference Room, Meeting Room, Classroom (Lecture/Training)
1 | 0.6 |  | Town Hall | 0.92 |  | Conference/Meeting/Multipurpose | 1.23 |  | Low Pressure Sodium |  | Conference/Meeting/Multipurpose | C-Conference/Meeting/Multipurpose | 1.23 | 6 | Yes | Yes | Conference Room, Meeting Room, Classroom (Lecture/Training) |  |  | 1 | Developed areas of national parks, state parks, forest land, and rural areas
2 | 0.6 |  | Transportation | 0.77 |  | Corridor/Transition | 0.66 |  | Incandescent |  | Corridor/Transition | C-Corridor/Transition | 0.66 | 8' wide | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  |  | 2 | Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas
3 | 1.4 |  | Warehouse | 0.66 |  | Dining Area | 0.65 |  | Induction |  | Dining Area | C-Dining Area | 0.65 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
4 | 2.5 |  | Workshop | 1.2 |  | Dining Area - Bar Lounge/Leisure Dining | 1.31 |  | Plasma |  | Dining Area - Bar Lounge/Leisure Dining | C-Dining Area - Bar Lounge/Leisure Dining | 1.31 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  |  | 3 | All other areas
[6 empty] | Dining Area - Family Dining | 0.89 |  | Other |  | Dining Area - Family Dining | C-Dining Area - Family Dining | 0.89 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  |  | 4 | High-activity commercial districts in major metropolitan areas as designated by the local jurisdiction
Control Methods | [5 empty] | Dressing/Fitting Room - Performing Arts Theater | 0.4 |  |  |  | Dressing/Fitting Room - Performing Arts Theater | C-Dressing/Fitting Room - Performing Arts Theater | 0.4 | 6 | Yes | Yes | NA
1 |  | Open office |  |  |  | Electrical/Mechanical Room | 0.95 |  |  |  | Electrical/Mechanical Room | C-Electrical/Mechanical Room | 0.95 | 6 | No | No | NA
2 |  | Private office |  |  |  | Food Preperation | 0.99 |  |  |  | Food Preperation | C-Food Preperation | 0.99 | 6 | Yes | No | NA |  | Sel | Select
3 |  | Conference Room |  |  |  | Laboratory - Classroom | 1.28 |  |  |  | Laboratory - Classroom | C-Laboratory - Classroom | 1.28 | 6 | Yes | Yes | Conference Room, Meeting Room, Classroom (Lecture/Training)
4 |  | Meeting Room |  |  |  | Laboratory - Research | 1.81 |  |  |  | Laboratory - Research | C-Laboratory - Research | 1.81 | 6 | Yes | No | NA |  | LZ0 | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction
5 |  | Classroom (Lecture/Training) |  |  |  | Lobby | 0.64 |  |  |  | Lobby | C-Lobby | 0.9 | 4 | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  | LZ1 | LZ1 - Developed areas of national parks, state parks, forest land, and rural areas
6 |  | Retail Sales Area |  |  |  | Lobby - Motion Picture Theater | 0.52 |  |  |  | Lobby - Motion Picture Theater | C-Lobby - Elevator | 0.64 | 6 | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  | LZ2 | LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas
7 |  | Lobby |  |  |  | Lobby - Performing Arts Theater | 2 |  |  |  | Lobby - Performing Arts Theater | C-Lobby - Motion Picture Theater | 0.52 | 4 | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  | LZ3 | LZ3 - All other areas
8 |  | Atrium |  |  |  | Locker Room | 0.75 |  |  |  | Locker Room | C-Lobby - Performing Arts Theater | 2 | 6 | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  | LZ4 | LZ4 - High activity commercial districts in major metropolitan areas as designated by the local jurisdiction
9 |  | Dining Area |  |  |  | Lounge/Recreation | 0.73 |  |  |  | Lounge/Recreation | C-Locker Room | 0.75 | 6 | Yes | Yes | NA
10 |  | Stairways |  |  |  | Office-Enclosed | 1.11 |  |  |  | Office-Enclosed | C-Lounge/Recreation | 0.73 | 4 | Yes | Yes | NA
11 |  | Gym |  |  |  | Office-Open | 0.98 |  |  |  | Office-Open | C-Office-Enclosed | 1.11 | 8 | Yes | Yes | Private Office
12 |  | Pool |  |  |  | Restrooms | 0.98 |  |  |  | Restrooms | C-Office-Open | 0.98 | 4 | Yes | No | Open Office
|  | Mall Concourse |  |  |  | Sales Area | 1.68 |  |  |  | Sales Area | C-Restrooms | 0.98 | 8 | No | Yes | NA
|  | Parking Garage |  |  |  | Stairway | 0.69 |  |  |  | Stairway | C-Sales Area | 1.68 | 6 | Yes | No | Retail Sales Area
[6 empty] | Storage | 0.63 |  |  |  | Storage | C-Stairway | 0.69 | 10 | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
[6 empty] | Workshop | 1.59 |  |  |  | Workshop | C-Storage | 0.63 | 6 | No | Yes | NA
[5 empty] | x | Laboratory - Classroom | 1.4 |  | Automotive | Service/Repair | Automotive - Service/Repair | C-Workshop | 1.59 | 6 | Yes | No | NA
[5 empty] | x | Laboratory - Research | 1.4 |  | Bank/Office | Banking Activity Area | Bank/Office - Banking Activity Area | S-Automotive - Service/Repair | 0.67 | 4 | Yes | No | NA
[5 empty] | x | Lobby | 1.3 |  | Convention Center | Audience Seating | Convention Center - Audience Seating | S-Bank/Office - Banking Activity Area | 1.38 | 6 | Yes | No | NA
[5 empty] | x | Lobby - Hotel | 1.1 |  | Convention Center | Exhibit Space | Convention Center - Exhibit Space | S-Convention Center - Audience Seating | 0.82 | 4 | Yes | No | NA
[5 empty] | x | Lobby - Motion Picture Theater | 1.1 |  | Courthouse/Police Station/Penitentiary | Confinement Cells | Courthouse/Police Station/Penitentiary - Confinement Cells | S-Convention Center - Exhibit Space | 1.45 | 4 | Yes | No | NA
[5 empty] | x | Lobby - Performing Arts Theater | 3.3 |  | Courthouse/Police Station/Penitentiary | Courtroom | Courthouse/Police Station/Penitentiary - Courtroom | S-Courthouse/Police Station/Penitentiary - Confinement Cells | 1.1 | 6 | Yes | No | NA
[5 empty] | x | Locker Room | 0.6 |  | Courthouse/Police Station/Penitentiary | Judges' Chambers | Courthouse/Police Station/Penitentiary - Judges' Chambers | S-Courthouse/Police Station/Penitentiary - Courtroom | 1.72 | 6 | Yes | No | NA
[5 empty] | x | Lounge/Recreation | 1.2 |  | Courthouse/Police Station/Penitentiary | Penitentiary Audience Seating | Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating | S-Courthouse/Police Station/Penitentiary - Judges' Chambers | 1.17 | 8 | Yes | No | NA
[5 empty] | x | Lounge/Recreation - Hospital | 0.8 |  | Courthouse/Police Station/Penitentiary | Penitentiary Dining | Courthouse/Police Station/Penitentiary - Penitentiary Dining | S-Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating | 0.43 | 4 | Yes | No | NA
[5 empty] | x | Office-Enclosed | 1.1 |  | Courthouse/Police Station/Penitentiary | Pentitentiary Classroom | Courthouse/Police Station/Penitentiary - Pentitentiary Classroom | S-Courthouse/Police Station/Penitentiary - Penitentiary Dining | 1.07 | 6 | Yes | No | NA
[5 empty] | x | Office-Open | 1.1 |  | Dormitory | Living Quarters | Dormitory - Living Quarters | S-Courthouse/Police Station/Penitentiary - Pentitentiary Classroom | 1.34 | 4 | Yes | No | NA
[5 empty] | x | Restrooms | 0.9 |  | Fire Stations | Engine Room | Fire Stations - Engine Room | S-Dormitory - Living Quarters | 0.38 | 8 | Yes | No | NA
[5 empty] | x | Sales Area | 1.7 |  | Fire Stations | Sleeping Quarters | Fire Stations - Sleeping Quarters | S-Fire Stations - Engine Room | 0.56 | 4 | Yes | No | NA
[5 empty] | x | Stairway | 0.6 |  | Gymnasium/Fitness Center | Fitness Area | Gymnasium/Fitness Center - Fitness Area | S-Fire Stations - Sleeping Quarters | 0.25 | 6 | Yes | No | NA
[5 empty] | x | Storage | 0.8 |  | Gymnasium/Fitness Center | Fitness Center - Audience Seating | Gymnasium/Fitness Center - Fitness Center - Audience Seating | S-Gymnasium/Fitness Center - Fitness Area | 0.72 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
[5 empty] | x | Storage - Hospital | 0.9 |  | Gymnasium/Fitness Center | Gymnasium - Audience Seating | Gymnasium/Fitness Center - Gymnasium - Audience Seating | S-Gymnasium/Fitness Center - Gymnasium - Audience Seating | 0.43 | 6 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
[5 empty] | x | Storage - Museum | 0.8 |  | Gymnasium/Fitness Center | Playing Area | Gymnasium/Fitness Center - Playing Area | S-Gymnasium/Fitness Center - Playing Area | 1.2 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
[5 empty] | x | Workshop | 1.9 |  | Hospital | Corridor/Transition | Hospital - Corridor/Transition | S-Hospital - Corridor/Transition | 0.89 | 8' wide | No | No | NA
[9 empty] | Hospital | Emergency | Hospital - Emergency | S-Hospital - Emergency | 2.26 | 6 | Yes | No | NA
[9 empty] | Hospital | Exam/Treatment | Hospital - Exam/Treatment | S-Hospital - Exam/Treatment | 1.66 | 8 | Yes | No | NA
[9 empty] | Hospital | Laundry - Washing | Hospital - Laundry - Washing | S-Hospital - Laundry - Washing | 0.6 | 4 | Yes | No | NA
[9 empty] | Hospital | Lounge/Recreation | Hospital - Lounge/Recreation | S-Hospital - Lounge/Recreation | 1.07 | 6 | Yes | No | NA
[9 empty] | Hospital | Medical Supply | Hospital - Medical Supply | S-Hospital - Medical Supply | 1.27 | 6 | Yes | No | NA
[9 empty] | Hospital | Nursery | Hospital - Nursery | S-Hospital - Nursery | 0.88 | 6 | Yes | No | NA
[9 empty] | Hospital | Nurses' Station | Hospital - Nurses' Station | S-Hospital - Nurses' Station | 0.87 | 6 | Yes | No | NA
[9 empty] | Hospital | Operating Room | Hospital - Operating Room | S-Hospital - Operating Room | 1.89 | 6 | Yes | No | NA
[9 empty] | Hospital | Patient Room | Hospital - Patient Room | S-Hospital - Patient Room | 0.62 | 6 | Yes | No | NA
[9 empty] | Hospital | Pharmacy | Hospital - Pharmacy | S-Hospital - Pharmacy | 1.14 | 6 | Yes | No | NA
[9 empty] | Hospital | Physical Therapy | Hospital - Physical Therapy | S-Hospital - Physical Therapy | 0.91 | 6 | Yes | No | NA
[9 empty] | Hospital | Radiology/Imaging | Hospital - Radiology/Imaging | S-Hospital - Radiology/Imaging | 1.32 | 6 | Yes | No | NA
[9 empty] | Hospital | Recovery | Hospital - Recovery | S-Hospital - Recovery | 1.15 | 6 | Yes | No | NA
[9 empty] | Hospital | Storage | Hospital - Storage | S-Hotel/Motel - Highway Lodging Dining | 0.88 | 4 | Yes | No | NA
[9 empty] | Hotel/Motel | Highway Lodging Dining | Hotel/Motel - Highway Lodging Dining | S-Hotel/Motel - Highway Lodging Guest Room | 0.75 | 6 | Yes | No | NA
[9 empty] | Hotel/Motel | Highway Lodging Guest Room | Hotel/Motel - Highway Lodging Guest Room | S-Hotel/Motel - Hotel Dining | 0.82 | 4 | Yes | No | NA
[9 empty] | Hotel/Motel | Hotel Dining | Hotel/Motel - Hotel Dining | S-Hotel/Motel - Hotel Guest Rooms | 1.11 | 6 | Yes | No | NA
[9 empty] | Hotel/Motel | Hotel Guest Rooms | Hotel/Motel - Hotel Guest Rooms | S-Hotel/Motel - Hotel Lobby | 1.06 | 4 | No | No | NA
[9 empty] | Hotel/Motel | Hotel Lobby | Hotel/Motel - Hotel Lobby | S-Library - Card File & Cataloging | 0.72 | 4 | Yes | No | NA | 1. Lights in corridors, electrical/mechanical rooms, public lobbies, restrooms, stairways, and storage rooms
[9 empty] | Library | Card File & Cataloging | Library - Card File & Cataloging | S-Library - Reading Area | 0.93 | 4 | Yes | No | NA | 2. Spaces with only one luminaire with rated input power less than 100 W.
[9 empty] | Library | Reading Area | Library - Reading Area | S-Library - Stacks | 1.71 | 4 | Yes | No | NA | 3. Spaces types with lighting power allowance of less than 0.6 W/sq.ft (see Table 9.6.1).
[9 empty] | Library | Stacks | Library - Stacks | S-Manufacturing - Corridor/Transition | 0.41 | 8' wide | No | No | NA
[9 empty] | Manufacturing | Corridor/Transition | Manufacturing - Corridor/Transition | S-Manufacturing - Detailed Manufacturing | 1.29 | 4 | Yes | No | NA
[9 empty] | Manufacturing | Detailed Manufacturing | Manufacturing - Detailed Manufacturing | S-Manufacturing - Equipment Room | 0.95 | 6 | Yes | No | NA
[9 empty] | Manufacturing | Equipment Room | Manufacturing - Equipment Room | S-Manufacturing - Extra High Bay (≥ 50') | 1.05 | 4 | Yes | No | NA
[9 empty] | Manufacturing | Extra High Bay (≥ 50') | Manufacturing - Extra High Bay (≥ 50') | S-Manufacturing - High Bay (≥ 25' & < 50') | 1.23 | 4 | Yes | No | NA
[9 empty] | Manufacturing | High Bay (≥ 25' & < 50') | Manufacturing - High Bay (≥ 25' & < 50') | S-Manufacturing - Low Bay (< 25') | 1.19 | 4 | Yes | No | NA
[9 empty] | Manufacturing | Low Bay (< 25') | Manufacturing - Low Bay (< 25') | S-Museum - General Exhibition | 1.05 | 6 | Yes | No | NA
[9 empty] | Museum | General Exhibition | Museum - General Exhibition | S-Museum - Restoration | 1.02 | 6 | Yes | No | NA
[9 empty] | Museum | Restoration | Museum - Restoration | S-Parking Garage - Garage Area | 0.19 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
[9 empty] | Museum | Storage | Museum - Storage | S-Post Office - Sorting Area | 0.94 | 4 | Yes | No | NA
[9 empty] | Parking Garage | Garage Area | Parking Garage - Garage Area | S-Religious Buildings - Audience Seating | 1.53 | 4 | Yes | No | NA
[9 empty] | Post Office | Sorting Area | Post Office - Sorting Area | S-Religious Buildings - Fellowship Hall | 0.64 | 4 | Yes | No | NA
[9 empty] | Religious Buildings | Audience Seating | Religious Buildings - Audience Seating | S-Religious Buildings - Worship Pulpit, Choir | 1.53 | 4 | Yes | No | NA
[9 empty] | Religious Buildings | Fellowship Hall | Religious Buildings - Fellowship Hall | S-Retail - Dressing/Fitting Room | 0.87 | 8 | Yes | Yes | NA
[9 empty] | Religious Buildings | Worship Pulpit, Choir | Religious Buildings - Worship Pulpit, Choir | S-Retail - Mall Concourse | 1.1 | 4 | No | No | NA
[9 empty] | Retail | Dressing/Fitting Room | Retail - Dressing/Fitting Room | S-Retail - Sales Area | 1.68 | 6 | Yes | No | Retail Sales Area
[9 empty] | Retail | Mall Concourse | Retail - Mall Concourse | S-Sports Arena - Audience Seating | 0.43 | 4 | Yes | No | NA
[9 empty] | Retail | Sales Area | Retail - Sales Area | S-Sports Arena - Court Sports Area - Class 1 | 3.01 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Audience Seating | Sports Arena - Audience Seating | S-Sports Arena - Court Sports Area - Class 2 | 1.92 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Court Sports Area - Class 1 | Sports Arena - Court Sports Area - Class 1 | S-Sports Arena - Court Sports Area - Class 3 | 1.2 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Court Sports Area - Class 2 | Sports Arena - Court Sports Area - Class 2 | S-Sports Arena - Court Sports Area - Class 4 | 0.72 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Court Sports Area - Class 3 | Sports Arena - Court Sports Area - Class 3 | S-Sports Arena - Ring Sports Area | 2.68 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Court Sports Area - Class 4 | Sports Arena - Court Sports Area - Class 4 | S-Transportation - Air/Train/Bus Baggage Area | 0.76 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Ring Sports Area | Sports Arena - Ring Sports Area | S-Transportation - Airport Concourse | 0.36 | 4 | No | No | NA
[9 empty] | Transportation | Air/Train/Bus Baggage Area | Transportation - Air/Train/Bus Baggage Area | S-Transportation - Audience Seating | 0.54 | 4 | Yes | No | NA
[9 empty] | Transportation | Airport Concourse | Transportation - Airport Concourse | S-Transportation - Terminal - Ticket Counter | 1.08 | 4 | Yes | No | NA
[9 empty] | Transportation | Audience Seating | Transportation - Audience Seating | S-Warehouse - Fine Material Storage | 0.95 | 6 | Yes | No | NA
[9 empty] | Transportation | Terminal - Ticket Counter | Transportation - Terminal - Ticket Counter | S-Warehouse - Medium/Bulky Material Storage | 0.58 | 4 | Yes | No | NA
[9 empty] | Warehouse | Fine Material Storage | Warehouse - Fine Material Storage
[9 empty] | Warehouse | Medium/Bulky Material Storage | Warehouse - Medium/Bulky Material Storage