Request for Official Interpretation

Note: An “official” interpretation is defined as a written explanation of the meaning of a specific provision of a standard or guideline, as determined by an existing cognizant Project Committee or an Interpretation Committee (IC), in response to a written request.  See StdC Reference Manual 10.2 for requests not covered. No provision is included for responding to requests for interpretation of superseded standards or guidelines. See StdC Reference Manual 10.3.2 for a request for “unofficial” interpretation.

Please tab through and provide the following information:

| Request from: |  | Name: |  | Randi Paananen, PE |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Affiliation: |  | Integrated Design Solutions |  |  |  |  |  |  |
|  |  | Address: |  | 1441 W Long Lake Rd, Suite 200 |  |  |  |  |  |  |
|  |  | City: | Troy |  |  | State: | MI |  | Zip: | 48098 |
|  |  | Telephone: |  | (248) 823-2186 |  |  |  |  |  |  |
|  |  | E-mail: |  | rpaananen@ids-michigan.com |  |  |  |  |  |  |
| Reference: |  | This request for interpretation refers to the requirements presented in: |  |  |  |  |  |  |  |  |
|  |  | ASHRAE Standard |  |  | Number and Year: |  |  | 90.1-2019 |  |  |
|  |  | Page Number(s): |  |  | 158 |  |  |  |  |  |
|  |  | Section(s): |  |  | 8.4.2 Automatic Receptacle Control |  |  |  |  |  |
|  |  | Table(s): |  |  |  |  |  |  |  |  |
|  |  | Relating to: |  |  | Automatic receptacle control “Individual Workstation” definition |  |  |  |  |  |
| Background: |  | Section 8.4.2 [a] requires automatic receptacle control in all private offices, individual workstations, and other room types. No definition is provided for the term “individual workstation”. |  |  |  |  |  |  |  |  |
|  |  | Note: Please provide background and supporting information here. State exactly what the requirements are and any conflicting information. |  |  |  |  |  |  |  |  |
| Interpretation: |  | The term “individual workstation” is intended to refer to a workstation that is analogous to a private office, such as a desk or cubicle within an open office. The term is not intended to refer to the planned desk location within a private office. |  |  |  |  |  |  |  |  |
| Question: | Is this Interpretation correct? |  |  |  |  |  |  |  |  |  |
| Answer: |  | YES |  |  |  |  |  |  |  |  |
| Comments: |  | “Individual workstation” is intended to refer to furniture containing receptacle outlets only in an open office setting. |  |  |  |  |  |  |  |  |

Submit this form by e-mail, fax or mail to: Manager of Standards, ASHRAE, 180 Technology Parkway NW, Peachtree Corners, Georgia 30092, mailto:standards.section@ashrae.org, Fax: 404-321-5478.