| ### ASHRAE Technical FAQ |  |
| --- | --- |
| ID; 2. Question; What is ASHRAE's recommendation for residential filtration?. Answer; ASHRAE Standard 62.2-2022, "Ventilation and Acceptable Indoor Air Quality (covers other residential type buildings including high-rise) notes that filters designated with a minimum efficiency of MERV 6, or better, when testing in accordance with ASHRAE Standard 52.2-2017, shall be provided . Most residential systems are shipped from the manufacturer with a filter that has a MERV ranging from 1 and 4. This lower level of filter efficiency is selected to protect the heat exchanger and/or cooling coil from fouling debris with minimal initial expense. Higher levels of MERVs are possible. When upgrading the filter MERV a higher restriction to airflow must be considered. Most modern systems can accommodate this higher resistance, but you should consult with your HVAC equipment manufacturer for recommendations on the highest recommended level of initial filter resistance for your HVAC equipment. Selection procedures based on user requirements such as degree and type of air cleanliness required, space available for filtration equipment, cost (initial and maintenance), amount and type of dust in the air to be filtered, etc. are covered in Chapter S29 of the 2020 ASHRAE Handbook - HVAC Systems and Equipment. It is also noted in this chapter that the Air-conditioning, Heating, and Refrigeration Institute (AHRI) has two standards - 680 and 850 - for air filtration equipment. The Minimum Efficiency Reporting Value (MERV) test procedure for air filters is defined in ASHRAE Standard 52.2-2017. The handbook and the other publications may be purchased and/or individual chapters of the handbook may be purchased and downloaded on-line at our website, www.ashrae.org or by calling 1-800-527-4723 in the USA and Canada or 1-404-636-8400 worldwide. AHRI – Air-conditioning, Heating, and Refrigeration Institute NAFA - National Air Filtration Association ACGIH - American Conference of Governmental Industrial Hygienists AIHA - American Industrial Hygiene Association, U.S. EPA - United States Environmental Protection Agency. ASHRAE Pubs; ASHRAE Standard 62.2-2022, plus ASHRAE BOD approved addenda. ASHRAE Standard 52.1-1992, plus ASHRAE BOD approved addenda. ASHRAE Standard 52.2-2017, plus ASHRAE BOD approved addenda. 2023 ASHRAE Handbook – HVAC Applications, Chapter A01 2021 ASHRAE Handbook - Fundamentals, Chapter F11 2020 ASHRAE Handbook - HVAC Systems and Equipment, Chapter S29 ASHRAE Position Document on Filtration and Air Cleaning. Topic References; filtration, filter, contaminants, residential filter, allergy, asthma, respiratory. Cognizant ASHRAE Committees; Refer to Organization. 1; TC 2.4; NAFA. 2; SSPC 62.2; ACGIH. 3; SSPC 52.2; AIHA. 4; U.S. EPA. 5; AHRI.. |  |