## DISCLAIMER
#VALUE!
© ASHRAE. Per international copyright law, additional reproduction, distribution, or transmission in either print or digital form is not permitted without ASHRAE's prior written permission.
Standard 62.1-2022 62.1 Appendix B Separation Distance Calculator
Last Updated: September 30, 2024
Disclaimer of Warranties ASHRAE and the distributors of this information do not warrant that the information is free of errors. This spreadsheet is provided “as is” without warranty of any kind, either expressed or implied. The entire risk as to the quality and performance of the file and information is with you. In no event will ASHRAE be liable to you for any damages, including without limitation any lost profits, lost savings or other incidental or consequential damages arising out of the use or inability to use this program or data. ASHRAE reserves the right to discontinue support for this product at any time in the future, including without limitation discontinuing support of servers facilitating access to this product. This product is for personal use only. It is not licensed for networks.

## Description
BACKGROUND
ANSI/ASHRAE Addendum ag to Standard 62.1-2022 replaces the calculation method in Normative Appendix B, “Separation of Exhaust Outlets and Outdoor Air Intakes,” with a new method based on ASHRAE Research Project (RP) 1635. RP-1635 provides a simple yet accurate procedure for calculating the minimum distance required between the outlet of an exhaust system and the outdoor air intake to a ventilation system to avoid re-entrainment of exhaust gases. The new procedure addresses the technical deficiencies in the simplified equations and tables that are in Standard 62.1 (as of the 2022 edition) and in model building codes. The study demonstrated that the new method is more accurate than the existing Standard 62.1 equation, which underpredicts and overpredicts observed dilution more frequently than the new method. In addition, the new method accounts for the following additional important variables: stack height, wind speed, and hidden versus visible intakes. The new method also has theoretically justified procedures for addressing heated exhaust, louvered exhaust, capped heated exhaust, and horizontal exhaust that is pointed away from the intake. The equation for determining heated exhaust is derived from the EPA’s User’s Guide for the Industrial Source Complex (ISC3) Dispersion Models (1995), Equation 1-10.
REFERENCES
EPA. 1995. User’s Guide for the Industrial Source Complex (ISC3) Dispersion Models, Vol. 2: Description of Model Algorithms. Research Triangle Park, NC: U.S. Environmental Protection Agency. EPA-454/B-95-003B.
ASHRAE. 2016. Simplified Procedure for Calculating Exhaust Intake Separation Distances. RP-1635 Final Report. Peachtree Corners, GA: ASHRAE.

## I-P
|  |  | Yes | Round | 0
Exhaust Configuration |  |  | No | Rectangular
Capped or Horizontal or Downblast (Yes/No) | Yes
Horizontal and Pointed Away from Intake (Yes/No) | Yes | Blank unless exhaust is horizontal ("Yes" in Row 4)
Hidden Intake (Yes/No) | No
Exhaust Outlet Shape | Round
Louvered (Yes/No) | No
Parameters
Dilution Factor (D) = | 300 | Input dilution factor from Table 5-8
Stack Height (hs) (ft) = | 10 | Stack height above the top of intake
Exhaust Outlet Diameter (de) (in) = | 24 | Blank if exhaust outlet shape is "Rectangular" (Row 8)
Exhaust Outlet Width (in) = |  | Blank if exhaust outlet shape is "Round" (Row 8)
Exhaust Outlet Height (in) = | 12 | Blank if exhaust outlet shape is "Round" (Row 8)
Louver Free Area (%) = | 90% | Blank unless exhaust outlet is louvered ("Yes" in Row 9)
Exhaust Air Volume Flowrate (Qe) (cfm) = | 1000
Exhaust Temperature (F) | 70 | Default is set to ambient
Ambient Temperature (F) | 70
Maximum Wind Speed (mph) | 23 | Default is 23 mph
Calculated Values
Critical Temperature Differential for Fb<55 (F) | 57.6825 | Eqtn 1-10 in EPA, 1995
Heated (Yes/No) | No | Exhaust is "heated" if the difference between the exhaust and ambient temperatures exceeds the critical temperature differentials
Capping Factor (β) = | 0
Final Dilution Factor | 176.4706
Exhaust Diameter (de) (ft) = | 2
Effective Exhaust Diameter (de) (ft) = | 2
Ve (fpm) = | 318.3099
Effective Ve (fpm) = | 318.3099
L (ft) | 64.8292
LFinal (ft) | 61.3292
Note on B5: Elizabeth Balke: Horizontal "pointed away" includes cases where the direction of the exhaust is oriented 180 degrees away from the intake +/- 45 degrees
Note on B6: Elizabeth Balke: must be 1) off the same roof as the exhaust and on a building sidewall or 2) on the same roof as the exhaust but on the other side of a significant obstruction. A significant obstacle is defined as follows: • is located no farther than 10 m (33 ft) from the stack, and • has a vertical plane square footage of at least 46.5 m2 (500 ft2), and • a height that is greater than 1.6 m (5.2 ft), and • a width that is greater than 4.8 m (16 ft).
Note on B14: Elizabeth Balke: For upblast, use the outer diameter
Note on B18: Elizabeth Balke: For variable flow, use the minimum airflow rate. For gravity vents, such as plumbing vents, use an exhaust rate of 150 cfm (75 L/s); for flue vents from fuel-burning appliances, assume a value of 250 cfm per million Btu/h (0.43 L/s per kW) of combustion input (or obtain actual rates from the combustion appliance manufacturer.
Note on D24: Elizabeth Balke: Applies to unstable or neutral atmosphere. According to the Pasquill stability classes, all daytime atmosphere is unstable or neutral and nighttime atmosphere depends on the windspeed and cloud cover.
Note on B34: Elizabeth Balke: Minimum separation, stretched string distance.

## Sheet1
Windspeed (U_H) (m/s) | Windspeed (U_H) (ft/min) | Windspeed (U_H) (mph) | Heated Exhaust Factor, Bfac | F1 | F2 | F1-F2
1.5 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
1.6 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
1.7 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
1.8 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
1.9 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
2 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
2.1 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
2.2 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
2.3 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
2.4 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
2.5 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
2.6 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
2.7 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
2.8 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
2.9 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
3 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
3.1 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
3.2 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
3.3 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
3.4 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
3.5 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
| 704 | 8 | 1 | 3409.0909 | 3337 | 72.0909
3.6 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
3.7 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
3.8 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
3.9 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
4 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
4.1 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
4.2 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
4.3 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
4.4 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
4.5 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
4.6 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
4.7 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
4.8 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
4.9 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
5 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
5.1 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
5.2 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
5.3 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
5.4 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
5.5 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
5.6 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
5.7 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
5.8 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
| 1144 | 13 | 1 | 2097.9021 | 3337 | -1239.0979
5.9 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
6 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
6.1 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
6.2 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
6.3 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
6.4 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
6.5 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
6.6 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
6.7 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
6.8 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
6.9 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
7 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
7.1 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
7.2 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
7.3 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
7.4 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
7.5 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
7.6 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
7.7 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
7.8 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
7.9 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
8 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
8.1 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
8.2 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
8.3 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
8.4 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
8.5 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
8.6 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
8.7 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
8.8 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
8.9 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
9 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
9.1 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
9.2 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
9.3 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
9.4 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
9.5 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
9.6 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
9.7 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
9.8 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
9.9 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
10 | 318.3099 | 3.6172 | 1 | 7539.8224 | 3337 | 4202.8224
Note on B2: Elizabeth Balke: Maximize F1-F2 by changing UH between 300 and 2000 fpm