ASHRAE Standard 62.1-2022 
Indoor Air Quality Procedure (IAQP) Calculator

Last Revised: March 27, 2024

Contents

Tool Organization and Input Data	2

Introduction Sheet	3

Project Data	3

Outside Air (OA) Concentration Data	4

Generation Rates	5

Input	5

Compliance	5

Tool Output	5

Use, Limitations, and Uncertainties	5

References	6

Background	6

Single-Zone Systems	7

Filter Location A1	7

Filter Location A2	9

Filter Location B	11

Multiple-Zone Systems	13

Filter Location A1	13

Filter Location A2	17

Filter Location B	22

# Tool Organization and Input Data

The calculator is a Microsoft Excel-based tool organized into the following sheets/groups:

- Introduction

This sheet contains general information, instructions for correctly setting up Excel to use the tool, and version information.

- Project Data

This sheet contains data inputs for tested air cleaning efficiency and outdoor contaminant concentrations. Optionally, there are data inputs for project-specific design compounds.

- Outside Air Concentration Data

This sheet contains instructions and hyperlinks to help users find outdoor air concentration data from the US EPA.

- Generation Rates

This sheet contains data inputs for emission rates per occupancy category.

- Input

This is the main worksheet the user will work on to input system-level data and zone-level data in order to obtain ventilation rates.

- Compliance

This sheet details the calculation results and provides tables to document the requirements for completing the IAQP.

- Calculation Worksheets (single-zone and multiple-zone)

This group of sheets run the ventilation calculations for different scenarios. The user should not edit any data in these worksheets.

- Reference

Reference tables, do not edit.

- ASHRAE Ref Tables

Reference tables, do not edit.

You can easily navigate between tabs using the navigation pane: click on the text boxes to jump to the respective tab (Figure 1). Cells containing data entry and data outputs have been color coded (Figure 2).

Figure 1. Navigation pane

Figure 2. Data input legend

## Introduction Sheet

In order to perform multizone calculations, you will need to enable iterative calculations in Excel. Use the instructions at the top of the sheet below attempting to use the tool:

- Click the File tab, click Options, and then click the Formulas category.

- Under the Calculation options heading, click the checkbox next to Enable iterative calculation. Set the maximum iterations value to 30 and the maximum change to 0.001.

- Click OK to accept the changes.

## Project Data

This worksheet contains data inputs for project-level inputs, including data for air-cleaning efficiency and outdoor air quality. Inputs are required for all design compounds in Table 1. If the project has additional contaminants within the design, information on up to five compounds can be added in Table 2.

Per ASHRAE Standard 62.1-2022 Addendum n, particulate filters must use an efficiency reporting value (MERV) in accordance with ASHRAE Standard 52.2 or reporting in accordance with ISO 16890. Gas-phase air cleaners must use efficiencies reported for all compounds included in the design with any of the following:

- ASHRAE Standard 145.2

- ISO 10121-2

- Testing by methods in Section 6.1.2,10.4, and 10.5 and reported as required in ASHRAE Standard 145.2, Section 11

- Testing to a national consensus standard approved by the authority having jurisdiction

- For technologies not covered by any of the above, please see Addendum n for information regarding custom tests.

Note that there are options to enter a PM2.5 filtration efficiency on the outdoor air intake, as well as the recirculation air. The MERV rating selections listed in the dropdown correspond to the minimum end of the efficiency range (e.g., MERV 11 selects an efficiency of 65%).

All entries for efficiencies must be a number from 0 to 1.

Outdoor air concentrations for design compounds can be obtained via the US EPA through the AirData Air Quality Monitors application:

- Click the Select Layer menu option and select a layer to view (generally, selecting Ozone - Active is a good place to start).

- Click a map marker near the project location.

- Click the link under Annual Data Download (links) for the most recent full calendar year (usually the second-to-last option).

- Open the downloaded Excel spreadsheet; record the arithmetic mean value for each contaminant as the outdoor concentration.

- Note: Most of the concentration data will need to be converted to the correct units for use in the calculator. Conversion factors have been provided in the OA Concentration Data worksheet. For example, EPA reported values for acetaldehyde are provided in units of [parts per billion]. To convert, multiply the value by the conversion factor given (1.805) to obtain the correct value in units [μg/m3].

## Outdoor Air (OA) Concentration Data

If site-specific outdoor air quality data are not available, the OA Concentration Data tab provides instructions to pull data from U.S. EPA air quality monitoring sites. Using the AirData Air Quality Monitors website application, you can select a station near the project site and download the previous year’s data logs. Note the information collected varies between AQS sites: some collect only NAAQS contaminant data, while others collect a more comprehensive set. You may need to reference multiple AQS sites to collect enough concentration data.

## Generation Rates

You will need to enter emission rate data for all of the design compounds listed in Table 3 of the GENERATION RATES tab, for each of the occupancy categories encompassed within the project site. Emission rates are calculated on an area basis and must be input in units of μg/m2/h. The corresponding citation for each cell entry needs to be added in Table 4.

## Input

This worksheet is the main data-entry section. You will need to appropriately select the ventilation system type (single-zone or multiple-zone), filter location, and system efficiency calculation method. The worksheet will then show specific instructions based on your selections. Minimally, you will need to input data for each ventilation zone. The final outdoor air calculation is iterative; you will need to increase or decrease the outdoor air value in order to ensure that all relevant mixtures are below 1 (see comprehensive instructions on the worksheet for specific cell references).

## Compliance

This worksheet provides a template for full documentation of the IAQP design. Double check that the outdoor air intake satisfies the compound mixtures check.

# Tool Output

The COMPLIANCE worksheet documents the IAQP calculation requirements, including:

- Design approach (steady-state mass-balance analysis)

- List of design compounds and PM2.5 (DC and PM2.5)

- Design limits with cognizant authority references

- List of mixtures of compounds

- DC and PM2.5 outdoor sources/concentrations

- DC and PM2.5 indoor sources

- DC and PM2.5 indoor emission rates, including citations

- DC and PM2.5 indoor calculated concentration

- Calculated mixed exposure sum(s)

- Mass-balance calculations for each zone

- Zone minimum outdoor airflow rates

- System minimum outdoor airflow rate

# Use, Limitations, and Uncertainties

The IAQP calculator was developed to model contaminant concentrations using time-independent (steady-state) analysis; this assumes the constancy of all variables, including airflows, outdoor pollutant loads, and indoor emissions. In reality, many recirculating systems have variable-airflow volumes, both for zone supply airflow and system outdoor airflow (i.e., economization). This is mitigated some by virtue of calculating minimum ventilation rates, assuming that the increase of outdoor air and commensurate decrease in recirculated air will only improve indoor air quality conditions. To help ensure that year-round ventilation rates are adequate, the user can run the IAQP ventilation calculation for both heating and cooling design conditions and use the smaller outdoor air value of the two.

To facilitate ease-of-use and availability to users, the tool is MS Excel based. It is easier to use than alternative contaminant modeling tools, but its flexibility limits the complexity of simulations that can be run. The tool is currently limited to the three air-cleaning configurations shown in the Background section (see below) for single-zone and multiple-zone systems. The modeling of contaminant transport in multiple-zone systems is limited to the ductwork distribution; contaminant flows between zones via openings (e.g., doors, corridors, adjoining spaces not separated by walls) and through the building envelope via infiltration/exfiltration air is not considered. The tool has undergone side-by-side testing by modeling identical systems in CONTAM; the Excel calculator results show good agreement with the CONTAM-modeled contaminant concentrations, assuming steady-state conditions.

# References

ANSI/ASHRAE Standard 52.2-2017, Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size

ANSI/ASHRAE Standard 62.1-2022, Ventilation and Acceptable Indoor Air Quality

ANSI/ASHRAE Standard 145.2-2016, Laboratory Test Method for Assessing the Performance Of Gas-Phase Air-Cleaning Systems: Air-Cleaning Devices

# Background

ASHRAE Standard 62.1-2022 Informative Appendix F, Table F-1 presents mass-balance equations that are appropriate for analyzing single-zone ventilation systems but does not provide a method that accounts for multiple-zone systems. This tool has been developed to model the distribution of contaminants throughout a mixed-air ventilation system; this accounts for the transport of contaminants from one space to another via recirculated air. The following sections demonstrate the calculation procedure for each scenario modeled within the tool.

## Single-Zone Systems

### Filter Location A1

The zone outdoor air ventilation rate for each design compound (DC) is calculated:

|  | Voz=N-EzVcEfCbzEzCbz-Co | (1) |
| --- | --- | --- |

where

Voz	is the estimated zone outdoor airflow [m3/h]

N	is the compound emission rate in the zone [μg/h]

Ez	is the ventilation effectiveness

Vc	is the discrete airflow through the air cleaning device [m3/h]

Ef	is the filter efficiency

Cbz	is the design limit for the DC [μg/m3]

Co	is the outdoor air concentration of the DC [μg/m3]

After the zone outdoor airflow rates for each design compound have been calculated and the highest estimated outdoor airflow is selected, the concentration of each DC in the zone must be calculated to ensure that the DL is met:

|  | Cbz=N+EzVozCoEzVoz+VcEf | (2) |
| --- | --- | --- |

The compounds for each mixture must now be checked. For each mixture, the mixed exposure sum (Em) must be calculated to be less than 1.0:

|  | Em=Cbz,1DL1+Cbz,2DL2+Cbz,jDLj | (3) |
| --- | --- | --- |

where

Em	is the mixed exposure sum

Cbz ,j	is the final calculated concentration for the jth DC

DLj	is the design limit for the jth DC

If the mixed exposure sum is less than unity for all relevant mixtures, the zone outdoor airflow is acceptable. If the zone fails the mixture check, the user will need to enter a value for the zone outdoor air that is higher than the current set value. The process is repeated from Step 2, substituting the user input value for Voz.

Once the mixtures check is satisfied, the system outdoor air intake (Vot) is then calculated:

|  | Vot=Voz | (4) |
| --- | --- | --- |

where

Vot	is the outdoor air intake [m3/h]

### Filter Location A2

The zone outdoor air ventilation rate for each design compound (DC) is estimated based on the size of the system:

|  | Voz=N-EzVpsEfCbzEzCbz1-Ef-Co | (1) |
| --- | --- | --- |

where

Voz	is the estimated zone outdoor airflow [m3/h]

N	is the compound emission rate in the zone [μg/h]

Ez	is the ventilation effectiveness

Vps	is the system primary airflow [m3/h]

Ef	is the filter efficiency

Cbz	is the design limit for the DC [μg/m3]

Co	is the outdoor air concentration of the DC [μg/m3]

Then use the estimated outdoor air rate to make a first-order estimate of the recirculated air volume that will pass through the filter:

|  | RVr=Vps-Voz | (2) |
| --- | --- | --- |

where

R	is the recirculation flow factor

Vr	is the return airflow [m3/h]

After the estimated airflow rates for each design compound have been calculated, the highest estimated outdoor airflow is selected, along with the corresponding recirculation airflow rate, and is applied to each design compound to calculate the zone outdoor airflow (separately for each design compound) as follows:

|  | Voz=N-EzRVrEfCbzEzCbz-Co | (3) |
| --- | --- | --- |

The concentration of each DC in the zone must now be calculated to ensure that the DL is met:

|  | Cbz=N+EzVozCoEzVoz+RVrEf | (4) |
| --- | --- | --- |

The compounds for each mixture must now be checked. For each mixture, the mixed exposure sum (Em) must be calculated to be less than 1.0:

|  | Em=Cbz,1DL1+Cbz,2DL2+Cbz,jDLj | (5) |
| --- | --- | --- |

where

Em	is the mixed exposure sum

Cbz ,j	is the final calculated concentration for the jth DC

DLj	is the design limit for the jth DC

If the mixed exposure sum is less than unity for all relevant mixtures, the zone outdoor airflow is acceptable. If the zone fails the mixture check, the user will need to enter a value for the zone outdoor air that is higher than the current set value. The process is repeated from Step 3, substituting the user input value for Voz.

Once the mixtures check is satisfied, the system outdoor air intake (Vot) is then calculated:

|  | Vot=Voz | (6) |
| --- | --- | --- |

where

Vot	is the outdoor air intake [m3/h]

### Filter Location B

The zone outdoor air ventilation rate for each design compound (DC) is estimated based on the size of the system:

|  | Voz=N-EzVpsEfCbzEzCbz-Co1-Ef | (1) |
| --- | --- | --- |

where

Voz	is the estimated zone outdoor airflow [m3/h]

N	is the compound emission rate in the zone [μg/h]

Ez	is the ventilation effectiveness

Vps	is the system primary airflow [m3/h]

Ef	is the filter efficiency

Cbz	is the design limit for the DC [μg/m3]

Co	is the outdoor air concentration of the DC [μg/m3]

Then use the estimated outdoor airflow rate to make a first-order estimate of the recirculated air volume that will pass through the filter:

|  | RVr=Vps-Voz | (2) |
| --- | --- | --- |

where

R	is the recirculation flow factor

Vr	is the return airflow [m3/h]

After the estimated airflow rates for each design compound have been calculated, the highest estimated outdoor airflow is selected, along with the corresponding recirculation airflow rate, and is applied to each design compound to calculate the zone outdoor airflow (separately for each design compound) as follows:

|  | Voz=N-EzRVrEfCbzEzCbz-1-EfCo | (3) |
| --- | --- | --- |

The concentration of each DC in the zone must now be calculated to ensure that the DL is met:

|  | Cbz=N+EzVoz1-EfCoEzVoz+RVrEf | (4) |
| --- | --- | --- |

The compounds for each mixture must now be checked. For each mixture, the mixed exposure sum (Em) must be calculated to be less than 1.0:

|  | Em=Cbz,1DL1+Cbz,2DL2+Cbz,jDLj | (5) |
| --- | --- | --- |

where

Em	is the mixed exposure sum

Cbz ,j	is the final calculated concentration for the jth DC

DLj	is the design limit for the jth DC

If the mixed exposure sum is less than unity for all relevant mixtures, the zone outdoor airflow is acceptable. If the zone fails the mixture check, the user will need to enter a value for the zone outdoor air that is higher than the current set value. The process is repeated from Step 3, substituting the user input value for Voz.

Once the mixtures check is satisfied, the system outdoor air intake (Vot) is then calculated:

|  | Vot=Voz | (6) |
| --- | --- | --- |

where

Vot	is the outdoor air intake [m3/h]

## Multiple-Zone Systems

### Filter Location A1

In order to calculate outdoor air rates for individual zones in a multizone system, this model iterates through a system-level estimate below breaking down to the zone level. First, estimate the uncorrected outdoor air ventilation rate for each design compound (DC) based on the size of the system:

|  | Vou,s=i=1nNi-VcEfCbzCbz-Co | (1) |
| --- | --- | --- |

where

Vou,s	is the estimated system uncorrected outdoor airflow [m3/h]

Ni	is the compound emission rate in zone i [μg/h]

Vc	is the discrete airflow through the air cleaning device [m3/h]

Ef	is the filter efficiency

Cbz	is the design limit for the DC [μg/m3]

Co	is the outdoor air concentration of the DC [μg/m3]

After the estimated airflow rates for each design compound have been calculated, the highest uncorrected outdoor airflow is selected and applied to each design compound to conduct preliminary calculations for each zone. The estimated cleaned airflow delivered to the breathing zone is then calculated for each zone (separately for each design compound) as follows:

|  | Vcz,i=NiEfCbz-Xo(Co-Cbz) | (2) |
| --- | --- | --- |

where

Vcz,i	is the breathing zone cleaned airflow in zone i [m3/h]

Xo	is the ratio of outdoor airflow to cleaned airflow

assuming

|  | Xo=Vou,sVc | (3) |
| --- | --- | --- |

Which is then used to estimate the volume of outdoor air that needs to be delivered to each zone:

|  | Vbz,i=Ni-Vcz,iEfCbzCbz-Co | (4) |
| --- | --- | --- |

where

Vbz,i	is the breathing zone outdoor airflow in zone i [m3/h]

The maximum breathing zone cleaned airflow (Vcz,i) for each zone across all design compounds is selected as the preliminary uncorrected cleaned airflow for the zone. A first-order correction is applied to the sum of cleaned airflows proportionally:

|  | Xc=i=1n{max⁡(Vcz,i)}Vc | (5) |
| --- | --- | --- |

where

Xc	is the ratio of summed cleaned airflow to the device cleaned airflow

The factor Xc is then applied to the cleaned airflow for each zone:

|  | Vcz,i,a=Vcz,iXc | (6) |
| --- | --- | --- |

where

Vcz,i,a	is the adjusted cleaned airflow in zone i [m3/h]

The recalculated cleaned airflow is then used to recalculate the estimated outdoor airflow as in Step 4:

|  | Vbz,i,a=Ni-Vcz,i,aEfCbzCbz-Co | (7) |
| --- | --- | --- |

where

Vbz,i,a	is the adjusted outdoor airflow in zone i [m3/h]

The final values for outdoor airflow and cleaned air in each zone are calculated:

|  | Vbz,i,f=Vpz,ii=1n{max⁡(Vbz,i,a)}Vps | (8) |
| --- | --- | --- |
|  | Vcz,i,f=Vpz,iVcVps | (9) |

where

Vbz,i,f	is the final adjusted outdoor airflow in zone i [m3/h]

Vcz,i,f	is the final adjusted cleaned airflow in zone i [m3/h]

The concentration of each DC in each zone must now be calculated to ensure that the DL in each zone is met. To do so, the model runs an iterative loop several times to model the migration of contaminants between zones via recirculated air. The loop is run enough times to reach convergence in each zone, for each DC:

|  | Cs,i=Vbz,i,fCo+Vcz,i,fCbz,o1-Ef+Vpz,i-Vbz,i,f-Vcz,i,fCbz,oVs | (10) |
| --- | --- | --- |

where

Cs,i	is the contaminant concentration in the system primary air in zone i [μg/m3]

Cbz,o	is the initial contaminant concentration, set as the ambient concentration [μg/m3]

|  | Cbz,i=Vpz,iCs+NVpz,i | (11) |
| --- | --- | --- |

where

Cbz,i	is the contaminant concentration for each sequent iteration for zone i [μg/m3]

This eventually converges on the final concentration in each zone, Cbz,f. The compounds for each mixture must now be checked. For each mixture, in each separate zone, the mixed exposure sum (Em) must be calculated to be less than 1.0:

|  | Em=Cbz,f,1DL1+Cbz,f,2DL2+Cbz,f,jDLj | (12) |
| --- | --- | --- |

where

Em	is the mixed exposure sum

Cbz,f,j	is the final calculated concentration for the jth DC

DLj	is the design limit for the jth DC

If the mixed exposure sum is less than unity for all relevant mixtures, the uncorrected outdoor airflow for the zone (Vbz,f) is acceptable. All zones must pass the mixtures check individually.

If there are any zones that fail the mixture check, the user will need to enter a value for the uncorrected outdoor air intake that is higher than the current set value. The process is repeated from Step 8, substituting the user input value for the summed outdoor airflow correction (Vbz,i,f).

The system ventilation efficiency is then calculated, equal to the lowest calculated zone ventilation efficiency.

For each contaminant, the zone outdoor airflow is calculated as follows:

|  | Voz,i=N-Ez,iVcz,i,fEfCbzEz,iCbz-Co | (13) |
| --- | --- | --- |

where

Voz,i	is the zone outdoor airflow for zone i [m3/h]

Ez,i	is the zone distribution effectiveness for zone i

The primary outdoor air fraction for the zone is then determined as follows:

|  | Zpz,i=Voz,i/Vpz,i | (14) |
| --- | --- | --- |

where

Zpz,i	is the primary outdoor air fraction for zone i

The average outdoor air fraction for the ventilation system is then calculated based on the uncorrected outdoor air intake and the system total primary airflow:

|  | Xs=Vou/Vs | (15) |
| --- | --- | --- |

where

Xs	is the average outdoor air fraction

Vou	is the uncorrected outdoor air intake [m3/h]

assuming

|  | Vou=i=1nVbz,f,i | (16) |
| --- | --- | --- |

where

Vbz,f,i	is the final breathing zone outdoor airflow in zone i [m3/h]

For single supply systems wherein all of the air supplied to each ventilation zone is a mixture of outdoor air and system-level recirculated air, the zone ventilation efficiency is calculated as follows:

|  | Evz,i=1+Xs-Zpz,i | (17) |
| --- | --- | --- |

where

Evz,i	is the zone ventilation efficiency in zone i

For secondary recirculation systems wherein all or part of the supply air to each ventilation zone is recirculated air (air that has not been directly mixed with outdoor air) from other zones, the zone ventilation efficiency shall be determined as follows:

|  | Evz,i=Fa,i+XsFb,i-Zpz,iEp,iFc,i/Fa,i | (18) |
| --- | --- | --- |

where

Evz,i	is the zone ventilation efficiency in zone i

assuming

|  | Fa,i=Ep,i+1-Ep,iEr,i | (19) |
| --- | --- | --- |

|  | Fb,i=Ep,i | (20) |
| --- | --- | --- |

|  | Fc,i=1-1-Ez,i1-Er,i1-Ep,i | (21) |
| --- | --- | --- |

Where the zone secondary recirculation fraction (Er) is determined by the designer based on system configuration and the zone primary air fraction (Ep) is determined as follows:

|  | Ep,i=Vpz,i/Vdz,i | (22) |
| --- | --- | --- |

where

Vdz,i	is the zone discharge airflow in zone i [m3/h]

The system ventilation efficiency (Ev) is equal to the lowest calculated ventilation efficiency among all the ventilation zones in the system:

|  | Ev=minimumEvz,i | (22) |
| --- | --- | --- |

The final outdoor air intake flow (Vot) is then calculated:

|  | Vot=Vou/Ev | (24) |
| --- | --- | --- |

where

Vot	is the outdoor air intake [m3/h]

### Filter Location A2

In order to calculate outdoor air rates for individual zones in a multizone  system, this model iterates through a system-level estimate below breaking down to the zone level. First, estimate the uncorrected outdoor air ventilation rate for each design compound (DC) based on the size of the system:

|  | Vou,s=i=1nNi-VsEfCbzCbz1-Ef-Co | (1) |
| --- | --- | --- |

where

Vou,s	is the estimated system uncorrected outdoor airflow [m3/h]

Ni	is the compound emission rate in zone i [μg/h]

Vs	is the system total airflow [m3/h]

Ef	is the filter efficiency

Cbz	is the design limit for the DC [μg/m3]

Co	is the outdoor air concentration of the DC [μg/m3]

assuming

|  | Vs=minVps,i=1nVpz,i | (2) |
| --- | --- | --- |

Vps	is the system primary airflow [m3/h]

Vpz,i	is the primary airflow in zone i [m3/h]

Then use the estimated outdoor air rate to make a first-order estimate of the recirculated air volume that will pass through the filter:

|  | RVr=Vs-Vou,s | (3) |
| --- | --- | --- |

where

R	is the recirculation flow factor

Vr	is the return airflow [m3/h]

After the estimated airflow rates for each design compound have been calculated, the highest uncorrected outdoor airflow is selected, along with the corresponding recirculation airflow rate, and is applied to each design compound to conduct preliminary calculations for each zone. The outdoor airflow in the breathing zone is then calculated for each zone (separately for each design compound) as follows:

|  | Vbz,i=NiCbz-Co+XREfCbz | (4) |
| --- | --- | --- |

where

Vbz,i	is the breathing zone outdoor airflow in zone i [m3/h]

XR	is the ratio of recirculated airflow to outdoor airflow

assuming

|  | XR=RVrVou,s | (5) |
| --- | --- | --- |

The maximum breathing zone outdoor airflow (Vbz,i) for each zone across all design compounds is selected as the preliminary uncorrected outdoor airflow for the zone. The recirculated airflow assigned to the zone is then calculated proportionally:

|  | RVr,i=maxVbz,iXo | (6) |
| --- | --- | --- |

where

RVr,i	is the recirculated airflow into zone i [m3/h]

Xo	is the ratio of total outdoor airflow to total recirculated airflow

assuming

|  | Xo=i=1nmaxVbz,iVs-i=1nmaxVbz,i | (7) |
| --- | --- | --- |

With preliminary zone-level values calculated for zone, the model then iterates to adjust for variations across the DCs. The first outdoor airflow correction (Vbz,i,c) is as follows:

|  | Vbz,i,c=Ni-RVr,iEfCbzCbz-Co | (8) |
| --- | --- | --- |

Steps 6 through 8 are then repeated. A final adjustment is performed to ensure that the ratio of outdoor airflow and recirculated airflow to each zone is proportional to that of the system:

|  | Vbz,f=Vpz,i i=1nVbz,i,cVs | (9) |
| --- | --- | --- |

with

|  | RVr,i,f=Vpz,i-Vbz,f | (10) |
| --- | --- | --- |

The concentration of each DC in each zone must now be calculated to ensure that the DL in each zone is met. To do so, the model runs an iterative loop several times to model the migration of contaminants between zones via recirculated air. The loop is run enough times to reach convergence in each zone, for each DC, substituting the Cbz,i term into the Cbz,o term after that first iteration:

|  | Cs,i=Vbz,fCo+RVr,i,fCbz,o1-EfVs | (11) |
| --- | --- | --- |

where

Cs	is the contaminant concentration in the system primary air [μg/m3]

Cbz,o	is the initial contaminant concentration, set as the ambient concentration [μg/m3]

|  | Cbz,i=Vpz,iCs+NVpz,i | (12) |
| --- | --- | --- |

where

Cbz,i	is the contaminant concentration for each sequent iteration for zone i [μg/m3]

This eventually converges on the final concentration in each zone, Cbz,f. The compounds for each mixture must now be checked. For each mixture, the mixed exposure sum (Em) must be calculated to be less than 1.0:

|  | Em=Cbz,f,1DL1+Cbz,f,2DL2+Cbz,f,jDLj | (13) |
| --- | --- | --- |

where

Em	is the mixed exposure sum

Cbz,f,j	is the final calculated concentration for the jth DC

DLj	is the design limit for the jth DC

If the mixed exposure sum is less than unity for all relevant mixtures, the uncorrected outdoor airflow for the zone (Vbz,f) is acceptable. All zones must pass the mixtures check individually.

If there are any zones that fail the mixture check, the user will need to enter a value for the uncorrected outdoor air intake that is higher than the current set value. The process is repeated from Step 9, substituting the user input value for the summed outdoor airflow correction (Vbz,i,c).

The system ventilation efficiency is then calculated, equal to the lowest calculated zone ventilation efficiency.

For each contaminant, the zone outdoor airflow is calculated as follows:

|  | Voz,i=N-Ez,iRVr,i,fEfCbzEz,iCbz-Co | (14) |
| --- | --- | --- |

where

Voz,i	is the zone outdoor airflow for zone i [m3/h]

Ez,i	is the zone distribution effectiveness for zone i

The primary outdoor air fraction for the zone is then determined as follows:

|  | Zpz,i=Voz,i/Vpz,i | (15) |
| --- | --- | --- |

where

Zpz,i	is the primary outdoor air fraction for zone i

The average outdoor air fraction for the ventilation system is then calculated based on the uncorrected outdoor air intake and the system total primary airflow:

|  | Xs=Vou/Vs | (16) |
| --- | --- | --- |

where

Xs	is the average outdoor air fraction

Vou	is the uncorrected outdoor air intake [m3/h]

assuming

|  | Vou=i=1nVbz,f,i | (17) |
| --- | --- | --- |

where

Vbz,f,i	is the final breathing zone outdoor airflow in zone i [m3/h]

For single supply systems wherein all of the air supplied to each ventilation zone is a mixture of outdoor air and system-level recirculated air, the zone ventilation efficiency is calculated as follows:

|  | Evz,i=1+Xs-Zpz,i | (18) |
| --- | --- | --- |

where

Evz,i	is the zone ventilation efficiency in zone i

For secondary recirculation systems wherein all or part of the supply air to each ventilation zone is recirculated air (air that has not been directly mixed with outdoor air) from other zones, the zone ventilation efficiency shall be determined as follows:

|  | Evz,i=Fa,i+XsFb,i-Zpz,iEp,iFc,i/Fa,i | (19) |
| --- | --- | --- |

where

Evz,i	is the zone ventilation efficiency in zone i

assuming

|  | Fa,i=Ep,i+1-Ep,iEr,i | (20) |
| --- | --- | --- |

|  | Fb,i=Ep,i | (21) |
| --- | --- | --- |

|  | Fc,i=1-1-Ez,i1-Er,i1-Ep,i | (22) |
| --- | --- | --- |

where the zone secondary recirculation fraction (Er) is determined by the designer based on system configuration and the zone primary air fraction (Ep) is determined as follows:

|  | Ep,i=Vpz,i/Vdz,i | (23) |
| --- | --- | --- |

where

Vdz,i	is the zone discharge airflow in zone i [m3/h]

The system ventilation efficiency (Ev) is equal the lowest calculated ventilation efficiency among all the ventilation zones in the system:

|  | Ev=minimumEvz,i | (24) |
| --- | --- | --- |

The final outdoor air intake flow (Vot) is then calculated:

|  | Vot=Vou/Ev | (25) |
| --- | --- | --- |

where

Vot	is the outdoor air intake [m3/h]

### Filter Location B

In order to calculate outdoor air rates for individual zones in a multizone  system, this model iterates through a system-level estimate below breaking down to the zone level. First, estimate the uncorrected outdoor air ventilation rate for each design compound (DC) based on the size of the system:

|  | Vou,s=i=1nNi-VsEfCbzCbz-Co1-Ef | (1) |
| --- | --- | --- |

where

Vou,s	is the estimated system uncorrected outdoor airflow [m3/h]

Ni	is the compound emission rate in zone i [μg/h]

Vs	is the system total airflow [m3/h]

Ef	is the filter efficiency

Cbz	is the design limit for the DC [μg/m3]

Co	is the outdoor air concentration of the DC [μg/m3]

assuming

|  | Vs=minVps,i=1nVpz,i | (2) |
| --- | --- | --- |

Vps	is the system primary airflow [m3/h]

Vpz,i	is the primary airflow in zone i [m3/h]

Then use the estimated outdoor air rate to make a first-order estimate of the recirculated air volume that will pass through the filter:

|  | RVr=Vs-Vou,s | (3) |
| --- | --- | --- |

where

R	is the recirculation flow factor

Vr	is the return airflow [m3/h]

After the estimated airflow rates for each design compound have been calculated, the highest uncorrected outdoor airflow is selected, along with the corresponding recirculation airflow rate, and is applied to each design compound to conduct preliminary calculations for each zone. The outdoor airflow in the breathing zone is then calculated for each zone (separately for each design compound) as follows:

|  | Vbz,i=NiCbz-1-EfCo+XREfCbz | (4) |
| --- | --- | --- |

where

Vbz,i	is the breathing zone outdoor airflow in zone i [m3/h]

XR	is the ratio of recirculated airflow to outdoor airflow

assuming

|  | XR=RVrVou,s | (5) |
| --- | --- | --- |

The maximum breathing zone outdoor airflow (Vbz,i) for each zone across all design compounds is selected as the preliminary uncorrected outdoor airflow for the zone. The recirculated airflow assigned to the zone is then calculated proportionally:

|  | RVr,i=maxVbz,iXo | (6) |
| --- | --- | --- |

where

RVr,i	is the recirculated airflow into zone i [m3/h]

Xo	is the ratio of total outdoor airflow to total recirculated airflow

assuming

|  | Xo=i=1nmaxVbz,iVs-i=1nmaxVbz,i | (7) |
| --- | --- | --- |

With preliminary zone-level values calculated for zone, the model then iterates to adjust for variations across the DCs. The first outdoor airflow correction (Vbz,i,c) is as follows:

|  | Vbz,i,c=Ni-RVr,iEfCbzCbz-1-EfCo | (8) |
| --- | --- | --- |

Steps 6 through 8 are then repeated. A final adjustment is performed to ensure that the ratio of outdoor airflow and recirculated airflow to each zone is proportional to that of the system:

|  | Vbz,f=Vpz,i i=1nVbz,i,cVs | (9) |
| --- | --- | --- |

with

|  | RVr,i,f=Vpz,i-Vbz,f | (10) |
| --- | --- | --- |

The concentration of each DC in each zone must now be calculated to ensure that the DL in each zone is met. To do so, the model runs an iterative loop several times to model the migration of contaminants between zones via recirculated air. The loop is run enough times to reach convergence in each zone for each DC:

|  | Cs=Vbz,fCo+RVr,i,fCbz,o1-EfVs | (11) |
| --- | --- | --- |

where

Cs	is the contaminant concentration in the system primary air [μg/m3]

Cbz,o	is the initial contaminant concentration, set as the ambient concentration [μg/m3]

|  | Cbz,i=Vpz,iCs+NVpz,i | (12) |
| --- | --- | --- |

where

Cbz,i	is the contaminant concentration for each sequent iteration for zone i [μg/m3]

This eventually converges on the final concentration in each zone, Cbz,f. The compounds for each mixture must now be checked. For each mixture, the mixed exposure sum (Em) must be calculated to be less than 1.0:

|  | Em=Cbz,f,1DL1+Cbz,f,2DL2+Cbz,f,jDLj | (13) |
| --- | --- | --- |

where

Em	is the mixed exposure sum

Cbz,f,j	is the final calculated concentration for the jth DC

DLj	is the design limit for the jth DC

If the mixed exposure sum is less than unity for all relevant mixtures, the uncorrected outdoor airflow for the zone (Vbz,f) is acceptable. All zones must pass the mixtures check individually.

If there are any zones that fail the mixture check, the user will need to enter a value for the uncorrected outdoor air intake that is higher than the current set value. The process is repeated from Step 9 substituting the user input value for the summed outdoor airflow correction (Vbz,i,c).

The system ventilation efficiency is then calculated, equal to the lowest calculated zone ventilation efficiency.

For each contaminant, the zone outdoor airflow is calculated as follows:

|  | Voz,i=N-Ez,iRVr,i,fEfCbzEz,iCbz-1-EfCo | (14) |
| --- | --- | --- |

where

Voz,i	is the zone outdoor airflow for zone i [m3/h]

Ez,i	is the zone distribution effectiveness for zone i

The primary outdoor air fraction for the zone is then determined as follows:

|  | Zpz,i=Voz,i/Vpz,i | (15) |
| --- | --- | --- |

where

Zpz,i	is the primary outdoor air fraction for zone i

The average outdoor air fraction for the ventilation system is then calculated based on the uncorrected outdoor air intake and the system total primary airflow:

|  | Xs=Vou/Vs | (16) |
| --- | --- | --- |

where

Xs	is the average outdoor air fraction

Vou	is the uncorrected outdoor air intake [m3/h]

assuming

|  | Vou=i=1nVbz,f,i | (17) |
| --- | --- | --- |

where

Vbz,f,i	is the final breathing zone outdoor airflow in zone i [m3/h]

For single supply systems wherein all of the air supplied to each ventilation zone is a mixture of outdoor air and system-level recirculated air, the zone ventilation efficiency is calculated as follows:

|  | Evz,i=1+Xs-Zpz,i | (18) |
| --- | --- | --- |

where

Evz,i	is the zone ventilation efficiency in zone i

For secondary recirculation systems wherein all or part of the supply air to each ventilation zone is recirculated air (air that has not been directly mixed with outdoor air) from other zones, the zone ventilation efficiency shall be determined as follows:

|  | Evz,i=Fa,i+XsFb,i-Zpz,iEp,iFc,i/Fa,i | (19) |
| --- | --- | --- |

where

Evz,i	is the zone ventilation efficiency in zone i

assuming

|  | Fa,i=Ep,i+1-Ep,iEr,i | (20) |
| --- | --- | --- |

|  | Fb,i=Ep,i | (21) |
| --- | --- | --- |

|  | Fc,i=1-1-Ez,i1-Er,i1-Ep,i | (22) |
| --- | --- | --- |

where the zone secondary recirculation fraction (Er) is determined by the designer based on system configuration and the zone primary air fraction (Ep) is determined as follows:

|  | Ep,i=Vpz,i/Vdz,i | (23) |
| --- | --- | --- |

where

Vdz,i	is the zone discharge airflow in zone i [m3/h]

The system ventilation efficiency (Ev) is equal the lowest calculated ventilation efficiency among all the ventilation zones in the system:

|  | Ev=minimumEvz,i | (24) |
| --- | --- | --- |

The final outdoor air intake flow (Vot) is then calculated:

|  | Vot=Vou/Ev | (25) |
| --- | --- | --- |

where

Vot	is the outdoor air intake [m3/h]