## Based on Standard Update
Tab | Cell | Changed based on Standard update
REFERENCE | E9; A12:G12 | Phenol and 1,1,1-trichloroethane DLs have been updated to reflect changes made in Addendum q (1,1,1-trichloroethane DL increased to 10,000 so as to not require more extensive modifications across the calculator).
COMPLIANCE | H30; Row 33; E50:E51; Columns Z, AW | Phenol DL has been updated to reflect changes made in Addendum q, 1,1,1-trichloroethane has been removed entirely from Compliance documentation
PROJECT DATA | Row 16 | 1,1,1-trichloroethane removed from Table 1, updated to reflect changes made in Addendum q
Addendum q was published October 31, 2024
https://www.ashrae.org/file%20library/technical%20resources/standards%20and%20guidelines/standards%20addenda/62_1_2022_q_20241031.pdf

## Erratum
Tab | Cell | Erratum
INPUT | N41:N240 | Cells reference to filter location B in following part of the function is incorrect: "...AND($D$6="Single Zone",E7="B")…". Appropriate corrections have been made.
COMPLIANCE | G22, H22, H23 | Units have been added to column headers for clarity.
Singe Zone, Location A2, IP | AQ26, AW26,…, FB26 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Singe Zone, Location A2, IP | FF26 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Singe Zone, Location B, IP | AQ26, AW26,…, FB26 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Singe Zone, Location B, IP | FF26 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Multiple Zone, Location A1, IP | J31 | Function originally used ISBLANK() function, now ammedned to as nested OR function
Multiple Zone, Location A1, IP | P32:Z32 | Functions now reference correct cells
Multiple Zone, Location A1, IP | BA30, BM30, …, JJ30 | Functions corrected to now sum properly
Multiple Zone, Location A1, IP | JW32:JW231 | Absolute reference to cell J30 has been corrected
Multiple Zone, Location A1, IP | KT32:KY32 | Functions now reference correct cells
Multiple Zone, Location A2, IP | J31 | Function originally used ISBLANK() function, now ammedned to as nested OR function
Multiple Zone, Location A2, IP | BB30, BN30, …, JK30 | Functions corrected to now sum properly
Multiple Zone, Location A2, IP | KO32:KO231 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Multiple Zone, Location A2, IP | KQ32:KQ231 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Multiple Zone, Location A2, IP | KS32:KS231 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Multiple Zone, Location A2, IP | KU32:KU231 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Multiple Zone, Location A2, IP | KV32:LO231 | Nested OR() function has been corrected to nested AND()
Multiple Zone, Location B, IP | J31 | Function originally used ISBLANK() function, now ammedned to as nested OR function
Multiple Zone, Location B, IP | G34 | Functions now reference correct cells
Multiple Zone, Location B, IP | BB30, BN30, …, JK30 | Functions corrected to now sum properly
Multiple Zone, Location B, IP | KO32:KO231 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Multiple Zone, Location B, IP | KQ32:KQ231 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Multiple Zone, Location B, IP | KS32:KS231 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Multiple Zone, Location B, IP | KU32:KU231 | When user entered system design airflow (Vps) value was lower than the calculated RVr necessary, this would result in negative values for RVr. RVr calculation for each contaminant has been corrected to prevent this.
Multiple Zone, Location B, IP | KV32:LO231 | Nested OR() function has been corrected to nested AND()
Multiple Zone, Location B, IP | MV32:MV231 | The correct formula beginning in cell MV32 should be: =IFERROR(MAX(MB32:MU32)/$J32,0). All formulas in column MV should be amended to reference correct cell range.
Singe Zone, Location A1, IP | D11 | Error occurred when Vot override was entered less than calculated Vot. Function corrected to only reference calculated Vot value.
Singe Zone, Location A2, IP | D11 | Error occurred when Vot override was entered less than calculated Vot. Function corrected to only reference calculated Vot value.
Singe Zone, Location B, IP | D11 | Error occurred when Vot override was entered less than calculated Vot. Function corrected to only reference calculated Vot value.
Multiple Zone, Location A1, IP | D16 | Error occurred when Vot override was entered less than calculated Vot. Function corrected to only reference calculated Vot value.
Multiple Zone, Location A2, IP | D16 | Error occurred when Vot override was entered less than calculated Vot. Function corrected to only reference calculated Vot value.
Multiple Zone, Location B, IP | D16 | Error occurred when Vot override was entered less than calculated Vot. Function corrected to only reference calculated Vot value.